## STK-WME092S570T4220326100456100
Root Name | Title | Author | Date/Time | Groups | Description | MAX_Config
STK-WME092S570T4220326100456100 |  |  |  | 2 |  | 800configData01172017.nce
Group | Channels | Description
Spec Sheet | 59
800 Ton Test | 183
Spec Sheet
Channel | Datatype | Unit | Length | Minimum | Maximum | Description | Unit | IP_Units | Spec_Data | Tol_Max | Tol_Min | Tol_Stability | X_0 | X_1 | X_2 | X_3 | Start Index
GO # | DT_DOUBLE |  | 0 |  |  |  | #######-#####
Job Name | DT_DOUBLE |  | 0 |  |  |  | WME092S570T4
Unit Code | DT_DOUBLE |  | 0 |  |  |  | WME092CSCM7/E3012-FB2C-2/C2612-GB2C-2/R134-CAAAPAB-U
% Load | DT_DOUBLE |  | 0 |  |  |  | 100.000
Refrigerant | DT_DOUBLE |  | 0 |  |  |  | R134a
Test Type | DT_DOUBLE |  | 0 |  |  |  | Standard Factory Test only
Test Length | DT_DOUBLE |  | 0 |  |  |  | 15.000000
Serial Number | DT_DOUBLE |  | 0 |  |  |  | STNU220100150
Operator Name | DT_DOUBLE |  | 0 |  |  |  | GARCIA
Units | DT_DOUBLE |  | 0 |  |  |  | IP
Motor Data | DT_DOUBLE |  | 0 |  |  |  | XXXX
Evap Capacity | DT_DOUBLE |  | 0 |  |  | Tons=(Evap flow)(delta temp)/24 |  | (tons) | 570.000 | 598.53 | 541.47
Evap Flow | DT_DOUBLE |  | 0 |  |  | gallons water/minute |  | (gpm) | 1368.000 | 1436.4 | 1299.6 | 10.26
EvapTemp In | DT_DOUBLE |  | 0 |  |  |  |  | (°F) | 53.659 | 54.2 | 53.2 | 0.18
EvapTemp Out | DT_DOUBLE |  | 0 |  |  |  |  | (°F) | 43.689 | 44.19 | 43.19 | 0.18
Evap Delta Press | DT_DOUBLE |  | 0 |  |  | pressure loss end to end heat exchanger |  | (ft H2O) | 26.900 | 30.935 | 0
Cond Flow | DT_DOUBLE |  | 0 |  |  | gallons/minute |  | (gpm) | 1710.000 | 1795.5 | 1624.5 | 12.82
Cond Temp In | DT_DOUBLE |  | 0 |  |  |  |  | (°F) | 85.993 | 86.49 | 85.49 | 0.18
Cond Temp Out | DT_DOUBLE |  | 0 |  |  |  |  | (°F) | 95.343 |  |  | 0.18
Cond Delta Press | DT_DOUBLE |  | 0 |  |  | pressure loss end to end heat exchanger |  | (ft H2O) | 30.800 | 35.420 | 0
Voltage Ave | DT_DOUBLE |  | 0 |  |  | 3 phase voltage average |  | (Volts) | 460 | 506.0 | 414.0 | 2.30
Volts Balance | DT_DOUBLE |  | 0 |  |  |  |  | % | 0 | 2.0 | 0
Frequency | DT_DOUBLE |  | 0 |  |  |  |  | (Hz) | 60 | 60.60 | 59.40 | 0.30
KWatts Sum | DT_DOUBLE |  | 0 |  |  | 3 phase KW sum |  | (Sum kW) | 323.120
Efficiency | DT_DOUBLE |  | 0 |  |  |  |  | (kW/Ton) | 0.5670 | 0.5954 | 0
Energy Balance | DT_DOUBLE |  | 0 |  |  |  |  | % | 0 | 3.553 | -3.553
Refrig Charge | DT_DOUBLE |  | 0 |  |  | pounds of freon |  | (pounds) | 1151.0 | 0.99330 | 0.31140 | 0.05005
Evap Refrig Press | DT_DOUBLE |  | 0 |  |  | in psi |  | (psi) | 37.7
Evap Sat Temp | DT_DOUBLE |  | 0 |  |  |  |  | (°F) | 42.7
Suction Temp | DT_DOUBLE |  | 0 |  |  | at suction line into compressor |  | (°F) | 43.7
Suction Superheat | DT_DOUBLE |  | 0 |  |  |  |  | (°F) | 1.0
Cond Press | DT_DOUBLE |  | 0 |  |  |  |  | (psi) | 117.4 |  |  |  | 0 | 1 | 0 | 0.00E+00
Cond Sat Temp | DT_DOUBLE |  | 0 |  |  |  |  | (°F) | 96.7
Discharge Temp | DT_DOUBLE |  | 0 |  |  | at discharge line from compressor |  | (°F)
Discharge Superheat | DT_DOUBLE |  | 0 |  |  | temperature above freon vaporizes at pressure |  | (°F)
Liquid Line Temp | DT_DOUBLE |  | 0 |  |  |  |  | (°F) | 88.1
Subcooling | DT_DOUBLE |  | 0 |  |  | temperature below which freon condensed at pressure |  | (°F) | 8.6
Oil Cooler Tons | DT_DOUBLE |  | 0 |  |  | XXX |  | (tons) | 0.0
Oil Feed Press | DT_DOUBLE |  | 0 |  |  | XXX |  | (psi)
Net Oil Press | DT_DOUBLE |  | 0 |  |  | XXX |  | (psi)
Oil Feed Temp | DT_DOUBLE |  | 0 |  |  | XXX |  | (°F)
Oil Sump Temp | DT_DOUBLE |  | 0 |  |  | XXX |  | (°F)
Amps Comp1 P1 | DT_DOUBLE |  | 0 |  |  |  |  | Amps | 444.000
Amps Comp1 P2 | DT_DOUBLE |  | 0 |  |  |  |  | Amps | 444.000
Amps Comp1 P3 | DT_DOUBLE |  | 0 |  |  |  |  | Amps | 444.000
Amps Comp2 P1 | DT_DOUBLE |  | 0 |  |  |  |  | Amps | 0.000
Amps Comp2 P2 | DT_DOUBLE |  | 0 |  |  |  |  | Amps | 0.000
Amps Comp2 P3 | DT_DOUBLE |  | 0 |  |  |  |  | Amps | 0.000
Evap Water Flow | DT_DOUBLE |  | 0 |  |  | IN GPM | [6 empty] | 0 | 1 | 0 | 0.00E+00
Cond Water Flow | DT_DOUBLE |  | 0 |  |  | IN GPM | [6 empty] | 0 | 1 | 0 | 0.00E+00
Evap Press | DT_DOUBLE |  | 0 | [9 empty] | 0 | 1 | 0 | 0.00E+00
Cond Press Drop | DT_DOUBLE |  | 0 | [9 empty] | 0 | 1 | 0 | 0.00E+00
Evap Press Drop | DT_DOUBLE |  | 0 | [9 empty] | 0 | 1 | 0 | 0.00E+00
Barometric Press | DT_DOUBLE |  | 0 | [9 empty] | 0 | 1 | 0 | 0.00E+00
Evap In Water Temp | DT_DOUBLE |  | 0 | [9 empty] | 0 | 1 | 0 | 0.00E+00
Evap Out Water Temp | DT_DOUBLE |  | 0 | [9 empty] | 0 | 1 | 0 | 0.00E+00
Cond In Water Temp | DT_DOUBLE |  | 0 | [9 empty] | 0 | 1 | 0 | 0.00E+00
Cond Out Water Temp | DT_DOUBLE |  | 0 | [9 empty] | 0 | 1 | 0 | 0.00E+00
Tank Probe | DT_DOUBLE |  | 0 |  |  | XXX | [6 empty] | 0 | 1 | 0 | 0.00E+00
800 Ton Test
Channel | Datatype | Unit | Length | Minimum | Maximum | Description | Start Index
Time Stamp | DT_STRING |  | 847
Evap Capacity | DT_DOUBLE |  | 847 |  |  | In Tons
Evap Flow | DT_DOUBLE |  | 847
Evap Temp In | DT_DOUBLE |  | 847
Evap Temp Out | DT_DOUBLE |  | 847
Evap Delta Temp | DT_DOUBLE |  | 847
Evap Delta Press Ft H2O | DT_DOUBLE |  | 847
Evap Refrig Press | DT_DOUBLE |  | 847
Barometric Press | DT_DOUBLE |  | 847
Cond Flow | DT_DOUBLE |  | 847
Cond Temp Out | DT_DOUBLE |  | 847
Cond Temp In | DT_DOUBLE |  | 847
Cond Delta Temp | DT_DOUBLE |  | 847
Cond Delta Press Ft H2O | DT_DOUBLE |  | 847
Cond Refrig Press | DT_DOUBLE |  | 847
Liquid Line Temp | DT_DOUBLE |  | 847
Subcooling | DT_DOUBLE |  | 847
Oil Feed Press | DT_DOUBLE |  | 847 |  |  | XXX
Net Press Oil | DT_DOUBLE |  | 847 |  |  | XXX
Sump Temp Oil | DT_DOUBLE |  | 847 |  |  | XXX
Oil Feed Temp | DT_DOUBLE |  | 847 |  |  | XXX
Suction Temp | DT_DOUBLE |  | 847
Discharge Temp | DT_DOUBLE |  | 847
Discharge Superheat | DT_DOUBLE |  | 847
Frequency | DT_DOUBLE |  | 847
Volts P1 | DT_DOUBLE |  | 847
Volts P2 | DT_DOUBLE |  | 847
Volts P3 | DT_DOUBLE |  | 847
Amps P1 | DT_DOUBLE |  | 847
Amps P2 | DT_DOUBLE |  | 847
Amps P3 | DT_DOUBLE |  | 847
KWatts Sum | DT_DOUBLE |  | 847
Efficiency | DT_DOUBLE |  | 847 |  |  | (KWatts Sum)/(Tons)
Energy Balance | DT_DOUBLE |  | 847
Suction Superheat | DT_DOUBLE |  | 847
Evap Sat Temp | DT_DOUBLE |  | 847 |  |  | XXX
Vent Press Oil | DT_DOUBLE |  | 847
Cond Sat Temp | DT_DOUBLE |  | 847
Refrig Charge | DT_DOUBLE |  | 847
Vibration | DT_DOUBLE |  | 847 |  |  | G inches/sec measured at compressor impeller
Amps Comp2 P1 | DT_DOUBLE |  | 847
Amps Comp2 P2 | DT_DOUBLE |  | 847
Amps Comp2 P3 | DT_DOUBLE |  | 847
KW Comp1 | DT_DOUBLE |  | 847
Q'ev | DT_DOUBLE |  | 847
Q'cd | DT_DOUBLE |  | 847
Oil Cooler Tons | DT_DOUBLE |  | 847 |  |  | XXX
p Evap | DT_DOUBLE |  | 847
p Cond | DT_DOUBLE |  | 847
cp Evap | DT_DOUBLE |  | 847
cp Cond | DT_DOUBLE |  | 847
Evap Water mf | DT_DOUBLE |  | 847
Cond Water mf | DT_DOUBLE |  | 847
Voltage Average | DT_DOUBLE |  | 847
Voltage Balance | DT_DOUBLE |  | 847
Evap Delta Press Adj Ft H2O | DT_DOUBLE |  | 847
Cond Delta Press Adj Ft H2O | DT_DOUBLE |  | 847
Evap Delta Press Raw Ft H2O | DT_DOUBLE |  | 847
Cond Delta Press Raw Ft H2O | DT_DOUBLE |  | 847
Liquid Line Temp Comp2 | DT_DOUBLE |  | 847
Subcooling Comp2 | DT_DOUBLE |  | 847
Feed Press Comp2 | DT_DOUBLE |  | 847
Net Press Comp2 | DT_DOUBLE |  | 847
Sump Temp Comp2 | DT_DOUBLE |  | 847
Feed Temp Comp2 | DT_DOUBLE |  | 847
Suction Temp Comp2 | DT_DOUBLE |  | 847
Discharge Temp Comp2 | DT_DOUBLE |  | 847
Discharge Superheat Comp2 | DT_DOUBLE |  | 847
Ambient Temp | DT_DOUBLE |  | 847
Evap Water Flow ma | DT_DOUBLE |  | 847 |  |  | signal from flowmeter
Cond Water Flow ma | DT_DOUBLE |  | 847 |  |  | signal from flowmeter
Transfer Pump ma | DT_DOUBLE |  | 847 |  |  | signal to control VFD in ma (4 to 20 ma)
Booster Pump ma | DT_DOUBLE |  | 847 |  |  | signal to control VFD in ma (4 to 20 ma)
Transfer Valve ma | DT_DOUBLE |  | 847
Booster Valve ma | DT_DOUBLE |  | 847
Tons Time Ave | DT_DOUBLE |  | 847
Evap WF Time Ave | DT_DOUBLE |  | 847
Evap WT In Time Ave | DT_DOUBLE |  | 847
Evap WT Out Time Ave | DT_DOUBLE |  | 847
Evap Delta Press Time Ave | DT_DOUBLE |  | 847
Cond WF Time Ave | DT_DOUBLE |  | 847
Cond WT In Time Ave | DT_DOUBLE |  | 847
Cond Delta Press Time Ave | DT_DOUBLE |  | 847
Voltage Ave Time Ave | DT_DOUBLE |  | 847
Voltage Bal Time Ave | DT_DOUBLE |  | 847
Voltage Freq Time Ave | DT_DOUBLE |  | 847
KW/Ton Time Ave | DT_DOUBLE |  | 847
Energy Bal Time Ave | DT_DOUBLE |  | 847
Evap WF Stab Time Ave | DT_DOUBLE |  | 847
Evap WT In Stab Time Ave | DT_DOUBLE |  | 847
Evap WT Out Stab Time Ave | DT_DOUBLE |  | 847
Cond WF Stab Time Ave | DT_DOUBLE |  | 847
Cond WT In Stab Time Ave | DT_DOUBLE |  | 847
Voltage Ave Stab Time Ave | DT_DOUBLE |  | 847
Voltage Freq Stab Time Ave | DT_DOUBLE |  | 847
Pass | DT_DOUBLE |  | 847 |  |  | parameters in range including stability limits for 15 minutes
BAS Active Cap Limit | DT_DOUBLE |  | 847 |  |  | Values polled from Chiller PLC
BAS C1 Avg Current | DT_DOUBLE |  | 847
BAS C1 Avg Voltage | DT_DOUBLE |  | 847
BAS C1 Disch Press | DT_DOUBLE |  | 847
BAS C1 Disch Temp | DT_DOUBLE |  | 847
BAS C1 % RLA | DT_DOUBLE |  | 847
BAS C1 Power | DT_DOUBLE |  | 847
BAS C1 Run Hours | DT_DOUBLE |  | 847
BAS C1 Sat Disch Temp | DT_DOUBLE |  | 847
BAS C1 Sat Suct Temp | DT_DOUBLE |  | 847
BAS C1 Starts | DT_DOUBLE |  | 847
BAS C1 Suct Press | DT_DOUBLE |  | 847
BAS C1 Suct Temp | DT_DOUBLE |  | 847
BAS Avg Current | DT_DOUBLE |  | 847
BAS C2 Avg Voltage | DT_DOUBLE |  | 847
BAS C2 Disch Press | DT_DOUBLE |  | 847
BAS C2 Disch Temp | DT_DOUBLE |  | 847
BAS C2 % RLA | DT_DOUBLE |  | 847
BAS C2 Power | DT_DOUBLE |  | 847
BAS C2 Run Hours | DT_DOUBLE |  | 847
BAS C2 Sat Disch Temp | DT_DOUBLE |  | 847
BAS C2 Sat Suct Temp | DT_DOUBLE |  | 847
BAS C2 Starts | DT_DOUBLE |  | 847
BAS C2 Suct Press | DT_DOUBLE |  | 847
BAS C2 Suct Temp | DT_DOUBLE |  | 847
BAS Cap Limit SP | DT_DOUBLE |  | 847
BAS Cond Sat Temp | DT_DOUBLE |  | 847
BAS Evap Sat Temp | DT_DOUBLE |  | 847
BAS Evap Water Tar | DT_DOUBLE |  | 847
Cond Flow Rate | DT_DOUBLE |  | 847
Cond Press | DT_DOUBLE |  | 847
Evap Flow Rate | DT_DOUBLE |  | 847
Evap Press | DT_DOUBLE |  | 847
EXV Pos FB | DT_DOUBLE |  | 847
EXV Pos SP | DT_DOUBLE |  | 847
Liq Line Press | DT_DOUBLE |  | 847
Liq Line Sat Temp | DT_DOUBLE |  | 847
Liq Line Temp | DT_DOUBLE |  | 847
Manual EXV Pos SP | DT_DOUBLE |  | 847
Motor Current Out | DT_DOUBLE |  | 847
Pressure Ratio | DT_DOUBLE |  | 847
Sat Cond Temp | DT_DOUBLE |  | 847
Sat Evap Temp | DT_DOUBLE |  | 847
C1 Disch Press | DT_DOUBLE |  | 847
C1 Disch Superheat | DT_DOUBLE |  | 847
C1 Disch Temp | DT_DOUBLE |  | 847
C1 IGV Pos FB | DT_DOUBLE |  | 847
C1 Manual IGV Pos SP | DT_DOUBLE |  | 847
C1 Manual VFD Speed SP | DT_DOUBLE |  | 847
C1 Mtr Case Temp | DT_DOUBLE |  | 847
C1 Mtr Gap Temp | DT_DOUBLE |  | 847
C1 Mtr Windg Temp1 | DT_DOUBLE |  | 847
C1 Mtr Windg Temp2 | DT_DOUBLE |  | 847
C1 Mtr Windg Temp3 | DT_DOUBLE |  | 847
C1 PLBV FB | DT_DOUBLE |  | 847
C1 Rtr Cool Valve FB | DT_DOUBLE |  | 847
C1 Rtr Pump Temp | DT_DOUBLE |  | 847
C1 Run Seconds | DT_DOUBLE |  | 847
C1 Sat Disch Temp | DT_DOUBLE |  | 847
C1 Sat Suct Temp | DT_DOUBLE |  | 847
C1 Suct Press | DT_DOUBLE |  | 847
C1 Suct Superheat | DT_DOUBLE |  | 847
C1 Suct Temp | DT_DOUBLE |  | 847
C1 VFD1 Amps | DT_DOUBLE |  | 847
C1 VFD1 DC Link | DT_DOUBLE |  | 847
C1 VFD1 Input Current | DT_DOUBLE |  | 847
C1 VFD1 Input Voltage | DT_DOUBLE |  | 847
C1 VFD1 Internal Temp | DT_DOUBLE |  | 847
C1 VFD1 KW | DT_DOUBLE |  | 847
C1 VFD1 Sink Temp | DT_DOUBLE |  | 847
C1 VFD1 Voltage | DT_DOUBLE |  | 847
C1 VFD2 Amps | DT_DOUBLE |  | 847
C1 VFD2 DC Link | DT_DOUBLE |  | 847
C1 VFD2 Input Current | DT_DOUBLE |  | 847
C1 VFD2 Input Volt | DT_DOUBLE |  | 847
C1 VFD2 Internal Temp | DT_DOUBLE |  | 847
C1 VFD2 KW | DT_DOUBLE |  | 847
C1 VFD2 Sink Temp | DT_DOUBLE |  | 847
C1 VFD2 Voltage | DT_DOUBLE |  | 847
C1 VFD Amps | DT_DOUBLE |  | 847
C1 VFD Input Power | DT_DOUBLE |  | 847
C1 VFD IPS Hightemp | DT_DOUBLE |  | 847
C1 VFD KW | DT_DOUBLE |  | 847
C1 VFD RLA | DT_DOUBLE |  | 847
C1 VFD Speed FB | DT_DOUBLE |  | 847
C1 VFD Speed SP | DT_DOUBLE |  | 847
C1 VFD Voltage | DT_DOUBLE |  | 847

## Spec Sheet
GO # | Job Name | Unit Code | % Load | Refrigerant | Test Type | Test Length | Serial Number | Operator Name | Units | Motor Data | Evap Capacity | Evap Flow | EvapTemp In | EvapTemp Out | Evap Delta Press | Cond Flow | Cond Temp In | Cond Temp Out | Cond Delta Press | Voltage Ave | Volts Balance | Frequency | KWatts Sum | Efficiency | Energy Balance | Refrig Charge | Evap Refrig Press | Evap Sat Temp | Suction Temp | Suction Superheat | Cond Press | Cond Sat Temp | Discharge Temp | Discharge Superheat | Liquid Line Temp | Subcooling | Oil Cooler Tons | Oil Feed Press | Net Oil Press | Oil Feed Temp | Oil Sump Temp | Amps Comp1 P1 | Amps Comp1 P2 | Amps Comp1 P3 | Amps Comp2 P1 | Amps Comp2 P2 | Amps Comp2 P3 | Evap Water Flow | Cond Water Flow | Evap Press | Cond Press Drop | Evap Press Drop | Barometric Press | Evap In Water Temp | Evap Out Water Temp | Cond In Water Temp | Cond Out Water Temp | Tank Probe

## 800 Ton Test
Time Stamp | Evap Capacity | Evap Flow | Evap Temp In | Evap Temp Out | Evap Delta Temp | Evap Delta Press Ft H2O | Evap Refrig Press | Barometric Press | Cond Flow | Cond Temp Out | Cond Temp In | Cond Delta Temp | Cond Delta Press Ft H2O | Cond Refrig Press | Liquid Line Temp | Subcooling | Oil Feed Press | Net Press Oil | Sump Temp Oil | Oil Feed Temp | Suction Temp | Discharge Temp | Discharge Superheat | Frequency | Volts P1 | Volts P2 | Volts P3 | Amps P1 | Amps P2 | Amps P3 | KWatts Sum | Efficiency | Energy Balance | Suction Superheat | Evap Sat Temp | Vent Press Oil | Cond Sat Temp | Refrig Charge | Vibration | Amps Comp2 P1 | Amps Comp2 P2 | Amps Comp2 P3 | KW Comp1 | Q'ev | Q'cd | Oil Cooler Tons | p Evap | p Cond | cp Evap | cp Cond | Evap Water mf | Cond Water mf | Voltage Average | Voltage Balance | Evap Delta Press Adj Ft H2O | Cond Delta Press Adj Ft H2O | Evap Delta Press Raw Ft H2O | Cond Delta Press Raw Ft H2O | Liquid Line Temp Comp2 | Subcooling Comp2 | Feed Press Comp2 | Net Press Comp2 | Sump Temp Comp2 | Feed Temp Comp2 | Suction Temp Comp2 | Discharge Temp Comp2 | Discharge Superheat Comp2 | Ambient Temp | Evap Water Flow ma | Cond Water Flow ma | Transfer Pump ma | Booster Pump ma | Transfer Valve ma | Booster Valve ma | Tons Time Ave | Evap WF Time Ave | Evap WT In Time Ave | Evap WT Out Time Ave | Evap Delta Press Time Ave | Cond WF Time Ave | Cond WT In Time Ave | Cond Delta Press Time Ave | Voltage Ave Time Ave | Voltage Bal Time Ave | Voltage Freq Time Ave | KW/Ton Time Ave | Energy Bal Time Ave | Evap WF Stab Time Ave | Evap WT In Stab Time Ave | Evap WT Out Stab Time Ave | Cond WF Stab Time Ave | Cond WT In Stab Time Ave | Voltage Ave Stab Time Ave | Voltage Freq Stab Time Ave | Pass | BAS Active Cap Limit | BAS C1 Avg Current | BAS C1 Avg Voltage | BAS C1 Disch Press | BAS C1 Disch Temp | BAS C1 % RLA | BAS C1 Power | BAS C1 Run Hours | BAS C1 Sat Disch Temp | BAS C1 Sat Suct Temp | BAS C1 Starts | BAS C1 Suct Press | BAS C1 Suct Temp | BAS Avg Current | BAS C2 Avg Voltage | BAS C2 Disch Press | BAS C2 Disch Temp | BAS C2 % RLA | BAS C2 Power | BAS C2 Run Hours | BAS C2 Sat Disch Temp | BAS C2 Sat Suct Temp | BAS C2 Starts | BAS C2 Suct Press | BAS C2 Suct Temp | BAS Cap Limit SP | BAS Cond Sat Temp | BAS Evap Sat Temp | BAS Evap Water Tar | Cond Flow Rate | Cond Press | Evap Flow Rate | Evap Press | EXV Pos FB | EXV Pos SP | Liq Line Press | Liq Line Sat Temp | Liq Line Temp | Manual EXV Pos SP | Motor Current Out | Pressure Ratio | Sat Cond Temp | Sat Evap Temp | C1 Disch Press | C1 Disch Superheat | C1 Disch Temp | C1 IGV Pos FB | C1 Manual IGV Pos SP | C1 Manual VFD Speed SP | C1 Mtr Case Temp | C1 Mtr Gap Temp | C1 Mtr Windg Temp1 | C1 Mtr Windg Temp2 | C1 Mtr Windg Temp3 | C1 PLBV FB | C1 Rtr Cool Valve FB | C1 Rtr Pump Temp | C1 Run Seconds | C1 Sat Disch Temp | C1 Sat Suct Temp | C1 Suct Press | C1 Suct Superheat | C1 Suct Temp | C1 VFD1 Amps | C1 VFD1 DC Link | C1 VFD1 Input Current | C1 VFD1 Input Voltage | C1 VFD1 Internal Temp | C1 VFD1 KW | C1 VFD1 Sink Temp | C1 VFD1 Voltage | C1 VFD2 Amps | C1 VFD2 DC Link | C1 VFD2 Input Current | C1 VFD2 Input Volt | C1 VFD2 Internal Temp | C1 VFD2 KW | C1 VFD2 Sink Temp | C1 VFD2 Voltage | C1 VFD Amps | C1 VFD Input Power | C1 VFD IPS Hightemp | C1 VFD KW | C1 VFD RLA | C1 VFD Speed FB | C1 VFD Speed SP | C1 VFD Voltage
03/26/22 10:04:56.222 | 558.6008 | 1369.4193 | 52.9046 | 43.1455 | 9.759 | 29.9465 | 50.6584 | 0 | 1782.315 | 69.1388 | 61.0891 | 8.0498 | 27.5338 | 68.1838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.974 | 461.37 | 458.35 | 462.24 | 295.79 | 318.6 | 297.11 | 221.62 | 0.39674 | 3.8442 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6729563.8868 | 7203422.8232 | 7203422.8232 | 62.4308 | 62.3519 | 1.002 | 0.9992 | 685516.7277 | 891653.8179 | 460.6533 | 0.50001 | 0 | 0 | 29.9465 | 27.5338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.018035 | 0.016956 | 0.00479 | 0.0119 | 0.0119 | 338.4471 | 1367.8685 | 51.2637 | 45.3433 | 31.597 | 1787.6373 | 58.275 | 26.4593 | #NV | #NV | #NV | #NV | #NV | 63.2174 | 2.5976 | 1.3082 | 3.2109 | 4.901 | 1.7436 | #NV | 0 | 100 | 411.2 | 308 | 75.68 | 86.78 | 71.51 | 216.1 | 3 | 72.93 | 40.1 | 4 | 35.35 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 73.4 | 0 | 36 | 64 | 64 | 70.83 | 69.65 | 62.65 | 0 | 71.72 | 1.74 | 71.4 | 40.77 | 75.68 | 13.83 | 86.79 | 110 | 0 | 14564 | 79.56 | 100.06 | 155.13 | 152.09 | 154.13 | 0 | 19.16 | 48.08 | 11680 | 72.95 | 40.1 | 35.35 | 3.85 | 40.1 | 0 | 611 | 310.5 | 462.8 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411.5 | 221.2 | 0 | 216.7 | 71.57 | 14557 | 14564 | 310
03/26/22 10:05:01.223 | 559.2951 | 1367.8916 | 52.9359 | 43.1538 | 9.7821 | 29.861 | 50.6518 | 0 | 1782.253 | 69.2082 | 61.1374 | 8.0707 | 27.3319 | 68.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.974 | 461.37 | 458.35 | 462.24 | 295.79 | 318.6 | 297.11 | 221.62 | 0.39625 | 3.7026 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6737790.2174 | 7221561.0738 | 7221561.0738 | 62.4308 | 62.3515 | 1.002 | 0.99919 | 684750.6951 | 891618.9283 | 460.6534 | 0.50001 | 0 | 0 | 29.861 | 27.3319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.018042 | 0.016956 | 0.00479 | 0.0119 | 0.0119 | 340.2044 | 1367.8717 | 51.2971 | 45.346 | 31.573 | 1787.6545 | 58.2729 | 26.4774 | #NV | #NV | #NV | #NV | #NV | 63.2396 | 2.5973 | 1.2731 | 3.2089 | 4.8765 | 1.7399 | #NV | 0 | 100 | 414 | 309 | 75.83 | 87 | 72 | 218.9 | 3 | 73.03 | 40.04 | 4 | 35.29 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 73.6 | 0 | 35.95 | 64 | 64 | 71.03 | 69.79 | 62.71 | 0 | 72 | 1.74 | 71.54 | 40.72 | 75.9 | 13.94 | 87.02 | 110 | 0 | 14600 | 78.77 | 100.13 | 155.55 | 152.5 | 154.55 | 0 | 19.25 | 48.3 | 11685 | 73.08 | 40.04 | 35.29 | 3.92 | 40.04 | 0 | 611 | 309.6 | 462.7 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414.1 | 224.7 | 0 | 220.1 | 72.02 | 14593 | 14600 | 308
03/26/22 10:05:06.223 | 561.2149 | 1368.8361 | 52.9721 | 43.1631 | 9.809 | 29.8589 | 50.6441 | 0 | 1780.3744 | 69.2876 | 61.1912 | 8.0964 | 27.3575 | 68.1884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.974 | 461.39 | 458.31 | 462.16 | 298.65 | 321.46 | 300.03 | 223.85 | 0.39887 | 3.7998 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6760844.4228 | 7236733.1422 | 7236733.1422 | 62.4307 | 62.3511 | 1.002 | 0.99919 | 685221.9583 | 890674.7498 | 460.62 | 0.5015 | 0 | 0 | 29.8589 | 27.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.018037 | 0.016956 | 0.00479 | 0.0119 | 0.0119 | 342.0463 | 1367.8989 | 51.3291 | 45.3458 | 31.5476 | 1787.6662 | 58.2734 | 26.495 | #NV | #NV | #NV | #NV | #NV | 63.2656 | 2.5815 | 1.242 | 3.209 | 4.8562 | 1.7408 | #NV | 0 | 100 | 417.2 | 312 | 76.15 | 87.25 | 72.5 | 221.9 | 3 | 73.25 | 39.99 | 4 | 35.24 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 73.83 | 0 | 35.89 | 64 | 64 | 71.2 | 69.93 | 62.78 | 0 | 72.5 | 1.75 | 71.69 | 40.66 | 76.15 | 14.02 | 87.27 | 110 | 0 | 14640 | 78.03 | 100.26 | 156.01 | 152.9 | 154.99 | 0 | 19.5 | 48.52 | 11690 | 73.25 | 39.99 | 35.23 | 3.97 | 39.99 | 0 | 611 | 312.8 | 462.6 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.8 | 226.6 | 0 | 221.9 | 72.66 | 14629 | 14640 | 308
03/26/22 10:05:11.222 | 564.964 | 1371.1018 | 53.0364 | 43.1781 | 9.8584 | 29.9524 | 50.6563 | 0 | 1785.8399 | 69.4289 | 61.285 | 8.1439 | 27.6576 | 68.1549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.97 | 461.35 | 458.25 | 462.1 | 301.28 | 324.23 | 302.73 | 225.92 | 0.39988 | 3.654 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6805958.9536 | 7301520.999 | 7301520.999 | 62.4306 | 62.3503 | 1.002 | 0.99918 | 686353.4483 | 893401.3592 | 460.5667 | 0.503 | 0 | 0 | 29.9524 | 27.6576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.018033 | 0.016956 | 0.00479 | 0.0119 | 0.0119 | 343.9454 | 1367.9269 | 51.3599 | 45.3432 | 31.5271 | 1787.7088 | 58.2762 | 26.5089 | #NV | #NV | #NV | #NV | #NV | 63.295 | 2.5922 | 1.2144 | 3.2105 | 4.7983 | 1.7452 | #NV | 0 | 100 | 420.9 | 311 | 76.35 | 87.51 | 73.2 | 224.1 | 3 | 73.38 | 39.93 | 4 | 35.19 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 74.03 | 0 | 35.84 | 64 | 64 | 71.4 | 70.06 | 62.84 | 0 | 73.01 | 1.76 | 71.82 | 40.6 | 76.35 | 14.11 | 87.51 | 110 | 0 | 14680 | 77.42 | 100.43 | 156.43 | 153.27 | 155.38 | 0 | 19.58 | 48.5 | 11695 | 73.38 | 39.93 | 35.19 | 4.04 | 39.93 | 0 | 610 | 315.4 | 462.4 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.9 | 228.8 | 0 | 224.1 | 73.2 | 14670 | 14680 | 311
03/26/22 10:05:16.222 | 565.9953 | 1370.8953 | 53.0611 | 43.1832 | 9.8779 | 29.6615 | 50.6505 | 0 | 1786.0722 | 69.4848 | 61.3221 | 8.1627 | 28.0374 | 68.1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9701 | 461.3501 | 458.2501 | 462.1001 | 301.2801 | 324.2301 | 302.7301 | 225.9201 | 0.39916 | 3.6127 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6818074.9415 | 7319647.4305 | 7319647.4305 | 62.4306 | 62.35 | 1.002 | 0.99917 | 686249.0515 | 893514.522 | 460.5667 | 0.503 | 0 | 0 | 29.6615 | 28.0374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.018032 | 0.016956 | 0.00479 | 0.0119 | 0.0119 | 345.9145 | 1367.9568 | 51.3893 | 45.3379 | 31.5059 | 1787.7352 | 58.2815 | 26.5239 | #NV | #NV | #NV | #NV | #NV | 63.3279 | 2.5952 | 1.191 | 3.2133 | 4.7759 | 1.7531 | #NV | 0 | 100 | 423.4 | 312 | 76.58 | 87.72 | 73.53 | 224.4 | 3 | 73.53 | 39.89 | 4 | 35.15 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 74.2 | 0 | 35.8 | 64 | 64 | 71.53 | 70.15 | 62.86 | 0 | 73.53 | 1.76 | 71.96 | 40.57 | 76.58 | 14.21 | 87.74 | 110 | 0 | 14712 | 76.87 | 100.62 | 156.84 | 153.67 | 155.79 | 0 | 19.75 | 48.68 | 11700 | 73.53 | 39.89 | 35.15 | 4.11 | 39.89 | 0 | 610 | 317.5 | 462.3 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424.2 | 232 | 0 | 227.3 | 73.77 | 14709 | 14712 | 311
03/26/22 10:05:21.222 | 567.277 | 1369.4915 | 53.1019 | 43.1915 | 9.9105 | 29.6835 | 50.6452 | 0 | 1788.3379 | 69.5794 | 61.3852 | 8.1943 | 27.5557 | 68.1417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9721 | 461.3201 | 458.2201 | 462.0801 | 302.5601 | 325.6001 | 304.0501 | 226.9301 | 0.40003 | 3.3131 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6833447.9957 | 7356482.3737 | 7356482.3737 | 62.4305 | 62.3495 | 1.0019 | 0.99916 | 685544.6045 | 894642.8107 | 460.5401 | 0.50376 | 0 | 0 | 29.6835 | 27.5557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.018028 | 0.016482 | 0.00479 | 0.0119 | 0.0119 | 348.0007 | 1367.971 | 51.4166 | 45.3288 | 31.4814 | 1787.754 | 58.2901 | 26.5398 | #NV | #NV | #NV | #NV | #NV | 63.3655 | 2.5966 | 1.1733 | 3.2171 | 4.7715 | 1.7645 | #NV | 0 | 100 | 426.6 | 310 | 76.77 | 87.96 | 74.19 | 226.2 | 3 | 73.64 | 39.8 | 4 | 35.06 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 74.43 | 0 | 35.73 | 64 | 64 | 71.75 | 70.3 | 62.89 | 0 | 74.02 | 1.77 | 72.11 | 40.49 | 76.8 | 14.31 | 87.98 | 110 | 0 | 14756 | 76.4 | 100.81 | 157.3 | 154.09 | 156.23 | 0 | 20.07 | 48.94 | 11705 | 73.67 | 39.8 | 35.06 | 4.22 | 39.8 | 0 | 610 | 319.2 | 462.2 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426.8 | 232.3 | 0 | 227.5 | 74.23 | 14749 | 14756 | 312
03/26/22 10:05:26.222 | 569.158 | 1368.16 | 53.1543 | 43.2011 | 9.9531 | 29.8846 | 50.6423 | 0 | 1786.8205 | 69.7056 | 61.4705 | 8.2351 | 27.5496 | 68.1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9721 | 461.3101 | 458.1901 | 462.0701 | 303.8201 | 326.9601 | 305.3001 | 227.9201 | 0.40045 | 3.2929 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6856170.9143 | 7386558.4666 | 7386558.4666 | 62.4304 | 62.3488 | 1.0019 | 0.99915 | 684875.8575 | 893876.7382 | 460.5234 | 0.50667 | 0 | 0 | 29.8846 | 27.5496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.018036 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 350.1678 | 1367.9685 | 51.4424 | 45.3167 | 31.4589 | 1787.7681 | 58.3016 | 26.5527 | #NV | #NV | #NV | #NV | #NV | 63.4072 | 2.5962 | 1.1601 | 3.221 | 4.765 | 1.7785 | #NV | 0 | 100 | 428.7 | 311 | 76.93 | 88.21 | 74.56 | 229.8 | 3 | 73.75 | 39.73 | 4 | 34.99 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 74.63 | 0 | 35.65 | 64 | 64 | 71.95 | 70.44 | 62.93 | 0 | 74.56 | 1.77 | 72.24 | 40.41 | 76.95 | 14.45 | 88.22 | 110 | 0 | 14792 | 75.97 | 100.98 | 157.79 | 154.51 | 156.67 | 0 | 20.36 | 49 | 11710 | 73.77 | 39.73 | 34.99 | 4.3 | 39.73 | 0 | 610 | 324.3 | 462.1 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429.6 | 234.8 | 0 | 230 | 74.71 | 14784 | 14792 | 313
03/26/22 10:05:31.222 | 572.273 | 1370.0747 | 53.202 | 43.2083 | 9.9937 | 30.4597 | 50.6484 | 0 | 1783.7807 | 69.8251 | 61.5522 | 8.2729 | 26.6318 | 68.1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.975 | 461.27 | 458.15 | 462.05 | 307.67 | 331.13 | 309.23 | 230.99 | 0.40364 | 3.5183 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6894093.7716 | 7406538.656 | 7406538.656 | 62.4304 | 62.3481 | 1.0019 | 0.99914 | 685832.2792 | 892349.3069 | 460.49 | 0.50815 | 0 | 0 | 30.4597 | 26.6318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.018039 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 352.4554 | 1367.964 | 51.4649 | 45.2992 | 31.4317 | 1787.7756 | 58.3173 | 26.5722 | #NV | #NV | #NV | #NV | #NV | 63.4546 | 2.5947 | 1.1538 | 3.2239 | 4.761 | 1.7941 | #NV | 0 | 100 | 433.1 | 310 | 77.05 | 88.47 | 75.32 | 230.5 | 3 | 73.84 | 39.66 | 4 | 34.93 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 74.85 | 0 | 35.59 | 64 | 64 | 72.17 | 70.59 | 62.99 | 0 | 75.1 | 1.78 | 72.39 | 40.35 | 77.05 | 14.64 | 88.49 | 110 | 0 | 14832 | 75.59 | 101.13 | 158.25 | 154.92 | 157.15 | 0 | 20.48 | 48.81 | 11715 | 73.84 | 39.66 | 34.93 | 4.37 | 39.66 | 0 | 610 | 327.8 | 462.1 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432.7 | 235.9 | 0 | 231.1 | 75.25 | 14823 | 14832 | 312
03/26/22 10:05:36.223 | 573.2833 | 1369.9199 | 53.2236 | 43.2111 | 10.0125 | 30.5071 | 50.6464 | 0 | 1782.4543 | 69.8807 | 61.5905 | 8.2902 | 26.9674 | 68.0963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9751 | 461.2701 | 458.1501 | 462.0501 | 307.6701 | 331.1301 | 309.2301 | 230.9901 | 0.40292 | 3.6752 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6906256.3514 | 7416740.4697 | 7416740.4697 | 62.4303 | 62.3478 | 1.0019 | 0.99914 | 685753.8615 | 891682.6333 | 460.4901 | 0.50815 | 0 | 0 | 30.5071 | 26.9674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.018043 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 354.8328 | 1367.9663 | 51.4859 | 45.2786 | 31.4093 | 1787.7692 | 58.3357 | 26.5891 | #NV | #NV | #NV | #NV | #NV | 63.5061 | 2.5963 | 1.1513 | 3.2254 | 4.7674 | 1.8106 | #NV | 0 | 100 | 435.7 | 314 | 77.33 | 88.7 | 75.62 | 234.3 | 3 | 74.01 | 39.58 | 4 | 34.85 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 75.1 | 0 | 35.51 | 64 | 64 | 72.43 | 70.76 | 63.04 | 0 | 75.62 | 1.79 | 72.55 | 40.27 | 77.4 | 14.7 | 88.76 | 110 | 0 | 14872 | 75.22 | 101.25 | 158.69 | 155.38 | 157.6 | 0 | 20.61 | 48.81 | 11720 | 74.06 | 39.57 | 34.85 | 4.44 | 39.57 | 0 | 610 | 327.6 | 461.9 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435.7 | 238.9 | 0 | 234 | 75.77 | 14863 | 14872 | 313
03/26/22 10:05:41.222 | 573.5198 | 1365.3421 | 53.2665 | 43.2162 | 10.0503 | 29.9448 | 50.641 | 0 | 1789.0036 | 70.0147 | 61.6894 | 8.3253 | 27.8862 | 68.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.978 | 461.22 | 458.09 | 462.04 | 312.15 | 336.08 | 313.84 | 234.58 | 0.40902 | 3.0639 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6908511.1248 | 7476303.1005 | 7476303.1005 | 62.4303 | 62.3471 | 1.0019 | 0.99912 | 683460.4987 | 894950.7744 | 460.45 | 0.51254 | 0 | 0 | 29.9448 | 27.8862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.018025 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 357.309 | 1367.9702 | 51.5043 | 45.2537 | 31.383 | 1787.7734 | 58.3578 | 26.6094 | #NV | #NV | #NV | #NV | #NV | 63.5626 | 2.5944 | 1.1529 | 3.2239 | 4.765 | 1.8266 | #NV | 0 | 100 | 434.8 | 314 | 77.78 | 89 | 75.6 | 232.4 | 3 | 74.31 | 39.31 | 4 | 34.58 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 75.5 | 0 | 35.26 | 64 | 64 | 72.83 | 71.01 | 63.13 | 0 | 75.6 | 1.8 | 72.82 | 40.02 | 77.83 | 14.68 | 89.04 | 110 | 0 | 14912 | 74.92 | 101.4 | 159.17 | 155.78 | 158.04 | 0 | 20.94 | 48.67 | 11725 | 74.34 | 39.27 | 34.54 | 4.74 | 39.27 | 0 | 610 | 329.3 | 461.8 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435 | 238 | 0 | 233.1 | 75.65 | 14904 | 14912 | 314
03/26/22 10:05:46.222 | 574.4344 | 1365.7343 | 53.2858 | 43.2198 | 10.0661 | 30.5711 | 50.6406 | 0 | 1792.9569 | 70.1205 | 61.7806 | 8.34 | 27.1744 | 68.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9791 | 461.1901 | 458.0701 | 462.0601 | 314.3301 | 338.5401 | 316.1201 | 236.3601 | 0.41147 | 2.8559 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6919959.6094 | 7502997.6825 | 7502997.6825 | 62.4302 | 62.3465 | 1.0019 | 0.99912 | 683627.731 | 896878.5698 | 460.4401 | 0.51472 | 0 | 0 | 30.5711 | 27.1744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.018023 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 359.8646 | 1367.9583 | 51.5207 | 45.2253 | 31.363 | 1787.8304 | 58.3831 | 26.6268 | #NV | #NV | #NV | #NV | #NV | 63.6235 | 2.6 | 1.1571 | 3.2191 | 4.7642 | 1.8421 | #NV | 0 | 100 | 438.1 | 313 | 78.1 | 89.3 | 76.19 | 237.1 | 3 | 74.52 | 39.05 | 4 | 34.34 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 75.88 | 0 | 35.04 | 64 | 64 | 73.15 | 71.23 | 63.26 | 0 | 76.19 | 1.82 | 73.05 | 39.78 | 78.18 | 14.8 | 89.35 | 110 | 0 | 14948 | 74.64 | 101.49 | 159.65 | 156.2 | 158.5 | 0 | 21.04 | 48.17 | 11730 | 74.55 | 39.02 | 34.3 | 4.93 | 39.02 | 0 | 610 | 336.5 | 461.8 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438.1 | 241.4 | 0 | 236.5 | 76.19 | 14939 | 14948 | 316
03/26/22 10:05:51.222 | 575.3579 | 1366.9988 | 53.2921 | 43.2218 | 10.0704 | 30.8843 | 50.6406 | 0 | 1791.6564 | 70.1855 | 61.8416 | 8.3439 | 26.7385 | 68.1231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.979 | 461.19 | 458.07 | 462.06 | 314.33 | 338.54 | 316.12 | 236.36 | 0.41081 | 3.09 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6931424.9474 | 7502457.1523 | 7502457.1523 | 62.4302 | 62.346 | 1.0019 | 0.99911 | 684288.7052 | 896265.1452 | 460.44 | 0.51473 | 0 | 0 | 30.8843 | 26.7385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.01804 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 362.491 | 1367.9515 | 51.5352 | 45.1938 | 31.3458 | 1787.8989 | 58.4111 | 26.6391 | #NV | #NV | #NV | #NV | #NV | 63.6881 | 2.6009 | 1.1629 | 3.2108 | 4.7297 | 1.8562 | #NV | 0 | 100 | 441.7 | 314 | 78.65 | 89.67 | 76.82 | 236 | 3 | 74.87 | 38.92 | 4 | 34.21 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 76.25 | 0 | 34.95 | 64 | 64 | 73.53 | 71.49 | 63.41 | 0 | 76.82 | 1.83 | 73.3 | 39.69 | 78.68 | 14.8 | 89.69 | 110 | 0 | 14988 | 74.36 | 101.56 | 160.1 | 156.65 | 158.94 | 0 | 20.91 | 47.57 | 11735 | 74.89 | 38.92 | 34.21 | 4.94 | 38.92 | 0 | 609 | 331.5 | 461.7 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 442.1 | 243.1 | 0 | 238.1 | 76.89 | 14980 | 14988 | 317
03/26/22 10:05:56.221 | 575.204 | 1366.8542 | 53.292 | 43.2233 | 10.0687 | 30.4448 | 50.6262 | 0 | 1781.5459 | 70.3435 | 62.0019 | 8.3416 | 27.1671 | 68.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9791 | 461.1701 | 458.0501 | 462.0501 | 316.5001 | 340.9501 | 318.4101 | 238.1301 | 0.41399 | 3.7285 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6929189.5936 | 7458351.5521 | 7458351.5521 | 62.4302 | 62.3449 | 1.0019 | 0.99909 | 684216.3597 | 891194.1176 | 460.4234 | 0.51547 | 0 | 0 | 30.4448 | 27.1671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.018035 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 365.1428 | 1367.9478 | 51.5486 | 45.1605 | 31.3229 | 1787.9114 | 58.4413 | 26.656 | #NV | #NV | #NV | #NV | #NV | 63.7554 | 2.602 | 1.1692 | 3.1999 | 4.7098 | 1.8702 | #NV | 0 | 100 | 444.7 | 316 | 79 | 89.96 | 77.34 | 237.6 | 3 | 75.1 | 38.85 | 4 | 34.15 | 43.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 76.58 | 0 | 34.86 | 64 | 64 | 73.77 | 71.67 | 63.55 | 0 | 77.34 | 1.84 | 73.51 | 39.61 | 79.05 | 14.87 | 90 | 110 | 0 | 15017 | 74.1 | 101.64 | 160.59 | 157.08 | 159.42 | 0 | 20.76 | 47.17 | 11740 | 75.13 | 38.82 | 34.13 | 4.97 | 38.82 | 0 | 609 | 340.1 | 461.5 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438.3 | 245.4 | 0 | 240.5 | 76.23 | 15011 | 15017 | 317
03/26/22 10:06:01.222 | 575.7392 | 1369.249 | 53.2828 | 43.2188 | 10.064 | 30.0601 | 50.633 | 0 | 1784.8387 | 70.4337 | 62.097 | 8.3367 | 27.8664 | 68.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.979 | 461.17 | 458.05 | 462.05 | 316.5 | 340.95 | 318.41 | 238.13 | 0.41361 | 3.6447 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6935478.3229 | 7470670.339 | 7470670.339 | 62.4302 | 62.3444 | 1.0019 | 0.99908 | 685102.7971 | 893002.734 | 460.4234 | 0.51547 | 0 | 0 | 30.0601 | 27.8664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.018038 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 367.8836 | 1367.9341 | 51.5593 | 45.1232 | 31.2965 | 1787.9324 | 58.475 | 26.6791 | #NV | #NV | #NV | #NV | #NV | 63.8274 | 2.5884 | 1.1762 | 3.1829 | 4.6875 | 1.8812 | #NV | 0 | 100 | 444.2 | 316 | 79.23 | 90.22 | 77.57 | 243.7 | 3 | 75.24 | 38.73 | 4 | 34.04 | 43.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 76.75 | 0 | 34.76 | 64 | 64 | 73.95 | 71.79 | 63.71 | 0 | 77.57 | 1.85 | 73.64 | 39.49 | 79.27 | 14.99 | 90.26 | 110 | 0 | 15023 | 73.89 | 101.69 | 161.05 | 157.5 | 159.9 | 0 | 20.81 | 47.22 | 11745 | 75.27 | 38.72 | 34.01 | 5 | 38.72 | 0 | 609 | 338.8 | 461.3 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 445.3 | 245.7 | 0 | 240.7 | 77.44 | 15022 | 15023 | 316
03/26/22 10:06:06.222 | 574.8468 | 1368.4026 | 53.2476 | 43.1966 | 10.051 | 30.239 | 50.6392 | 0 | 1787.8063 | 70.6267 | 62.3008 | 8.3259 | 27.0973 | 68.1054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.97 | 461.01 | 457.94 | 461.97 | 321.27 | 346.33 | 323.64 | 242.08 | 0.42112 | 3.6451 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6924752.0746 | 7470043.6006 | 7470043.6006 | 62.4303 | 62.3429 | 1.0019 | 0.99906 | 684993.3079 | 894300.5571 | 460.3067 | 0.51415 | 0 | 0 | 30.239 | 27.0973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.018031 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 370.6825 | 1367.9148 | 51.5686 | 45.0836 | 31.2713 | 1787.956 | 58.5104 | 26.6997 | #NV | #NV | #NV | #NV | #NV | 63.9019 | 2.5574 | 1.1831 | 3.162 | 4.6635 | 1.8901 | #NV | 0 | 100 | 446 | 314 | 79.43 | 90.44 | 76.66 | 241.8 | 3 | 75.37 | 38.68 | 4 | 33.99 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 76.93 | 0 | 34.71 | 64 | 64 | 74.15 | 71.92 | 63.88 | 0 | 76.66 | 1.85 | 73.75 | 39.44 | 79.45 | 15.09 | 90.47 | 110 | 0 | 15014 | 73.68 | 101.78 | 161.51 | 157.93 | 160.33 | 0 | 20.86 | 47.12 | 11750 | 75.39 | 38.68 | 33.98 | 4.99 | 38.68 | 0 | 609 | 329.9 | 461.4 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 443 | 238.5 | 0 | 233.6 | 77.04 | 15016 | 15014 | 315
03/26/22 10:06:11.221 | 574.1395 | 1367.4736 | 53.229 | 43.1837 | 10.0454 | 30.3029 | 50.6476 | 0 | 1788.4669 | 70.7079 | 62.3862 | 8.3217 | 26.9277 | 68.1235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9701 | 461.0101 | 457.9401 | 461.9701 | 321.2701 | 346.3301 | 323.6401 | 242.0801 | 0.42164 | 3.5971 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6916302.5696 | 7468735.4381 | 7468735.4381 | 62.4304 | 62.3424 | 1.0019 | 0.99905 | 684529.0618 | 894623.7579 | 460.3067 | 0.51415 | 0 | 0 | 30.3029 | 26.9277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.018036 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 373.5357 | 1367.8847 | 51.5757 | 45.0407 | 31.2499 | 1788.0078 | 58.5494 | 26.711 | #NV | #NV | #NV | #NV | #NV | 63.9808 | 2.5303 | 1.1893 | 3.1349 | 4.6166 | 1.8974 | #NV | 0 | 100 | 443 | 314 | 79.58 | 90.63 | 76.71 | 239.1 | 3 | 75.45 | 38.68 | 4 | 33.99 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.1 | 0 | 34.71 | 64 | 64 | 74.33 | 72.04 | 64.04 | 0 | 76.71 | 1.86 | 73.87 | 39.44 | 79.58 | 15.17 | 90.63 | 110 | 0 | 14994 | 73.52 | 101.86 | 161.93 | 158.34 | 160.74 | 0 | 21.15 | 47.5 | 11755 | 75.47 | 38.68 | 33.99 | 4.9 | 38.68 | 0 | 609 | 336.6 | 461.5 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 441.5 | 242 | 0 | 237 | 76.78 | 14997 | 14994 | 314
03/26/22 10:06:16.222 | 573.2346 | 1366.7201 | 53.184 | 43.149 | 10.035 | 29.5235 | 50.652 | 0 | 1789.0294 | 70.8772 | 62.5628 | 8.3144 | 27.9845 | 68.1541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.967 | 460.95 | 457.92 | 461.92 | 322.26 | 347.35 | 324.95 | 242.97 | 0.42386 | 3.5303 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6904745.0747 | 7465505.8487 | 7465505.8487 | 62.4305 | 62.3412 | 1.0019 | 0.99904 | 684153.7897 | 894890.0758 | 460.2634 | 0.50913 | 0 | 0 | 29.5235 | 27.9845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.018028 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 376.4195 | 1367.8686 | 51.5815 | 44.996 | 31.222 | 1788.0503 | 58.5904 | 26.7322 | #NV | #NV | #NV | #NV | #NV | 64.0624 | 2.5284 | 1.1946 | 3.1039 | 4.5904 | 1.9039 | #NV | 0 | 100 | 438.1 | 314 | 79.65 | 90.75 | 76.24 | 240.7 | 3 | 75.5 | 38.67 | 4 | 33.98 | 43.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.15 | 0 | 34.7 | 64 | 64 | 74.38 | 72.07 | 64.16 | 0 | 76.24 | 1.86 | 73.9 | 39.43 | 79.67 | 15.26 | 90.77 | 110 | 0 | 14976 | 73.36 | 101.93 | 162.42 | 158.72 | 161.18 | 0 | 21.22 | 47.4 | 11760 | 75.51 | 38.67 | 33.98 | 4.89 | 38.67 | 0 | 609 | 330.5 | 461.5 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 441.9 | 238.6 | 0 | 233.8 | 76.85 | 14980 | 14976 | 314
03/26/22 10:06:21.222 | 571.9061 | 1364.6196 | 53.1374 | 43.1114 | 10.026 | 29.7315 | 50.6476 | 0 | 1793.8756 | 71.0301 | 62.7209 | 8.3092 | 27.4704 | 68.1545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.97 | 460.92 | 457.93 | 461.89 | 322.38 | 347.42 | 325.21 | 243.09 | 0.42505 | 3.1445 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6888859.7185 | 7478974.1077 | 7478974.1077 | 62.4306 | 62.3403 | 1.002 | 0.99903 | 683057.3919 | 897019.2153 | 460.2467 | 0.50335 | 0 | 0 | 29.7315 | 27.4704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.018017 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 379.3289 | 1367.8322 | 51.5857 | 44.9491 | 31.1976 | 1788.1105 | 58.6335 | 26.748 | #NV | #NV | #NV | #NV | #NV | 64.1468 | 2.5291 | 1.1988 | 3.0675 | 4.5879 | 1.9084 | #NV | 0 | 100 | 440.7 | 312 | 79.63 | 90.83 | 76.64 | 236.9 | 3 | 75.5 | 38.68 | 4 | 33.99 | 43.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.17 | 0 | 34.71 | 64 | 64 | 74.45 | 72.12 | 64.25 | 0 | 76.64 | 1.86 | 73.92 | 39.44 | 79.65 | 15.3 | 90.83 | 110 | 0 | 14961 | 73.21 | 101.98 | 162.85 | 159.15 | 161.65 | 0 | 21.44 | 47.66 | 11765 | 75.53 | 38.69 | 34 | 4.87 | 38.69 | 0 | 609 | 332.4 | 461.7 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440.1 | 243.2 | 0 | 238.3 | 76.54 | 14963 | 14961 | 313
03/26/22 10:06:26.221 | 572.0939 | 1365.8117 | 53.1112 | 43.0897 | 10.0215 | 30.0484 | 50.6417 | 0 | 1794.3607 | 71.1113 | 62.8043 | 8.3069 | 27.0119 | 68.1553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9701 | 460.9201 | 457.9301 | 461.8901 | 322.3801 | 347.4201 | 325.2101 | 243.0901 | 0.42491 | 3.1757 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6891500.1734 | 7479595.3428 | 7479595.3428 | 62.4306 | 62.3396 | 1.002 | 0.99902 | 683702.1759 | 897536.0209 | 460.2467 | 0.50335 | 0 | 0 | 30.0484 | 27.0119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.01803 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 382.2794 | 1367.8068 | 51.5888 | 44.9005 | 31.1741 | 1788.1697 | 58.6783 | 26.7625 | #NV | #NV | #NV | #NV | #NV | 64.2332 | 2.5263 | 1.202 | 3.0268 | 4.5994 | 1.9112 | #NV | 0 | 100 | 439 | 314 | 79.67 | 90.87 | 76.35 | 237.8 | 3 | 75.53 | 38.74 | 4 | 34.05 | 43.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.25 | 0 | 34.76 | 64 | 64 | 74.5 | 72.16 | 64.41 | 0 | 76.35 | 1.86 | 73.97 | 39.49 | 79.67 | 15.34 | 90.87 | 110 | 0 | 14953 | 73.08 | 102 | 163.28 | 159.55 | 162.08 | 0 | 21.52 | 47.51 | 11770 | 75.53 | 38.74 | 34.06 | 4.82 | 38.74 | 0 | 609 | 332.5 | 461.6 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 441.1 | 238.7 | 0 | 233.8 | 76.71 | 14953 | 14953 | 313
03/26/22 10:06:31.221 | 572.6361 | 1367.6181 | 53.0398 | 43.0223 | 10.0175 | 30.057 | 50.6522 | 0 | 1786.3973 | 71.3469 | 63.0387 | 8.3082 | 27.2603 | 68.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.975 | 460.92 | 457.93 | 461.86 | 321.67 | 346.6 | 324.46 | 242.51 | 0.4235 | 3.6903 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6898049.1647 | 7447501.1699 | 7447501.1699 | 62.4308 | 62.3379 | 1.002 | 0.99899 | 684609.3947 | 893532.4317 | 460.2367 | 0.50119 | 0 | 0 | 30.057 | 27.2603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.018032 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 385.2556 | 1367.8082 | 51.5909 | 44.8504 | 31.1462 | 1788.183 | 58.7248 | 26.7817 | #NV | #NV | #NV | #NV | #NV | 64.3218 | 2.5256 | 1.2042 | 2.9821 | 4.5949 | 1.9136 | #NV | 0 | 100 | 440.9 | 313 | 79.75 | 90.91 | 76.64 | 236.9 | 3 | 75.56 | 38.8 | 4 | 34.1 | 43.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.35 | 0 | 34.8 | 64 | 64 | 74.6 | 72.22 | 64.44 | 0 | 76.64 | 1.86 | 74.03 | 39.53 | 79.73 | 15.33 | 90.91 | 110 | 0 | 14950 | 72.96 | 102.03 | 163.69 | 159.97 | 162.49 | 0 | 21.52 | 47.53 | 11775 | 75.58 | 38.8 | 34.1 | 4.8 | 38.8 | 0 | 610 | 329.1 | 461.8 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440.9 | 241.8 | 0 | 236.9 | 76.68 | 14950 | 14950 | 312
03/26/22 10:06:36.222 | 573.9915 | 1369.7186 | 53.0065 | 42.9778 | 10.0287 | 30.0672 | 50.6505 | 0 | 1785.7006 | 71.4911 | 63.1697 | 8.3214 | 27.2043 | 68.1785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.975 | 460.95 | 457.97 | 461.88 | 321.09 | 345.91 | 323.83 | 242.04 | 0.42168 | 3.795 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6914321.0181 | 7453466.8148 | 7453466.8148 | 62.4309 | 62.3371 | 1.002 | 0.99898 | 685623.3659 | 893130.2685 | 460.2667 | 0.49899 | 0 | 0 | 30.0672 | 27.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.018028 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 388.272 | 1367.8175 | 51.5917 | 44.7985 | 31.1205 | 1788.1972 | 58.7731 | 26.798 | #NV | #NV | #NV | #NV | #NV | 64.4128 | 2.5293 | 1.2051 | 2.9322 | 4.5829 | 1.9149 | #NV | 0 | 100 | 441 | 314 | 79.8 | 90.95 | 76.47 | 236 | 3 | 75.61 | 38.84 | 4 | 34.14 | 43.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.4 | 0 | 34.84 | 64 | 64 | 74.65 | 72.26 | 64.54 | 0 | 76.47 | 1.86 | 74.06 | 39.57 | 79.78 | 15.35 | 90.95 | 110 | 0 | 14949 | 72.82 | 102.03 | 164.09 | 160.33 | 162.89 | 0 | 21.59 | 47.38 | 11780 | 75.59 | 38.85 | 34.15 | 4.78 | 38.85 | 0 | 609 | 332.4 | 461.7 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 439.3 | 241.9 | 0 | 236.9 | 76.4 | 14948 | 14949 | 311
03/26/22 10:06:41.221 | 574.798 | 1367.5871 | 52.9784 | 42.923 | 10.0553 | 31.1068 | 50.6662 | 0 | 1786.3302 | 71.6629 | 63.3133 | 8.3496 | 25.9527 | 68.1859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.978 | 460.97 | 458 | 461.87 | 320.62 | 345.29 | 323.28 | 241.63 | 0.42037 | 3.5262 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6924913.8402 | 7482213.6203 | 7482213.6203 | 62.431 | 62.3359 | 1.002 | 0.99896 | 684596.4823 | 893474.8893 | 460.28 | 0.49535 | 0 | 0 | 31.1068 | 25.9527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.018027 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 391.2952 | 1367.8157 | 51.5921 | 44.746 | 31.1005 | 1788.2035 | 58.8222 | 26.8077 | #NV | #NV | #NV | #NV | #NV | 64.5048 | 2.5288 | 1.2055 | 2.8793 | 4.5787 | 1.9151 | #NV | 0 | 100 | 440.2 | 312 | 79.93 | 90.99 | 76.56 | 234 | 3 | 75.69 | 38.86 | 4 | 34.16 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.52 | 0 | 34.88 | 64 | 64 | 74.73 | 72.31 | 64.63 | 0 | 76.56 | 1.86 | 74.14 | 39.61 | 79.9 | 15.3 | 90.99 | 110 | 0 | 14951 | 72.72 | 102.03 | 164.45 | 160.66 | 163.24 | 0 | 21.61 | 47.38 | 11785 | 75.69 | 38.86 | 34.16 | 4.79 | 38.86 | 0 | 610 | 336.1 | 461.8 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 441.5 | 239.2 | 0 | 234.3 | 76.78 | 14949 | 14951 | 313
03/26/22 10:06:46.222 | 575.7666 | 1367.8452 | 52.9703 | 42.8999 | 10.0703 | 31.0178 | 50.6513 | 0 | 1784.8077 | 71.7403 | 63.3751 | 8.3652 | 26.3239 | 68.1813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.978 | 460.97 | 458 | 461.87 | 320.62 | 345.29 | 323.28 | 241.63 | 0.41967 | 3.5513 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6936464.4821 | 7490137.9277 | 7490137.9277 | 62.4311 | 62.3354 | 1.002 | 0.99896 | 684725.9956 | 892707.9468 | 460.28 | 0.49535 | 0 | 0 | 31.0178 | 26.3239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.01803 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 394.3458 | 1367.8212 | 51.5917 | 44.6923 | 31.0851 | 1788.204 | 58.8726 | 26.8128 | #NV | #NV | #NV | #NV | #NV | 64.5987 | 2.5278 | 1.2051 | 2.8221 | 4.5783 | 1.9147 | #NV | 0 | 100 | 443.1 | 312 | 79.98 | 91.05 | 77.06 | 237.4 | 3 | 75.72 | 38.9 | 4 | 34.2 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.6 | 0 | 34.9 | 64 | 64 | 74.85 | 72.39 | 64.68 | 0 | 76.8 | 1.86 | 74.19 | 39.64 | 79.98 | 15.32 | 91.05 | 110 | 0 | 14956 | 72.64 | 102.03 | 164.82 | 161.01 | 163.62 | 0 | 21.58 | 47.35 | 11789 | 75.72 | 38.9 | 34.2 | 4.75 | 38.9 | 0 | 609 | 334.5 | 461.6 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 442.3 | 243.8 | 0 | 238.9 | 76.92 | 14955 | 14956 | 312
03/26/22 10:06:51.221 | 577.2684 | 1368.3871 | 52.9644 | 42.8684 | 10.096 | 30.8191 | 50.6381 | 0 | 1786.1031 | 71.8613 | 63.4698 | 8.3915 | 26.6038 | 68.1335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9801 | 461.0101 | 458.0301 | 461.8701 | 320.3801 | 344.9401 | 322.9301 | 241.4101 | 0.41819 | 3.4183 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6954316.5798 | 7516632.7349 | 7516632.7349 | 62.4311 | 62.3347 | 1.002 | 0.99895 | 684938.079 | 893309.6129 | 460.3034 | 0.49388 | 0 | 0 | 30.8191 | 26.6038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.018032 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 397.4278 | 1367.8275 | 51.5907 | 44.6374 | 31.0663 | 1788.203 | 58.9241 | 26.8242 | #NV | #NV | #NV | #NV | #NV | 64.6942 | 2.5278 | 1.2039 | 2.7598 | 4.5788 | 1.9129 | #NV | 0 | 100 | 444.4 | 312 | 80.1 | 91.09 | 77.29 | 235.4 | 3 | 75.8 | 38.93 | 4 | 34.23 | 43.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.68 | 0 | 34.94 | 64 | 64 | 74.93 | 72.44 | 64.7 | 0 | 77.29 | 1.86 | 74.24 | 39.67 | 80.1 | 15.3 | 91.1 | 110 | 0 | 14967 | 72.54 | 102.05 | 165.18 | 161.35 | 163.98 | 0 | 21.66 | 47.32 | 11794 | 75.8 | 38.93 | 34.23 | 4.76 | 38.93 | 0 | 609 | 334.6 | 461.6 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 442.3 | 241 | 0 | 236 | 76.92 | 14963 | 14967 | 312
03/26/22 10:06:56.221 | 578.3093 | 1366.0491 | 52.9707 | 42.8426 | 10.128 | 29.6166 | 50.6313 | 0 | 1784.8697 | 72.001 | 63.5772 | 8.4238 | 27.9461 | 68.1723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.979 | 461.02 | 458.03 | 461.88 | 320.43 | 345 | 322.96 | 241.45 | 0.41751 | 3.2002 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6965711.1627 | 7544217.9689 | 7544217.9689 | 62.4312 | 62.3338 | 1.002 | 0.99894 | 683826.9131 | 892721.1027 | 460.31 | 0.49532 | 0 | 0 | 29.6166 | 27.9461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.018035 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 400.5351 | 1367.8078 | 51.589 | 44.5813 | 31.0383 | 1788.1988 | 58.9768 | 26.847 | #NV | #NV | #NV | #NV | #NV | 64.7913 | 2.5278 | 1.2018 | 2.6919 | 4.5815 | 1.9097 | #NV | 0 | 100 | 446.2 | 312 | 80.18 | 91.16 | 77.6 | 236 | 3 | 75.85 | 38.97 | 4 | 34.25 | 43.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.78 | 0 | 34.98 | 64 | 64 | 75.02 | 72.5 | 64.74 | 0 | 77.6 | 1.86 | 74.31 | 39.71 | 80.2 | 15.3 | 91.16 | 110 | 0 | 14976 | 72.48 | 102.05 | 165.52 | 161.72 | 164.31 | 0 | 21.82 | 47.82 | 11799 | 75.86 | 38.97 | 34.26 | 4.74 | 38.97 | 0 | 609 | 334 | 461.5 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 444.2 | 245 | 0 | 240 | 77.25 | 14973 | 14976 | 312
03/26/22 10:07:01.221 | 579.2273 | 1366.5343 | 52.9767 | 42.8362 | 10.1405 | 29.3602 | 50.6309 | 0 | 1786.6605 | 72.0552 | 63.6186 | 8.4366 | 28.411 | 68.1867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9791 | 461.0201 | 458.0301 | 461.8801 | 320.4301 | 345.0001 | 322.9601 | 241.4501 | 0.41685 | 3.0814 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6976510.6433 | 7563655.2167 | 7563655.2167 | 62.4312 | 62.3334 | 1.002 | 0.99893 | 684069.5119 | 893613.1517 | 460.3101 | 0.49532 | 0 | 0 | 29.3602 | 28.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.01802 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 403.6543 | 1367.7884 | 51.5871 | 44.5247 | 31.0101 | 1788.2035 | 59.0299 | 26.8706 | #NV | #NV | #NV | #NV | #NV | 64.8891 | 2.524 | 1.1992 | 2.6197 | 4.5795 | 1.9052 | #NV | 0 | 100 | 444.1 | 312 | 80.25 | 91.22 | 77.23 | 234.4 | 3 | 75.9 | 38.98 | 4 | 34.27 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.88 | 0 | 34.99 | 64 | 64 | 75.13 | 72.57 | 64.82 | 0 | 77.23 | 1.86 | 74.37 | 39.73 | 80.3 | 15.31 | 91.24 | 110 | 0 | 14993 | 72.4 | 102.1 | 165.84 | 162 | 164.66 | 0 | 22.43 | 48.57 | 11804 | 75.91 | 38.98 | 34.27 | 4.77 | 38.98 | 0 | 609 | 331.5 | 461.5 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 446.1 | 243.6 | 0 | 238.7 | 77.58 | 14988 | 14993 | 312
03/26/22 10:07:06.221 | 582.8032 | 1371.2359 | 53.0026 | 42.8345 | 10.1682 | 30.4616 | 50.6631 | 0 | 1792.0692 | 72.1834 | 63.7173 | 8.4661 | 27.14 | 68.1875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 461 | 458.05 | 461.92 | 322.24 | 347.07 | 324.88 | 242.95 | 0.41686 | 3.0499 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7020480.7032 | 7611303.2201 | 7611303.2201 | 62.4311 | 62.3326 | 1.002 | 0.99892 | 686422.0136 | 896309.5475 | 460.3234 | 0.49386 | 0 | 0 | 30.4616 | 27.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.01802 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 406.7908 | 1367.7882 | 51.5851 | 44.4679 | 30.9826 | 1788.2346 | 59.0834 | 26.8932 | #NV | #NV | #NV | #NV | #NV | 64.9874 | 2.5237 | 1.1965 | 2.5434 | 4.5846 | 1.9 | #NV | 0 | 100 | 446.3 | 314 | 80.38 | 91.3 | 77.62 | 245.5 | 3 | 75.97 | 38.98 | 4 | 34.27 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 77.95 | 0 | 34.99 | 64 | 64 | 75.15 | 72.59 | 64.87 | 0 | 77.62 | 1.86 | 74.42 | 39.73 | 80.38 | 15.33 | 91.3 | 110 | 0 | 15015 | 72.32 | 102.12 | 166.15 | 162.3 | 164.98 | 0 | 22.58 | 48.13 | 11809 | 75.97 | 38.97 | 34.26 | 4.78 | 38.97 | 0 | 609 | 328.7 | 461.7 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 449.9 | 239.1 | 0 | 234.2 | 78.24 | 15012 | 15015 | 313
03/26/22 10:07:11.220 | 581.6722 | 1366.0337 | 53.0343 | 42.8471 | 10.1872 | 30.7042 | 50.659 | 0 | 1787.2334 | 72.2802 | 63.7933 | 8.4868 | 26.2943 | 68.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9871 | 460.9901 | 458.0701 | 461.9301 | 323.3601 | 348.2801 | 326.1901 | 243.9001 | 0.41931 | 2.9496 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7007020.0443 | 7608225.4923 | 7608225.4923 | 62.4311 | 62.332 | 1.002 | 0.99891 | 683816.4937 | 893884.1168 | 460.3301 | 0.49095 | 0 | 0 | 30.7042 | 26.2943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.01803 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 409.9204 | 1367.7598 | 51.5831 | 44.4112 | 30.9601 | 1788.2429 | 59.1372 | 26.9088 | #NV | #NV | #NV | #NV | #NV | 65.086 | 2.507 | 1.1939 | 2.4635 | 4.5858 | 1.8948 | #NV | 0 | 100 | 451.5 | 315 | 80.55 | 91.4 | 78.52 | 241 | 3 | 76.07 | 38.97 | 4 | 34.26 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 78.15 | 0 | 34.99 | 64 | 64 | 75.3 | 72.69 | 64.91 | 0 | 78.52 | 1.87 | 74.55 | 39.73 | 80.52 | 15.31 | 91.4 | 110 | 0 | 15048 | 72.28 | 102.15 | 166.49 | 162.63 | 165.27 | 0 | 22.4 | 47.72 | 11814 | 76.09 | 38.97 | 34.26 | 4.8 | 38.97 | 0 | 609 | 341.3 | 461.3 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450.4 | 249 | 0 | 243.9 | 78.33 | 15039 | 15048 | 314
03/26/22 10:07:16.221 | 582.6407 | 1367.262 | 53.0564 | 42.8599 | 10.1965 | 30.9484 | 50.6573 | 0 | 1783.6155 | 72.3333 | 63.8355 | 8.4977 | 26.0936 | 68.1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9871 | 460.9701 | 458.0801 | 461.9301 | 324.8101 | 349.8501 | 327.8301 | 245.1001 | 0.42067 | 3.1982 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7018828.9566 | 7603910.1902 | 7603910.1902 | 62.431 | 62.3318 | 1.002 | 0.99891 | 684487.5344 | 892554.5568 | 460.3268 | 0.48806 | 0 | 0 | 30.9484 | 26.0936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.018039 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 413.0488 | 1367.7418 | 51.5814 | 44.3548 | 30.9378 | 1788.2189 | 59.191 | 26.9232 | #NV | #NV | #NV | #NV | #NV | 65.1846 | 2.498 | 1.1916 | 2.3804 | 4.5937 | 1.8897 | #NV | 0 | 100 | 452.9 | 316 | 80.65 | 91.54 | 78.9 | 243.5 | 3 | 76.15 | 38.93 | 4 | 34.23 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 78.33 | 0 | 34.96 | 64 | 64 | 75.45 | 72.79 | 64.97 | 0 | 78.9 | 1.87 | 74.66 | 39.7 | 80.68 | 15.37 | 91.56 | 110 | 0 | 15077 | 72.22 | 102.17 | 166.78 | 162.9 | 165.61 | 0 | 22.42 | 47.56 | 11819 | 76.16 | 38.93 | 34.23 | 4.86 | 38.93 | 0 | 609 | 344.3 | 461.4 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454.2 | 252 | 0 | 246.9 | 78.99 | 15069 | 15077 | 316
03/26/22 10:07:21.220 | 582.1612 | 1364.6608 | 53.0831 | 42.877 | 10.2061 | 30.9436 | 50.646 | 0 | 1783.0684 | 72.3916 | 63.8818 | 8.5097 | 26.0887 | 68.1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.99 | 460.98 | 458.12 | 461.96 | 326.59 | 351.74 | 329.81 | 246.57 | 0.42354 | 3.0899 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7013070.918 | 7610541.736 | 7610541.736 | 62.431 | 62.3313 | 1.002 | 0.99891 | 683127.2284 | 891793.1289 | 460.3534 | 0.48513 | 0 | 0 | 30.9436 | 26.0887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.018038 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 416.156 | 1367.7518 | 51.5803 | 44.2993 | 30.9197 | 1788.182 | 59.2441 | 26.9343 | #NV | #NV | #NV | #NV | #NV | 65.2825 | 2.4865 | 1.19 | 2.2959 | 4.6105 | 1.8861 | #NV | 0 | 100 | 456.7 | 313 | 80.88 | 91.7 | 79.43 | 246.8 | 3 | 76.31 | 38.89 | 4 | 34.19 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 78.53 | 0 | 34.93 | 64 | 64 | 75.65 | 72.92 | 65 | 0 | 79.43 | 1.88 | 74.78 | 39.66 | 80.88 | 15.42 | 91.71 | 110 | 0 | 15121 | 72.16 | 102.22 | 167.09 | 163.2 | 165.93 | 0 | 22.45 | 47.41 | 11824 | 76.29 | 38.89 | 34.18 | 4.92 | 38.89 | 0 | 609 | 345.8 | 461.3 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457.4 | 251.1 | 0 | 246 | 79.55 | 15113 | 15121 | 314
03/26/22 10:07:26.220 | 581.7051 | 1362.6325 | 53.1136 | 42.8982 | 10.2155 | 30.2331 | 50.6505 | 0 | 1780.5602 | 72.4517 | 63.9297 | 8.522 | 26.9723 | 68.1372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9901 | 460.9801 | 458.1201 | 461.9601 | 326.5901 | 351.7401 | 329.8101 | 246.5701 | 0.42387 | 3.0852 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7007090.6241 | 7609964.644 | 7609964.644 | 62.4309 | 62.331 | 1.002 | 0.9989 | 682072.0869 | 890571.2196 | 460.3534 | 0.48513 | 0 | 0 | 30.2331 | 26.9723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016242 | 0.018042 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 419.2294 | 1367.7463 | 51.5799 | 44.2451 | 30.9 | 1788.1461 | 59.2966 | 26.9483 | #NV | #NV | #NV | #NV | #NV | 65.3793 | 2.4968 | 1.1896 | 2.211 | 4.6446 | 1.8843 | #NV | 0 | 100 | 461.7 | 316 | 81.05 | 91.87 | 80.3 | 248.9 | 3 | 76.4 | 38.85 | 4 | 34.15 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 78.7 | 0 | 34.89 | 64 | 64 | 75.85 | 73.05 | 65.08 | 0 | 80.3 | 1.88 | 74.9 | 39.62 | 81.05 | 15.49 | 91.89 | 110 | 0 | 15164 | 72.13 | 102.25 | 167.41 | 163.52 | 166.22 | 0 | 22.43 | 47.27 | 11829 | 76.4 | 38.84 | 34.14 | 4.97 | 38.84 | 0 | 609 | 349 | 461.2 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461.8 | 255.3 | 0 | 250.2 | 80.31 | 15154 | 15164 | 316
03/26/22 10:07:31.220 | 584.0762 | 1365.9149 | 53.1643 | 42.9338 | 10.2305 | 30.3825 | 50.6491 | 0 | 1783.0943 | 72.5445 | 64.0037 | 8.5408 | 26.5383 | 68.1273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.991 | 460.95 | 458.13 | 461.94 | 331.09 | 356.38 | 334.65 | 250.17 | 0.42832 | 3.0709 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7035582.8782 | 7638681.6773 | 7638681.6773 | 62.4308 | 62.3303 | 1.002 | 0.99889 | 683751.5912 | 891795.1254 | 460.34 | 0.48008 | 0 | 0 | 30.3825 | 26.5383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.018041 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 422.2694 | 1367.7425 | 51.5804 | 44.1922 | 30.8792 | 1788.1101 | 59.3481 | 26.9604 | #NV | #NV | #NV | #NV | #NV | 65.4748 | 2.5035 | 1.1902 | 2.1264 | 4.674 | 1.8844 | #NV | 0 | 100 | 464.6 | 314 | 81.18 | 92.05 | 80.8 | 252 | 3 | 76.48 | 38.81 | 4 | 34.11 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 78.88 | 0 | 34.86 | 64 | 64 | 76 | 73.15 | 65.11 | 0 | 80.8 | 1.89 | 75 | 39.6 | 81.18 | 15.57 | 92.08 | 110 | 0 | 15200 | 72.08 | 102.32 | 167.69 | 163.78 | 166.51 | 0 | 22.59 | 47.56 | 11834 | 76.48 | 38.81 | 34.11 | 5 | 38.81 | 0 | 609 | 354.8 | 461 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465.4 | 257.1 | 0 | 251.9 | 80.94 | 15196 | 15200 | 314
03/26/22 10:07:36.220 | 586.1434 | 1369.2386 | 53.2002 | 42.9583 | 10.2419 | 30.3864 | 50.6553 | 0 | 1784.1213 | 72.6083 | 64.0539 | 8.5544 | 26.9402 | 68.1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 460.92 | 458.13 | 461.93 | 333.48 | 358.92 | 337.27 | 252.12 | 0.43013 | 3.4049 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7060458.1814 | 7655549.4523 | 7655549.4523 | 62.4307 | 62.3299 | 1.002 | 0.99889 | 685413.8416 | 892304.2931 | 460.3267 | 0.4772 | 0 | 0 | 30.3864 | 26.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.018041 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 425.2789 | 1367.7372 | 51.5822 | 44.1414 | 30.8564 | 1788.0694 | 59.3984 | 26.9788 | #NV | #NV | #NV | #NV | #NV | 65.5686 | 2.5033 | 1.1924 | 2.0441 | 4.6844 | 1.8879 | #NV | 0 | 100 | 467 | 315 | 81.45 | 92.23 | 81.27 | 252.7 | 3 | 76.64 | 38.74 | 4 | 34.05 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 79.1 | 0 | 34.81 | 64 | 64 | 76.18 | 73.25 | 65.15 | 0 | 81.27 | 1.89 | 75.16 | 39.54 | 81.45 | 15.6 | 92.25 | 110 | 0 | 15234 | 72.04 | 102.39 | 167.99 | 164.08 | 166.82 | 0 | 22.74 | 47.43 | 11840 | 76.65 | 38.74 | 34.05 | 5.05 | 38.74 | 0 | 608 | 355.7 | 460.8 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 467 | 257.9 | 0 | 252.7 | 81.22 | 15227 | 15234 | 315
03/26/22 10:07:41.220 | 586.44 | 1369.7083 | 53.2115 | 42.9659 | 10.2456 | 30.1393 | 50.6524 | 0 | 1784.9161 | 72.6288 | 64.07 | 8.5587 | 27.3212 | 68.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 460.9201 | 458.1301 | 461.9301 | 333.4801 | 358.9201 | 337.2701 | 252.1201 | 0.42992 | 3.4106 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7064021.0687 | 7658556.7666 | 7658556.7666 | 62.4307 | 62.3298 | 1.002 | 0.99889 | 685635.7822 | 892422.3028 | 460.3267 | 0.4772 | 0 | 0 | 30.1393 | 27.3212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.018036 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 428.263 | 1367.7351 | 51.585 | 44.092 | 30.8329 | 1788.0511 | 59.4478 | 26.999 | #NV | #NV | #NV | #NV | #NV | 65.6612 | 2.5015 | 1.1956 | 1.9626 | 4.6903 | 1.8932 | #NV | 0 | 100 | 469.3 | 316 | 81.65 | 92.43 | 81.62 | 252.9 | 3 | 76.78 | 38.67 | 4 | 33.98 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 79.25 | 0 | 34.74 | 64 | 64 | 76.35 | 73.38 | 65.24 | 0 | 81.62 | 1.9 | 75.26 | 39.47 | 81.67 | 15.64 | 92.47 | 110 | 0 | 15264 | 72.01 | 102.46 | 168.3 | 164.37 | 167.13 | 0 | 22.61 | 46.94 | 11844 | 76.8 | 38.67 | 33.98 | 5.13 | 38.67 | 0 | 608 | 355.4 | 460.7 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470.1 | 261 | 0 | 255.8 | 81.76 | 15257 | 15264 | 319
03/26/22 10:07:46.221 | 587.4143 | 1369.1354 | 53.2621 | 42.9988 | 10.2632 | 29.0719 | 50.6557 | 0 | 1788.8952 | 72.7222 | 64.1439 | 8.5783 | 28.9929 | 68.1483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9821 | 460.8801 | 458.1101 | 461.8901 | 335.9801 | 361.5301 | 339.9501 | 254.1101 | 0.43259 | 3.159 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7074627.6262 | 7694712.0089 | 7694712.0089 | 62.4306 | 62.3292 | 1.002 | 0.99888 | 685615.5522 | 894367.0318 | 460.2934 | 0.47434 | 0 | 0 | 29.0719 | 28.9929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.018037 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 431.2144 | 1367.7431 | 51.5891 | 44.0445 | 30.8059 | 1788.0647 | 59.4962 | 27.0245 | #NV | #NV | #NV | #NV | #NV | 65.7525 | 2.5037 | 1.2001 | 1.8829 | 4.6891 | 1.9012 | #NV | 0 | 100 | 471.6 | 316 | 81.67 | 92.61 | 82.05 | 254.6 | 3 | 76.78 | 38.61 | 4 | 33.93 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 79.4 | 0 | 34.68 | 64 | 64 | 76.45 | 73.44 | 65.34 | 0 | 82.05 | 1.91 | 75.35 | 39.4 | 81.73 | 15.81 | 92.63 | 110 | 0 | 15291 | 71.98 | 102.53 | 168.56 | 164.62 | 167.39 | 0 | 22.52 | 46.86 | 11849 | 76.83 | 38.61 | 33.93 | 5.16 | 38.61 | 0 | 608 | 359.1 | 460.7 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471.6 | 259.8 | 0 | 254.6 | 82.02 | 15282 | 15291 | 316
03/26/22 10:07:51.220 | 587.8297 | 1368.098 | 53.3046 | 43.0244 | 10.2802 | 29.8979 | 50.6456 | 0 | 1790.5106 | 72.8054 | 64.2088 | 8.5965 | 28.1312 | 68.1566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9821 | 460.8801 | 458.1201 | 461.8901 | 338.4801 | 364.1901 | 342.6301 | 256.1301 | 0.43572 | 2.965 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7080241.6747 | 7721794.2298 | 7721794.2298 | 62.4305 | 62.3286 | 1.0019 | 0.99887 | 684838.4433 | 895485.7861 | 460.2967 | 0.47288 | 0 | 0 | 29.8979 | 28.1312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.018028 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 434.1306 | 1367.7826 | 51.5945 | 43.9991 | 30.7813 | 1788.1065 | 59.5435 | 27.0464 | #NV | #NV | #NV | #NV | #NV | 65.8421 | 2.4521 | 1.2056 | 1.8066 | 4.6771 | 1.9121 | #NV | 0 | 100 | 474.5 | 315 | 81.95 | 92.79 | 82.52 | 256.7 | 3 | 76.97 | 38.55 | 4 | 33.86 | 43.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 79.55 | 0 | 34.63 | 64 | 64 | 76.65 | 73.56 | 65.41 | 0 | 82.52 | 1.91 | 75.43 | 39.35 | 81.98 | 15.84 | 92.81 | 110 | 0 | 15324 | 71.96 | 102.61 | 168.85 | 164.92 | 167.7 | 0 | 22.82 | 47.28 | 11854 | 76.97 | 38.53 | 33.85 | 5.18 | 38.53 | 0 | 608 | 363.3 | 460.7 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.3 | 263.7 | 0 | 258.4 | 82.66 | 15320 | 15324 | 320
03/26/22 10:07:56.220 | 588.7427 | 1367.1691 | 53.3562 | 43.0519 | 10.3043 | 30.1122 | 50.6594 | 0 | 1790.4642 | 72.9109 | 64.2903 | 8.6206 | 27.3961 | 68.1797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.983 | 460.86 | 458.13 | 461.88 | 340.99 | 366.93 | 345.41 | 258.17 | 0.43851 | 2.9918 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7091311.8008 | 7737222.5829 | 7737222.5829 | 62.4304 | 62.328 | 1.0019 | 0.99887 | 684487.7049 | 895135.9093 | 460.29 | 0.46927 | 0 | 0 | 30.1122 | 27.3961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.018027 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 436.9897 | 1367.7939 | 51.6018 | 43.9564 | 30.7533 | 1788.1276 | 59.5891 | 27.0716 | #NV | #NV | #NV | #NV | #NV | 65.9296 | 2.4464 | 1.2123 | 1.7357 | 4.6809 | 1.9264 | #NV | 0 | 100 | 477.5 | 319 | 82.08 | 92.97 | 83.04 | 258.9 | 3 | 77.05 | 38.45 | 4 | 33.78 | 43.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 79.67 | 0 | 34.54 | 64 | 64 | 76.77 | 73.64 | 65.45 | 0 | 83.04 | 1.92 | 75.53 | 39.26 | 82.13 | 15.93 | 93.01 | 110 | 0 | 15364 | 71.94 | 102.71 | 169.18 | 165.2 | 168 | 0 | 23.03 | 47.28 | 11859 | 77.08 | 38.44 | 33.76 | 5.24 | 38.44 | 0 | 608 | 365 | 460.6 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 477.5 | 265.7 | 0 | 260.4 | 83.04 | 15355 | 15364 | 318
03/26/22 10:08:01.220 | 589.8629 | 1368.9858 | 53.3781 | 43.062 | 10.3161 | 30.4965 | 50.6573 | 0 | 1790.1493 | 72.9577 | 64.3262 | 8.6315 | 26.9226 | 68.1797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.983 | 460.86 | 458.13 | 461.88 | 340.99 | 366.93 | 345.41 | 258.17 | 0.43768 | 3.0173 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7105122.2481 | 7748656.4372 | 7748656.4372 | 62.4303 | 62.3277 | 1.0019 | 0.99886 | 685021.5526 | 895434.6405 | 460.29 | 0.46927 | 0 | 0 | 30.4965 | 26.9226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.018026 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 439.8271 | 1367.8076 | 51.61 | 43.915 | 30.7323 | 1788.1486 | 59.6341 | 27.087 | #NV | #NV | #NV | #NV | #NV | 66.0161 | 2.4462 | 1.2193 | 1.6659 | 4.6814 | 1.942 | #NV | 0 | 100 | 480.2 | 321 | 82.35 | 93.21 | 83.53 | 261.3 | 3 | 77.22 | 38.36 | 4 | 33.69 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 79.85 | 0 | 34.46 | 64 | 64 | 76.93 | 73.75 | 65.49 | 0 | 83.53 | 1.92 | 75.64 | 39.18 | 82.35 | 15.99 | 93.21 | 110 | 0 | 15404 | 71.92 | 102.78 | 169.48 | 165.51 | 168.35 | 0 | 23.1 | 47.16 | 11864 | 77.22 | 38.36 | 33.68 | 5.3 | 38.36 | 0 | 608 | 366.9 | 460.4 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480.5 | 267.3 | 0 | 262 | 83.57 | 15396 | 15404 | 319
03/26/22 10:08:06.220 | 592.0279 | 1369.1406 | 53.429 | 43.083 | 10.346 | 30.682 | 50.6567 | 0 | 1790.9028 | 73.0706 | 64.4124 | 8.6582 | 27.2495 | 68.1549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.982 | 460.77 | 458.03 | 461.81 | 348.35 | 374.95 | 353.35 | 264.07 | 0.44604 | 3.2268 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7131329.1373 | 7777298.4355 | 7777298.4355 | 62.4302 | 62.3269 | 1.0019 | 0.99885 | 685354.9823 | 895663.4142 | 460.2034 | 0.47225 | 0 | 0 | 30.682 | 27.2495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.018023 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 442.6311 | 1367.8053 | 51.6195 | 43.8755 | 30.7161 | 1788.143 | 59.6779 | 27.0984 | #NV | #NV | #NV | #NV | #NV | 66.1009 | 2.4443 | 1.2265 | 1.5996 | 4.6783 | 1.9591 | #NV | 0 | 100 | 484 | 321 | 82.63 | 93.43 | 84.17 | 262.6 | 3 | 77.39 | 38.29 | 4 | 33.63 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 80.1 | 0 | 34.4 | 64 | 64 | 77.15 | 73.88 | 65.56 | 0 | 84.17 | 1.93 | 75.8 | 39.11 | 82.65 | 16.05 | 93.45 | 110 | 0 | 15444 | 71.9 | 102.88 | 169.77 | 165.81 | 168.67 | 0 | 23.32 | 47.35 | 11870 | 77.41 | 38.28 | 33.61 | 5.38 | 38.28 | 0 | 608 | 373 | 460.3 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 484.6 | 269.5 | 0 | 264.1 | 84.28 | 15437 | 15444 | 322
03/26/22 10:08:11.219 | 592.7824 | 1368.7329 | 53.4545 | 43.0922 | 10.3623 | 30.3949 | 50.6514 | 0 | 1790.1339 | 73.1291 | 64.4569 | 8.6722 | 27.4188 | 68.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9821 | 460.7701 | 458.0301 | 461.8101 | 348.3501 | 374.9501 | 353.3501 | 264.0701 | 0.44548 | 3.2169 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7140122.7081 | 7786587.9993 | 7786587.9993 | 62.4302 | 62.3266 | 1.0019 | 0.99885 | 685149.7849 | 895274.7817 | 460.2034 | 0.47225 | 0 | 0 | 30.3949 | 27.4188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.018025 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 445.417 | 1367.8187 | 51.6302 | 43.8375 | 30.6951 | 1788.14 | 59.7213 | 27.1161 | #NV | #NV | #NV | #NV | #NV | 66.185 | 2.4427 | 1.2341 | 1.5349 | 4.6768 | 1.978 | #NV | 0 | 100 | 485.7 | 319 | 82.78 | 93.66 | 84.47 | 266.1 | 3 | 77.48 | 38.21 | 4 | 33.55 | 43.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 80.25 | 0 | 34.32 | 64 | 64 | 77.3 | 74 | 65.66 | 0 | 84.47 | 1.94 | 75.9 | 39.03 | 82.78 | 16.15 | 93.66 | 110 | 0 | 15468 | 71.88 | 102.97 | 170.07 | 166.05 | 168.94 | 0 | 23.58 | 47.35 | 11874 | 77.48 | 38.21 | 33.54 | 5.46 | 38.21 | 0 | 607 | 374 | 460.1 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486.4 | 271 | 0 | 265.6 | 84.59 | 15462 | 15468 | 321
03/26/22 10:08:16.220 | 595.3038 | 1370.3792 | 53.5074 | 43.1092 | 10.3982 | 29.1465 | 50.6629 | 0 | 1792.6886 | 73.2537 | 64.5507 | 8.7029 | 28.8438 | 68.1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9811 | 460.7601 | 458.0001 | 461.7901 | 352.9401 | 379.9201 | 358.2101 | 267.7301 | 0.44974 | 3.227 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7169366.2416 | 7820160.709 | 7820160.709 | 62.4301 | 62.3259 | 1.0019 | 0.99884 | 685943.4447 | 896129.153 | 460.1834 | 0.47445 | 0 | 0 | 29.1465 | 28.8438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.018014 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 448.2144 | 1367.8506 | 51.6413 | 43.7999 | 30.6675 | 1788.1447 | 59.7649 | 27.1413 | #NV | #NV | #NV | #NV | #NV | 66.2695 | 2.4377 | 1.2419 | 1.4676 | 4.6801 | 1.9972 | #NV | 0 | 100 | 488.1 | 320 | 82.88 | 93.85 | 84.71 | 266.8 | 3 | 77.55 | 38.12 | 4 | 33.46 | 43.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 80.4 | 0 | 34.25 | 64 | 64 | 77.43 | 74.08 | 65.73 | 0 | 84.71 | 1.94 | 75.99 | 38.95 | 82.85 | 16.33 | 93.87 | 110 | 0 | 15498 | 71.88 | 103.04 | 170.39 | 166.35 | 169.26 | 0 | 23.7 | 47.09 | 11879 | 77.53 | 38.12 | 33.45 | 5.59 | 38.12 | 0 | 607 | 373.6 | 460.1 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488.4 | 273.6 | 0 | 268.2 | 84.94 | 15491 | 15498 | 323
03/26/22 10:08:21.219 | 596.0144 | 1369.9715 | 53.531 | 43.1162 | 10.4148 | 29.9508 | 50.6687 | 0 | 1795.9348 | 73.3109 | 64.5934 | 8.7175 | 27.8036 | 68.2036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9811 | 460.7601 | 458.0001 | 461.7901 | 352.9401 | 379.9201 | 358.2101 | 267.7301 | 0.4492 | 3.0773 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7178399.9738 | 7846695.5347 | 7846695.5347 | 62.4301 | 62.3255 | 1.0019 | 0.99884 | 685759.0825 | 897906.476 | 460.1834 | 0.47445 | 0 | 0 | 29.9508 | 27.8036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.018007 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 450.9765 | 1367.8681 | 51.6538 | 43.7642 | 30.6441 | 1788.1608 | 59.8076 | 27.1609 | #NV | #NV | #NV | #NV | #NV | 66.3525 | 2.4416 | 1.2495 | 1.404 | 4.702 | 2.0179 | #NV | 0 | 100 | 490.2 | 322 | 82.9 | 94.06 | 85.13 | 266.9 | 3 | 77.55 | 38.04 | 4 | 33.38 | 43.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 80.48 | 0 | 34.18 | 64 | 64 | 77.5 | 74.13 | 65.81 | 0 | 85.13 | 1.95 | 76.04 | 38.88 | 82.9 | 16.52 | 94.08 | 110 | 0 | 15525 | 71.86 | 103.12 | 170.71 | 166.65 | 169.6 | 0 | 23.4 | 46.36 | 11884 | 77.56 | 38.03 | 33.38 | 5.68 | 38.03 | 0 | 607 | 376.2 | 460 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490.2 | 272.3 | 0 | 266.9 | 85.25 | 15518 | 15525 | 322
03/26/22 10:08:26.219 | 597.3489 | 1367.8194 | 53.5805 | 43.1311 | 10.4494 | 30.206 | 50.6687 | 0 | 1792.6576 | 73.4305 | 64.6826 | 8.7479 | 27.3676 | 68.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9801 | 460.7401 | 457.9801 | 461.7801 | 355.2501 | 382.3901 | 360.6401 | 269.5601 | 0.45126 | 3.1229 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7194737.3216 | 7864998.7568 | 7864998.7568 | 62.43 | 62.3246 | 1.0019 | 0.99883 | 684687.0686 | 896516.1932 | 460.1667 | 0.47519 | 0 | 0 | 30.206 | 27.3676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.018005 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 453.7193 | 1367.8804 | 51.6671 | 43.7297 | 30.6171 | 1788.1628 | 59.8497 | 27.1836 | #NV | #NV | #NV | #NV | #NV | 66.4346 | 2.4429 | 1.2569 | 1.341 | 4.7049 | 2.0388 | #NV | 0 | 100 | 492.5 | 320 | 83.13 | 94.24 | 85.62 | 271.7 | 3 | 77.69 | 37.97 | 4 | 33.33 | 43.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 80.7 | 0 | 34.11 | 64 | 64 | 77.75 | 74.29 | 65.82 | 0 | 85.62 | 1.95 | 76.18 | 38.81 | 83.2 | 16.55 | 94.28 | 110 | 0 | 15555 | 71.86 | 103.19 | 171.06 | 166.96 | 169.96 | 0 | 23.42 | 46.36 | 11889 | 77.75 | 37.96 | 33.31 | 5.75 | 37.96 | 0 | 607 | 378.4 | 459.9 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 492.5 | 275.2 | 0 | 269.7 | 85.65 | 15550 | 15555 | 321
03/26/22 10:08:31.220 | 597.814 | 1366.5394 | 53.6067 | 43.1393 | 10.4674 | 30.2195 | 50.6582 | 0 | 1793.6485 | 73.4923 | 64.7287 | 8.7635 | 27.1585 | 68.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9801 | 460.7401 | 457.9801 | 461.7801 | 355.2501 | 382.3901 | 360.6401 | 269.5601 | 0.45091 | 2.9627 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7200305.4641 | 7883017.2784 | 7883017.2784 | 62.4299 | 62.3243 | 1.0019 | 0.99882 | 684045.241 | 897007.4863 | 460.1667 | 0.47519 | 0 | 0 | 30.2195 | 27.1585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.018001 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 456.4354 | 1367.8602 | 51.6815 | 43.6965 | 30.5926 | 1788.1715 | 59.8916 | 27.2037 | #NV | #NV | #NV | #NV | #NV | 66.5162 | 2.4388 | 1.2642 | 1.2796 | 4.7136 | 2.0612 | #NV | 0 | 100 | 493.6 | 323 | 83.33 | 94.48 | 85.84 | 271.6 | 3 | 77.83 | 37.88 | 4 | 33.24 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 80.83 | 0 | 34 | 64 | 64 | 77.9 | 74.37 | 65.86 | 0 | 85.84 | 1.96 | 76.26 | 38.7 | 83.35 | 16.64 | 94.5 | 110 | 0 | 15585 | 71.86 | 103.29 | 171.4 | 167.29 | 170.28 | 0 | 23.59 | 46.54 | 11894 | 77.84 | 37.87 | 33.23 | 5.86 | 37.87 | 0 | 607 | 382.8 | 459.8 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494 | 275.9 | 0 | 270.4 | 85.91 | 15576 | 15585 | 323
03/26/22 10:08:36.220 | 599.4732 | 1367.3445 | 53.6443 | 43.1515 | 10.4928 | 30.2018 | 50.6491 | 0 | 1791.4293 | 73.5799 | 64.7941 | 8.7858 | 26.8488 | 68.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9811 | 460.7201 | 457.9301 | 461.7201 | 359.7201 | 387.0001 | 365.2001 | 273.0301 | 0.45545 | 3.2165 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7220081.8674 | 7893649.2308 | 7893649.2308 | 62.4299 | 62.3237 | 1.0019 | 0.99881 | 684451.9408 | 896196.7545 | 460.1234 | 0.47668 | 0 | 0 | 30.2018 | 26.8488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.018009 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 459.1347 | 1367.8382 | 51.6968 | 43.6645 | 30.5686 | 1788.1761 | 59.933 | 27.2234 | #NV | #NV | #NV | #NV | #NV | 66.597 | 2.4255 | 1.2712 | 1.2193 | 4.7164 | 2.0844 | #NV | 0 | 100 | 496.3 | 323 | 83.45 | 94.65 | 86.31 | 272 | 3 | 77.9 | 37.8 | 4 | 33.15 | 43.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 81 | 0 | 33.91 | 64 | 64 | 78 | 74.45 | 65.94 | 0 | 86.23 | 1.97 | 76.37 | 38.61 | 83.5 | 16.75 | 94.67 | 110 | 0 | 15615 | 71.86 | 103.38 | 171.77 | 167.61 | 170.67 | 0 | 23.87 | 46.72 | 11899 | 77.92 | 37.79 | 33.15 | 5.89 | 37.79 | 0 | 607 | 380.5 | 459.8 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496.9 | 277.4 | 0 | 271.9 | 86.42 | 15610 | 15615 | 323
03/26/22 10:08:41.220 | 601.3135 | 1366.7769 | 53.6976 | 43.1706 | 10.5271 | 30.2247 | 50.672 | 0 | 1785.4322 | 73.7014 | 64.8846 | 8.8167 | 27.1061 | 68.2169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 460.71 | 457.9 | 461.7 | 364.1 | 391.63 | 369.68 | 276.47 | 0.45978 | 3.5546 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7242308.297 | 7894049.4097 | 7894049.4097 | 62.4298 | 62.3229 | 1.0019 | 0.99881 | 684160.1209 | 892884.097 | 460.1034 | 0.47888 | 0 | 0 | 30.2247 | 27.1061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.018011 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 461.8143 | 1367.8432 | 51.713 | 43.6338 | 30.5437 | 1788.1866 | 59.9738 | 27.2435 | #NV | #NV | #NV | #NV | #NV | 66.6769 | 2.423 | 1.2776 | 1.1601 | 4.7156 | 2.1078 | #NV | 0 | 100 | 500.2 | 325 | 83.6 | 94.9 | 86.99 | 274.6 | 3 | 78.01 | 37.72 | 4 | 33.09 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 81.23 | 0 | 33.85 | 64 | 64 | 78.28 | 74.61 | 66.05 | 0 | 86.99 | 1.98 | 76.51 | 38.53 | 83.63 | 16.88 | 94.9 | 110 | 0 | 15658 | 71.86 | 103.48 | 172.08 | 167.9 | 171 | 0 | 23.96 | 46.53 | 11904 | 78.01 | 37.71 | 33.07 | 5.93 | 37.71 | 0 | 607 | 385.7 | 459.8 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500.2 | 279.6 | 0 | 274.1 | 86.99 | 15647 | 15658 | 325
03/26/22 10:08:46.219 | 603.7991 | 1370.0902 | 53.7268 | 43.1818 | 10.5451 | 30.3513 | 50.6625 | 0 | 1785.1535 | 73.7661 | 64.9323 | 8.8338 | 27.0261 | 68.2697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 460.71 | 457.9 | 461.7 | 364.1 | 391.63 | 369.68 | 276.47 | 0.45788 | 3.8179 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7272311.1107 | 7907872.302 | 7907872.302 | 62.4297 | 62.3225 | 1.0019 | 0.9988 | 685817.3874 | 892740.3062 | 460.1034 | 0.47888 | 0 | 0 | 30.3513 | 27.0261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.018022 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 464.4946 | 1367.8751 | 51.7301 | 43.6041 | 30.5217 | 1788.1729 | 60.0146 | 27.2625 | #NV | #NV | #NV | #NV | #NV | 66.7567 | 2.4146 | 1.2839 | 1.1012 | 4.7208 | 2.1323 | #NV | 0 | 100 | 503.7 | 325 | 83.88 | 95.16 | 87.6 | 278.5 | 3 | 78.17 | 37.64 | 4 | 33.01 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 81.35 | 0 | 33.78 | 64 | 64 | 78.42 | 74.73 | 66.08 | 0 | 87.6 | 1.98 | 76.59 | 38.45 | 83.88 | 16.99 | 95.16 | 110 | 0 | 15703 | 71.86 | 103.6 | 172.42 | 168.25 | 171.39 | 0 | 24.02 | 46.43 | 11909 | 78.17 | 37.64 | 33.01 | 6 | 37.64 | 0 | 607 | 389.6 | 459.5 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 503.8 | 282.5 | 0 | 276.9 | 87.62 | 15695 | 15703 | 324
03/26/22 10:08:51.219 | 607.3746 | 1374.4874 | 53.7749 | 43.2012 | 10.5737 | 29.2745 | 50.6745 | 0 | 1786.934 | 73.8704 | 65.0082 | 8.8622 | 28.3349 | 68.2437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9851 | 460.6601 | 457.8301 | 461.6401 | 368.8501 | 396.6101 | 374.5401 | 280.1701 | 0.46128 | 3.9669 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7314352.3762 | 7942474.6346 | 7942474.6346 | 62.4296 | 62.3218 | 1.0019 | 0.99879 | 688016.3439 | 893623.7039 | 460.0434 | 0.48111 | 0 | 0 | 29.2745 | 28.3349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.018006 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 467.1601 | 1367.9158 | 51.748 | 43.5757 | 30.4974 | 1788.1303 | 60.0547 | 27.2857 | #NV | #NV | #NV | #NV | #NV | 66.8356 | 2.4449 | 1.2894 | 1.0437 | 4.7411 | 2.1571 | #NV | 0 | 100 | 506.3 | 326 | 83.95 | 95.45 | 87.98 | 280.2 | 3 | 78.2 | 37.55 | 4 | 32.93 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 81.53 | 0 | 33.7 | 64 | 64 | 78.58 | 74.82 | 66.1 | 0 | 87.98 | 1.99 | 76.7 | 38.37 | 83.9 | 17.3 | 95.48 | 110 | 0 | 15743 | 71.88 | 103.72 | 172.82 | 168.58 | 171.78 | 0 | 24.09 | 46.24 | 11914 | 78.18 | 37.55 | 32.93 | 6.09 | 37.55 | 0 | 606 | 392.8 | 459.3 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506.3 | 285.8 | 0 | 280.2 | 88.05 | 15733 | 15743 | 326
03/26/22 10:08:56.219 | 607.6429 | 1372.8256 | 53.8056 | 43.2144 | 10.5912 | 29.9132 | 50.6724 | 0 | 1791.2177 | 73.9356 | 65.0555 | 8.8801 | 27.1514 | 68.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9851 | 460.6601 | 457.8301 | 461.6401 | 368.8501 | 396.6101 | 374.5401 | 280.1701 | 0.46108 | 3.6677 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7318103.2793 | 7976080.7491 | 7976080.7491 | 62.4295 | 62.3214 | 1.0019 | 0.99879 | 687183.1349 | 895761.4899 | 460.0434 | 0.48111 | 0 | 0 | 29.9132 | 27.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.018003 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 469.8059 | 1367.9618 | 51.7671 | 43.5487 | 30.4733 | 1788.1698 | 60.0945 | 27.3049 | #NV | #NV | #NV | #NV | #NV | 66.9137 | 2.4664 | 1.2942 | 0.9883 | 4.7367 | 2.1828 | #NV | 0 | 100 | 508.3 | 326 | 84 | 95.73 | 88.4 | 282.4 | 3 | 78.24 | 37.44 | 4 | 32.81 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 81.67 | 0 | 33.59 | 64 | 64 | 78.7 | 74.9 | 66.2 | 0 | 88.4 | 2 | 76.8 | 38.25 | 84 | 17.51 | 95.75 | 110 | 0 | 15779 | 71.9 | 103.87 | 173.19 | 168.94 | 172.19 | 0 | 24.3 | 46.4 | 11919 | 78.24 | 37.43 | 32.8 | 6.21 | 37.43 | 0 | 606 | 392.2 | 459.2 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508.7 | 287.7 | 0 | 282.1 | 88.47 | 15776 | 15779 | 325
03/26/22 10:09:01.219 | 607.9023 | 1371.0708 | 53.8431 | 43.2313 | 10.6119 | 30.1157 | 50.6807 | 0 | 1787.3624 | 74.0132 | 65.112 | 8.9012 | 26.7867 | 68.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9851 | 460.6601 | 457.8301 | 461.6401 | 368.8501 | 396.6101 | 374.5401 | 280.1701 | 0.46088 | 3.7328 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7321502.4275 | 7974165.241 | 7974165.241 | 62.4295 | 62.321 | 1.0019 | 0.99878 | 686437.8205 | 893979.1272 | 460.0434 | 0.48111 | 0 | 0 | 30.1157 | 26.7867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.01801 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 472.4197 | 1367.995 | 51.7874 | 43.5234 | 30.4525 | 1788.1857 | 60.1335 | 27.3199 | #NV | #NV | #NV | #NV | #NV | 66.9908 | 2.4678 | 1.298 | 0.93617 | 4.7291 | 2.2093 | #NV | 0 | 100 | 511.2 | 327 | 84.3 | 96 | 88.9 | 285.4 | 3 | 78.43 | 37.34 | 4 | 32.74 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 81.88 | 0 | 33.51 | 64 | 64 | 78.93 | 75.05 | 66.25 | 0 | 88.9 | 2 | 76.92 | 38.17 | 84.33 | 17.59 | 96.05 | 110 | 0 | 15829 | 71.92 | 104.03 | 173.62 | 169.31 | 172.55 | 0 | 24.41 | 46.15 | 11924 | 78.46 | 37.33 | 32.73 | 6.31 | 37.33 | 0 | 606 | 396.3 | 459 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512.4 | 287.3 | 0 | 281.6 | 89.11 | 15814 | 15829 | 326
03/26/22 10:09:06.220 | 608.8712 | 1368.6348 | 53.9073 | 43.2619 | 10.6454 | 29.7625 | 50.6611 | 0 | 1788.663 | 74.1403 | 65.2062 | 8.9341 | 27.5674 | 68.2445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.979 | 460.52 | 457.67 | 461.54 | 376.7 | 405.19 | 382.76 | 286.39 | 0.47036 | 3.5443 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7332630.7326 | 8013223.932 | 8013223.932 | 62.4293 | 62.3201 | 1.0019 | 0.99877 | 685080.917 | 894469.8421 | 459.91 | 0.48705 | 0 | 0 | 29.7625 | 27.5674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.018002 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 475.0365 | 1368.0304 | 51.8083 | 43.499 | 30.4302 | 1788.1694 | 60.1723 | 27.3379 | #NV | #NV | #NV | #NV | #NV | 67.0674 | 2.453 | 1.3011 | 0.88387 | 4.7295 | 2.2358 | #NV | 0 | 100 | 515.1 | 326 | 84.5 | 96.36 | 89.58 | 287.8 | 3 | 78.54 | 37.21 | 4 | 32.61 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 82.05 | 0 | 33.43 | 64 | 64 | 79.08 | 75.15 | 66.33 | 0 | 89.58 | 2.01 | 77.02 | 38.08 | 84.48 | 17.82 | 96.39 | 110 | 0 | 15874 | 71.94 | 104.21 | 173.99 | 169.63 | 172.96 | 0 | 24.47 | 46.04 | 11929 | 78.54 | 37.21 | 32.61 | 6.43 | 37.21 | 0 | 606 | 403.3 | 458.9 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 515.4 | 293.1 | 0 | 287.4 | 89.63 | 15866 | 15874 | 330
03/26/22 10:09:11.219 | 608.9416 | 1366.5807 | 53.9422 | 43.2795 | 10.6627 | 29.8093 | 50.6706 | 0 | 1790.1442 | 74.2069 | 65.2563 | 8.9507 | 27.5259 | 68.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.979 | 460.52 | 457.67 | 461.54 | 376.7 | 405.19 | 382.76 | 286.39 | 0.47031 | 3.3793 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7333476.4481 | 8034506.9884 | 8034506.9884 | 62.4293 | 62.3197 | 1.0018 | 0.99877 | 684051.1924 | 895205.8511 | 459.91 | 0.48705 | 0 | 0 | 29.8093 | 27.5259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.018002 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 477.5918 | 1368.0383 | 51.831 | 43.4769 | 30.4048 | 1788.1843 | 60.2101 | 27.3606 | #NV | #NV | #NV | #NV | #NV | 67.1426 | 2.446 | 1.3024 | 0.83831 | 4.7315 | 2.2638 | #NV | 0 | 100 | 518.2 | 327 | 84.73 | 96.67 | 90.12 | 290 | 3 | 78.67 | 37.07 | 4 | 32.49 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 82.23 | 0 | 33.31 | 64 | 64 | 79.23 | 75.23 | 66.4 | 0 | 89.97 | 2.02 | 77.14 | 37.96 | 84.73 | 18.01 | 96.7 | 110 | 0 | 15929 | 71.98 | 104.36 | 174.37 | 170.03 | 173.38 | 0 | 24.71 | 46.11 | 11934 | 78.69 | 37.07 | 32.48 | 6.56 | 37.07 | 0 | 605 | 406.1 | 458.6 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 519.4 | 295 | 0 | 289.3 | 90.33 | 15918 | 15929 | 329
03/26/22 10:09:16.219 | 609.1234 | 1363.7732 | 53.9955 | 43.3075 | 10.688 | 29.6386 | 50.6896 | 0 | 1790.2732 | 74.3071 | 65.3319 | 8.9752 | 27.8783 | 68.2747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.989 | 460.42 | 457.56 | 461.48 | 382.7 | 411.8 | 389.17 | 291.18 | 0.47803 | 3.2159 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7335454.8751 | 8057329.8013 | 8057329.8013 | 62.4292 | 62.319 | 1.0018 | 0.99876 | 682643.4913 | 895263.2906 | 459.82 | 0.4915 | 0 | 0 | 29.6386 | 27.8783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017999 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 480.115 | 1368.0649 | 51.8549 | 43.4567 | 30.3854 | 1788.2044 | 60.247 | 27.3764 | #NV | #NV | #NV | #NV | #NV | 67.2164 | 2.394 | 1.3019 | 0.79738 | 4.7315 | 2.2921 | #NV | 0 | 100 | 521.6 | 330 | 84.9 | 96.98 | 90.71 | 290.2 | 3 | 78.81 | 36.99 | 4 | 32.4 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 82.4 | 0 | 33.21 | 64 | 64 | 79.38 | 75.34 | 66.5 | 0 | 90.71 | 2.03 | 77.25 | 37.87 | 84.88 | 18.27 | 97.04 | 110 | 0 | 15972 | 72 | 104.52 | 174.78 | 170.38 | 173.79 | 0 | 24.91 | 46.14 | 11939 | 78.78 | 36.97 | 32.39 | 6.67 | 36.97 | 0 | 605 | 408.3 | 458.7 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521.9 | 296.7 | 0 | 290.9 | 90.77 | 15962 | 15972 | 332
03/26/22 10:09:21.219 | 609.931 | 1363.5925 | 54.0296 | 43.3259 | 10.7037 | 30.2773 | 50.6862 | 0 | 1787.9869 | 74.3702 | 65.3797 | 8.9905 | 26.7569 | 68.3073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 460.38 | 457.52 | 461.46 | 385.85 | 415.24 | 392.54 | 293.7 | 0.48153 | 3.414 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7345701.7677 | 8059328.6871 | 8059328.6871 | 62.4291 | 62.3186 | 1.0018 | 0.99876 | 682551.5514 | 894115.4655 | 459.7867 | 0.49298 | 0 | 0 | 30.2773 | 26.7569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.018004 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 482.6207 | 1368.0593 | 51.8797 | 43.4375 | 30.369 | 1788.193 | 60.2838 | 27.386 | #NV | #NV | #NV | #NV | #NV | 67.29 | 2.4041 | 1.3004 | 0.75755 | 4.7296 | 2.3209 | #NV | 0 | 100 | 526 | 331 | 84.98 | 97.31 | 91.29 | 294.7 | 3 | 78.86 | 36.86 | 4 | 32.29 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 82.63 | 0 | 33.13 | 64 | 64 | 79.55 | 75.45 | 66.55 | 0 | 91.29 | 2.04 | 77.39 | 37.76 | 85.02 | 18.45 | 97.34 | 110 | 0 | 16026 | 72.04 | 104.72 | 175.22 | 170.76 | 174.17 | 0 | 25.39 | 46.64 | 11944 | 78.86 | 36.86 | 32.29 | 6.76 | 36.86 | 0 | 605 | 412.2 | 458.6 | 25 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 527.4 | 300.6 | 0 | 294.7 | 91.72 | 16012 | 16026 | 328
03/26/22 10:09:26.219 | 611.7466 | 1365.626 | 54.0645 | 43.3449 | 10.7196 | 29.9821 | 50.6805 | 0 | 1787.254 | 74.4338 | 65.4286 | 9.0052 | 27.0132 | 68.3329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 460.38 | 457.52 | 461.46 | 385.85 | 415.24 | 392.54 | 293.7 | 0.4801 | 3.6507 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7367270.0397 | 8069349.5933 | 8069349.5933 | 62.429 | 62.3182 | 1.0018 | 0.99875 | 683567.8334 | 893744.3691 | 459.7867 | 0.49298 | 0 | 0 | 29.9821 | 27.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017993 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 485.0984 | 1368.0147 | 51.9058 | 43.4201 | 30.3476 | 1788.1249 | 60.3198 | 27.4 | #NV | #NV | #NV | #NV | #NV | 67.3624 | 2.3742 | 1.2969 | 0.72226 | 4.6533 | 2.3501 | #NV | 0 | 100 | 530.7 | 334 | 85.35 | 97.65 | 92.21 | 296.7 | 3 | 79.07 | 36.78 | 4 | 32.21 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 82.85 | 0 | 33.04 | 64 | 64 | 79.78 | 75.58 | 66.59 | 0 | 92.21 | 2.04 | 77.53 | 37.67 | 85.4 | 18.56 | 97.65 | 110 | 0 | 16092 | 72.08 | 104.91 | 175.62 | 171.16 | 174.62 | 0 | 25.96 | 46.95 | 11949 | 79.09 | 36.78 | 32.2 | 6.82 | 36.78 | 0 | 605 | 416.4 | 458.3 | 25 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.7 | 302.7 | 0 | 296.7 | 92.3 | 16081 | 16092 | 334
03/26/22 10:09:31.219 | 615.9645 | 1370.9469 | 54.1351 | 43.3833 | 10.7518 | 29.9372 | 50.6765 | 0 | 1792.2912 | 74.562 | 65.5289 | 9.0331 | 27.7009 | 68.3089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0051 | 460.3401 | 457.4901 | 461.4601 | 392.2401 | 422.2501 | 399.4201 | 298.8601 | 0.48519 | 3.8654 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7417947.342 | 8117729.6872 | 8117729.6872 | 62.4289 | 62.3173 | 1.0018 | 0.99874 | 686228.1032 | 896253.7836 | 459.7634 | 0.49446 | 0 | 0 | 29.9372 | 27.7009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017991 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 487.5685 | 1368.0151 | 51.9332 | 43.4044 | 30.3264 | 1788.1069 | 60.3554 | 27.4158 | #NV | #NV | #NV | #NV | #NV | 67.434 | 2.3747 | 1.2914 | 0.69146 | 4.6317 | 2.3801 | #NV | 0 | 100 | 533.3 | 333 | 85.35 | 97.98 | 92.75 | 300.7 | 3 | 79.07 | 36.65 | 4 | 32.1 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 82.98 | 0 | 32.94 | 64 | 64 | 79.88 | 75.66 | 66.64 | 0 | 92.75 | 2.05 | 77.61 | 37.56 | 85.35 | 18.94 | 98.01 | 110 | 0 | 16149 | 72.12 | 105.11 | 176.08 | 171.57 | 175.05 | 0 | 26.34 | 46.85 | 11954 | 79.07 | 36.64 | 32.09 | 6.96 | 36.64 | 0 | 605 | 414.8 | 458.3 | 25 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 533.5 | 305.7 | 0 | 299.7 | 92.78 | 16142 | 16149 | 332
03/26/22 10:09:36.219 | 615.4376 | 1367.5407 | 54.1749 | 43.4054 | 10.7695 | 30.2242 | 50.6782 | 0 | 1790.3145 | 74.6361 | 65.588 | 9.0481 | 27.1019 | 68.3605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0081 | 460.3201 | 457.4601 | 461.4601 | 395.5401 | 425.8401 | 402.9301 | 301.4901 | 0.48988 | 3.7474 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7411811.9913 | 8121407.5186 | 8121407.5186 | 62.4288 | 62.3168 | 1.0018 | 0.99874 | 684521.3051 | 895259.7235 | 459.7467 | 0.49738 | 0 | 0 | 30.2242 | 27.1019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017995 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 490.0211 | 1367.995 | 51.9615 | 43.3898 | 30.3088 | 1788.0948 | 60.3907 | 27.4258 | #NV | #NV | #NV | #NV | #NV | 67.5052 | 2.3631 | 1.2843 | 0.66297 | 4.6229 | 2.4103 | #NV | 0 | 100 | 535.4 | 330 | 85.6 | 98.3 | 93.11 | 302.5 | 3 | 79.22 | 36.53 | 4 | 31.99 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 83.15 | 0 | 32.84 | 64 | 64 | 80.05 | 75.77 | 66.74 | 0 | 93.15 | 2.06 | 77.72 | 37.45 | 85.65 | 19.04 | 98.33 | 110 | 0 | 16195 | 72.16 | 105.31 | 176.5 | 171.95 | 175.53 | 0 | 26.39 | 46.16 | 11959 | 79.25 | 36.53 | 31.99 | 7.07 | 36.53 | 0 | 605 | 420.2 | 458.1 | 25 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535.4 | 308.5 | 0 | 302.5 | 93.11 | 16179 | 16195 | 330
03/26/22 10:09:41.218 | 614.447 | 1363.288 | 54.2124 | 43.4265 | 10.7859 | 30.2182 | 50.6939 | 0 | 1787.8269 | 74.7066 | 65.6451 | 9.0614 | 27.204 | 68.3704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0081 | 460.3201 | 457.4601 | 461.4601 | 395.5401 | 425.8401 | 402.9301 | 301.4901 | 0.49067 | 3.6978 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7399765.2266 | 8122476.7942 | 8122476.7942 | 62.4287 | 62.3164 | 1.0018 | 0.99873 | 682579.8478 | 894297.8587 | 459.7468 | 0.49738 | 0 | 0 | 30.2182 | 27.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017996 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 492.4468 | 1367.9502 | 51.9906 | 43.3761 | 30.289 | 1788.072 | 60.4258 | 27.4402 | #NV | #NV | #NV | #NV | #NV | 67.576 | 2.3755 | 1.2757 | 0.63603 | 4.6141 | 2.4406 | #NV | 0 | 100 | 538.4 | 335 | 85.88 | 98.64 | 93.63 | 303 | 3 | 79.39 | 36.46 | 4 | 31.93 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 83.35 | 0 | 32.76 | 64 | 64 | 80.3 | 75.93 | 66.78 | 0 | 93.63 | 2.07 | 77.84 | 37.37 | 85.85 | 19.29 | 98.66 | 110 | 0 | 16246 | 72.2 | 105.5 | 176.93 | 172.35 | 175.93 | 0 | 26.25 | 45.57 | 11964 | 79.38 | 36.45 | 31.91 | 7.17 | 36.45 | 0 | 605 | 426.1 | 458 | 25 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 538.4 | 310.6 | 0 | 304.5 | 93.63 | 16236 | 16246 | 334
03/26/22 10:09:46.218 | 615.7609 | 1363.2209 | 54.2665 | 43.457 | 10.8095 | 30.7116 | 50.6889 | 0 | 1785.427 | 74.8086 | 65.7287 | 9.0799 | 26.7391 | 68.3457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0111 | 460.3001 | 457.4401 | 461.4601 | 398.8401 | 429.4301 | 406.4101 | 304.1301 | 0.49391 | 3.9419 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7416034.1552 | 8126967.8548 | 8126967.8548 | 62.4286 | 62.3156 | 1.0018 | 0.99873 | 682354.9374 | 892802.3736 | 459.7334 | 0.49884 | 0 | 0 | 30.7116 | 26.7391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.018005 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 494.8481 | 1367.9183 | 52.021 | 43.3644 | 30.272 | 1788.0406 | 60.4603 | 27.4534 | #NV | #NV | #NV | #NV | #NV | 67.6458 | 2.4002 | 1.264 | 0.61454 | 4.6127 | 2.4714 | #NV | 0 | 100 | 540.7 | 336 | 85.92 | 99.05 | 94.03 | 307.1 | 3 | 79.42 | 36.37 | 4 | 31.84 | 43.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 83.53 | 0 | 32.7 | 64 | 64 | 80.42 | 76.01 | 66.89 | 0 | 94.03 | 2.07 | 77.93 | 37.3 | 85.92 | 19.63 | 99.05 | 110 | 0 | 16306 | 72.24 | 105.7 | 177.4 | 172.75 | 176.43 | 0 | 26.32 | 45.48 | 11969 | 79.42 | 36.37 | 31.84 | 7.3 | 36.37 | 0 | 604 | 425.9 | 457.9 | 25 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540.7 | 313.2 | 0 | 307.1 | 94.03 | 16289 | 16306 | 336
03/26/22 10:09:51.218 | 616.946 | 1364.5989 | 54.3022 | 43.4768 | 10.8253 | 30.0115 | 50.6803 | 0 | 1783.6413 | 74.8762 | 65.7839 | 9.0923 | 27.4142 | 68.3288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0111 | 460.3101 | 457.4501 | 461.4701 | 402.1601 | 433.0001 | 409.9401 | 306.7801 | 0.49726 | 4.196 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7429722.7057 | 8128133.2055 | 8128133.2055 | 62.4285 | 62.3153 | 1.0018 | 0.99872 | 682875.4947 | 891889.7604 | 459.7434 | 0.49883 | 0 | 0 | 30.0115 | 27.4142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.018006 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 497.2226 | 1367.8866 | 52.0527 | 43.3543 | 30.2623 | 1787.9901 | 60.4942 | 27.4586 | #NV | #NV | #NV | #NV | #NV | 67.7145 | 2.4063 | 1.2492 | 0.59736 | 4.6109 | 2.5023 | #NV | 0 | 100 | 545.2 | 337 | 86.05 | 99.43 | 94.59 | 310.5 | 3 | 79.5 | 36.33 | 4 | 31.8 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 83.7 | 0 | 32.65 | 64 | 64 | 80.55 | 76.09 | 66.91 | 0 | 94.49 | 2.08 | 78.04 | 37.25 | 86.05 | 19.93 | 99.43 | 110 | 0 | 16366 | 72.28 | 105.96 | 177.9 | 173.21 | 176.95 | 0 | 26.72 | 45.82 | 11974 | 79.5 | 36.33 | 31.8 | 7.36 | 36.33 | 0 | 604 | 429.2 | 457.8 | 25 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.2 | 316.6 | 0 | 310.5 | 94.82 | 16355 | 16366 | 337
03/26/22 10:09:56.218 | 618.6876 | 1365.2801 | 54.3526 | 43.5045 | 10.8481 | 30.1828 | 50.6854 | 0 | 1783.0478 | 74.9728 | 65.8624 | 9.1105 | 27.2975 | 68.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 460.3001 | 457.4401 | 461.4701 | 405.4301 | 436.5101 | 413.4201 | 309.3901 | 0.50007 | 4.3829 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7450576.184 | 8141436.3486 | 8141436.3486 | 62.4284 | 62.3146 | 1.0018 | 0.99871 | 683444.2225 | 891658.1425 | 459.7367 | 0.49956 | 0 | 0 | 30.1828 | 27.2975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.018007 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 499.5908 | 1367.859 | 52.0852 | 43.3452 | 30.2585 | 1787.9341 | 60.528 | 27.4594 | #NV | #NV | #NV | #NV | #NV | 67.7831 | 2.4075 | 1.2325 | 0.58205 | 4.6093 | 2.5335 | #NV | 0 | 100 | 546.9 | 336 | 86.1 | 99.76 | 94.99 | 312.6 | 3 | 79.51 | 36.26 | 4 | 31.74 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 83.85 | 0 | 32.59 | 64 | 64 | 80.68 | 76.16 | 67.04 | 0 | 94.99 | 2.08 | 78.15 | 37.18 | 86.1 | 20.23 | 99.79 | 110 | 0 | 16420 | 72.32 | 106.17 | 178.42 | 173.68 | 177.48 | 0 | 27.08 | 46.01 | 11979 | 79.53 | 36.26 | 31.74 | 7.47 | 36.26 | 0 | 604 | 433.3 | 457.7 | 25 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546.5 | 319 | 0 | 312.8 | 95.04 | 16416 | 16420 | 336
03/26/22 10:10:01.218 | 621.1424 | 1366.8697 | 54.4136 | 43.5383 | 10.8753 | 30.2657 | 50.6749 | 0 | 1784.8232 | 75.0896 | 65.957 | 9.1326 | 26.8782 | 68.3969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 460.3001 | 457.4401 | 461.4701 | 405.4301 | 436.5101 | 413.4201 | 309.3901 | 0.4981 | 4.3696 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7480292.1733 | 8170962.6498 | 8170962.6498 | 62.4282 | 62.3137 | 1.0018 | 0.99871 | 684174.6871 | 892478.6542 | 459.7368 | 0.49956 | 0 | 0 | 30.2657 | 26.8782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.018 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 501.9508 | 1367.8455 | 52.1184 | 43.3371 | 30.2577 | 1787.9027 | 60.562 | 27.4576 | #NV | #NV | #NV | #NV | #NV | 67.8516 | 2.4062 | 1.2138 | 0.56894 | 4.6111 | 2.565 | #NV | 0 | 100 | 549 | 338 | 86.33 | 100.14 | 95.48 | 313 | 3 | 79.65 | 36.22 | 4 | 31.7 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 84.03 | 0 | 32.55 | 64 | 64 | 80.88 | 76.28 | 67.08 | 0 | 95.48 | 2.09 | 78.26 | 37.14 | 86.35 | 20.46 | 100.17 | 110 | 0 | 16476 | 72.38 | 106.43 | 178.92 | 174.15 | 177.94 | 0 | 27.46 | 46.15 | 11984 | 79.68 | 36.22 | 31.7 | 7.51 | 36.22 | 0 | 604 | 435.2 | 457.5 | 25 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549 | 319.1 | 0 | 313 | 95.48 | 16462 | 16476 | 338
03/26/22 10:10:06.218 | 622.1743 | 1366.6014 | 54.4609 | 43.5653 | 10.8956 | 30.0817 | 50.6823 | 0 | 1787.7443 | 75.1789 | 66.0291 | 9.1498 | 27.008 | 68.3771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9991 | 460.2301 | 457.3901 | 461.4301 | 411.5101 | 443.1601 | 419.9201 | 314.2601 | 0.5051 | 4.1618 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7492507.8571 | 8199680.1454 | 8199680.1454 | 62.4281 | 62.3131 | 1.0018 | 0.9987 | 684038.2073 | 893932.4112 | 459.6834 | 0.49889 | 0 | 0 | 30.0817 | 27.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.018006 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 504.2664 | 1367.8369 | 52.1522 | 43.3302 | 30.2533 | 1787.9047 | 60.5961 | 27.4594 | #NV | #NV | #NV | #NV | #NV | 67.9197 | 2.4079 | 1.1937 | 0.55859 | 4.611 | 2.5966 | #NV | 0 | 100 | 550.2 | 339 | 86.53 | 100.47 | 95.77 | 314.8 | 3 | 79.79 | 36.19 | 4 | 31.68 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 84.17 | 0 | 32.53 | 64 | 64 | 81 | 76.37 | 67.13 | 0 | 95.77 | 2.09 | 78.35 | 37.12 | 86.58 | 20.71 | 100.55 | 110 | 0 | 16500 | 72.42 | 106.66 | 179.44 | 174.61 | 178.48 | 0 | 27.73 | 46.03 | 11989 | 79.82 | 36.18 | 31.66 | 7.59 | 36.18 | 0 | 604 | 436.7 | 457.4 | 25 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550.2 | 320.7 | 0 | 314.6 | 95.69 | 16499 | 16500 | 337
03/26/22 10:10:11.219 | 623.7673 | 1366.8594 | 54.5251 | 43.6035 | 10.9216 | 30.2742 | 50.6924 | 0 | 1784.0491 | 75.2966 | 66.1236 | 9.173 | 26.4853 | 68.4357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 460.1501 | 457.3101 | 461.3701 | 416.4001 | 448.4301 | 425.0601 | 318.1101 | 0.50998 | 4.6255 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7511798.8038 | 8202663.8291 | 8202663.8291 | 62.428 | 62.3123 | 1.0017 | 0.99869 | 684164.418 | 892075.5854 | 459.6101 | 0.50042 | 0 | 0 | 30.2742 | 26.4853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.018014 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 506.5198 | 1367.8362 | 52.1859 | 43.3245 | 30.2499 | 1787.933 | 60.6312 | 27.456 | #NV | #NV | #NV | #NV | #NV | 67.9876 | 2.4081 | 1.1741 | 0.55041 | 4.5712 | 2.6284 | #NV | 0 | 100 | 550.9 | 338 | 86.7 | 100.86 | 95.81 | 315.1 | 3 | 79.89 | 36.16 | 4 | 31.65 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 84.35 | 0 | 32.5 | 64 | 64 | 81.2 | 76.48 | 67.25 | 0 | 95.81 | 2.1 | 78.46 | 37.09 | 86.73 | 20.95 | 100.86 | 110 | 0 | 16500 | 72.48 | 106.88 | 179.96 | 175.1 | 179.07 | 0 | 27.88 | 45.86 | 11994 | 79.91 | 36.16 | 31.65 | 7.61 | 36.16 | 0 | 604 | 436.9 | 457.2 | 25 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551.2 | 320.8 | 0 | 314.7 | 95.86 | 16498 | 16500 | 340
03/26/22 10:10:16.218 | 625.3018 | 1369.1251 | 54.5647 | 43.6281 | 10.9366 | 30.4993 | 50.6759 | 0 | 1781.355 | 75.3672 | 66.1804 | 9.1868 | 26.4635 | 68.4452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 460.15 | 457.31 | 461.37 | 416.4 | 448.43 | 425.06 | 318.11 | 0.50873 | 4.924 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7530340.3771 | 8201731.3715 | 8201731.3715 | 62.4279 | 62.3119 | 1.0017 | 0.99869 | 685095.5306 | 890897.023 | 459.61 | 0.50042 | 0 | 0 | 30.4993 | 26.4635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.018018 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 508.7681 | 1367.8445 | 52.2197 | 43.3193 | 30.2487 | 1787.9492 | 60.6669 | 27.4494 | #NV | #NV | #NV | #NV | #NV | 68.0558 | 2.41 | 1.1545 | 0.54293 | 4.5425 | 2.6599 | #NV | 0 | 100 | 551.6 | 339 | 86.83 | 101.12 | 95.93 | 315 | 3 | 79.97 | 36.15 | 4 | 31.64 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 84.5 | 0 | 32.49 | 64 | 64 | 81.33 | 76.59 | 67.31 | 0 | 95.93 | 2.1 | 78.55 | 37.07 | 86.83 | 21.18 | 101.15 | 110 | 0 | 16500 | 72.54 | 107.08 | 180.51 | 175.59 | 179.61 | 0 | 28.09 | 45.82 | 11999 | 79.97 | 36.15 | 31.64 | 7.66 | 36.15 | 0 | 604 | 436.4 | 457.2 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551.6 | 321.2 | 0 | 315 | 95.97 | 16501 | 16500 | 339
03/26/22 10:10:21.218 | 627.1581 | 1369.4503 | 54.6328 | 43.6723 | 10.9605 | 30.2315 | 50.6926 | 0 | 1778.181 | 75.4842 | 66.2749 | 9.2093 | 26.7209 | 68.4452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.985 | 460.13 | 457.29 | 461.35 | 418.34 | 450.48 | 427.07 | 319.63 | 0.50965 | 5.1643 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7552501.3429 | 8208005.9504 | 8208005.9504 | 62.4277 | 62.311 | 1.0017 | 0.99868 | 685456.2841 | 889126.8416 | 459.59 | 0.50045 | 0 | 0 | 30.2315 | 26.7209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.018024 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 510.8976 | 1367.8594 | 52.2526 | 43.315 | 30.2474 | 1787.9362 | 60.7044 | 27.4438 | #NV | #NV | #NV | #NV | #NV | 68.1242 | 2.4116 | 1.1382 | 0.53702 | 4.5672 | 2.6911 | #NV | 0 | 100 | 552.3 | 339 | 86.95 | 101.34 | 96.05 | 314.7 | 3 | 80.04 | 36.15 | 4 | 31.64 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 84.65 | 0 | 32.5 | 64 | 64 | 81.48 | 76.65 | 67.36 | 0 | 96.05 | 2.1 | 78.63 | 37.09 | 87 | 21.3 | 101.39 | 110 | 0 | 16500 | 72.58 | 107.23 | 181.01 | 176.04 | 180.13 | 0 | 28.38 | 45.92 | 12004 | 80.06 | 36.16 | 31.65 | 7.67 | 36.16 | 0 | 604 | 437.7 | 457.3 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552.3 | 322 | 0 | 315.8 | 96.05 | 16498 | 16500 | 339
03/26/22 10:10:26.218 | 626.978 | 1366.0388 | 54.7099 | 43.725 | 10.9849 | 30.0294 | 50.7125 | 0 | 1784.0129 | 75.609 | 66.3768 | 9.2322 | 26.7638 | 68.4563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.984 | 460.12 | 457.27 | 461.33 | 419.91 | 452.14 | 428.7 | 320.86 | 0.51176 | 4.6118 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7550095.4144 | 8255215.7169 | 8255215.7169 | 62.4275 | 62.3101 | 1.0017 | 0.99867 | 683745.1959 | 892033.092 | 459.5734 | 0.50119 | 0 | 0 | 30.0294 | 26.7638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016241 | 0.018014 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 512.957 | 1367.8546 | 52.2848 | 43.3111 | 30.2423 | 1787.9297 | 60.7434 | 27.4391 | #NV | #NV | #NV | #NV | #NV | 68.1932 | 2.4128 | 1.1244 | 0.53155 | 4.5755 | 2.7217 | #NV | 0 | 100 | 553 | 338 | 87.15 | 101.58 | 96.17 | 317 | 3 | 80.16 | 36.18 | 4 | 31.66 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 84.78 | 0 | 32.51 | 64 | 64 | 81.63 | 76.75 | 67.4 | 0 | 96.17 | 2.11 | 78.72 | 37.1 | 87.15 | 21.42 | 101.58 | 110 | 0 | 16500 | 72.64 | 107.37 | 181.6 | 176.55 | 180.7 | 0 | 28.62 | 45.88 | 12009 | 80.16 | 36.18 | 31.66 | 7.67 | 36.18 | 0 | 604 | 439.8 | 457.4 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 323.1 | 0 | 316.9 | 96.17 | 16499 | 16500 | 339
03/26/22 10:10:31.218 | 627.9135 | 1366.7252 | 54.7483 | 43.7524 | 10.9959 | 29.636 | 50.722 | 0 | 1784.2761 | 75.6686 | 66.4258 | 9.2428 | 27.6686 | 68.4629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9891 | 460.0901 | 457.2201 | 461.3101 | 421.9601 | 454.4201 | 430.7701 | 322.4701 | 0.51356 | 4.597 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7560989.7731 | 8266839.4657 | 8266839.4657 | 62.4274 | 62.3097 | 1.0017 | 0.99866 | 684086.9897 | 892159.9488 | 459.5401 | 0.50485 | 0 | 0 | 29.636 | 27.6686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.018021 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 514.9682 | 1367.8325 | 52.3162 | 43.3075 | 30.236 | 1787.9472 | 60.7838 | 27.4409 | #NV | #NV | #NV | #NV | #NV | 68.2628 | 2.408 | 1.1135 | 0.52626 | 4.5558 | 2.7516 | #NV | 0 | 100 | 553.6 | 338 | 87.25 | 101.73 | 96.28 | 315.2 | 3 | 80.21 | 36.22 | 4 | 31.7 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 84.93 | 0 | 32.55 | 64 | 64 | 81.73 | 76.81 | 67.46 | 0 | 96.28 | 2.11 | 78.8 | 37.14 | 87.23 | 21.52 | 101.73 | 110 | 0 | 16500 | 72.7 | 107.49 | 182.16 | 177.08 | 181.25 | 0 | 28.69 | 45.59 | 12014 | 80.21 | 36.22 | 31.7 | 7.63 | 36.22 | 0 | 604 | 437.5 | 457.4 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553.7 | 322.3 | 0 | 316.2 | 96.3 | 16500 | 16500 | 337
03/26/22 10:10:36.219 | 630.5697 | 1370.596 | 54.8085 | 43.7971 | 11.0114 | 29.1704 | 50.7286 | 0 | 1787.445 | 75.7596 | 66.5017 | 9.2579 | 28.4295 | 68.4497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 460.1 | 457.21 | 461.3 | 422.55 | 455.02 | 431.29 | 322.9 | 0.51208 | 4.6753 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7592527.1155 | 8295703.9683 | 8295703.9683 | 62.4273 | 62.309 | 1.0017 | 0.99866 | 686021.6121 | 893737.0107 | 459.5367 | 0.50631 | 0 | 0 | 29.1704 | 28.4295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.018015 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 516.888 | 1367.8574 | 52.3461 | 43.3039 | 30.2258 | 1787.9513 | 60.8266 | 27.4501 | #NV | #NV | #NV | #NV | #NV | 68.3333 | 2.4054 | 1.1074 | 0.52074 | 4.5544 | 2.7801 | #NV | 0 | 100 | 553.9 | 335 | 87.28 | 101.85 | 96.31 | 315.2 | 3 | 80.25 | 36.22 | 4 | 31.7 | 43.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 85 | 0 | 32.56 | 64 | 64 | 81.77 | 76.86 | 67.53 | 0 | 96.31 | 2.11 | 78.86 | 37.16 | 87.3 | 21.61 | 101.85 | 110 | 0 | 16500 | 72.74 | 107.61 | 182.68 | 177.56 | 181.82 | 0 | 28.77 | 45.49 | 12019 | 80.24 | 36.22 | 31.7 | 7.69 | 36.22 | 0 | 604 | 439.6 | 457.3 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553.7 | 320.8 | 0 | 314.6 | 96.3 | 16500 | 16500 | 339
03/26/22 10:10:41.217 | 631.62 | 1371.8914 | 54.8636 | 43.8401 | 11.0235 | 29.0968 | 50.7157 | 0 | 1791.9815 | 75.8404 | 66.5707 | 9.2697 | 28.6378 | 68.4679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 460.1 | 457.21 | 461.3 | 422.55 | 455.02 | 431.29 | 322.9 | 0.51123 | 4.5116 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7605182.5475 | 8322803.2848 | 8322803.2848 | 62.4272 | 62.3086 | 1.0017 | 0.99865 | 686569.828 | 895754.8973 | 459.5367 | 0.50631 | 0 | 0 | 29.0968 | 28.6378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.018006 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 518.7719 | 1367.8972 | 52.3752 | 43.3004 | 30.2143 | 1788.0088 | 60.871 | 27.4615 | #NV | #NV | #NV | #NV | #NV | 68.4047 | 2.4125 | 1.1043 | 0.51496 | 4.5396 | 2.8076 | #NV | 0 | 100 | 554.9 | 339 | 87.4 | 101.94 | 96.43 | 315.5 | 3 | 80.31 | 36.26 | 4 | 31.74 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 85.1 | 0 | 32.6 | 64 | 64 | 81.93 | 76.95 | 67.64 | 0 | 96.43 | 2.11 | 78.92 | 37.2 | 87.4 | 21.63 | 101.94 | 110 | 0 | 16500 | 72.8 | 107.68 | 183.28 | 178.08 | 182.42 | 0 | 28.85 | 45.29 | 12024 | 80.31 | 36.27 | 31.75 | 7.7 | 36.27 | 0 | 604 | 440.1 | 457.2 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555.1 | 321.7 | 0 | 315.5 | 96.54 | 16499 | 16500 | 336
03/26/22 10:10:46.218 | 632.6192 | 1371.5972 | 54.9543 | 43.9148 | 11.0395 | 29.1649 | 50.7166 | 0 | 1795.7748 | 75.9675 | 66.6817 | 9.2857 | 28.105 | 68.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 460.14 | 457.19 | 461.33 | 423.15 | 455.66 | 431.78 | 323.35 | 0.51113 | 4.2276 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7617135.3473 | 8358665.7131 | 8358665.7131 | 62.4269 | 62.3075 | 1.0017 | 0.99864 | 686515.9256 | 897884.3476 | 459.5534 | 0.51427 | 0 | 0 | 29.1649 | 28.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017998 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 520.6093 | 1367.9324 | 52.4034 | 43.2968 | 30.2024 | 1788.0779 | 60.9168 | 27.4725 | #NV | #NV | #NV | #NV | #NV | 68.4768 | 2.4203 | 1.1037 | 0.50871 | 4.5379 | 2.8338 | #NV | 0 | 100 | 554.9 | 337 | 87.4 | 102.04 | 96.49 | 317.2 | 3 | 80.31 | 36.29 | 4 | 31.77 | 44.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 85.15 | 0 | 32.63 | 64 | 64 | 81.98 | 76.98 | 67.72 | 0 | 96.49 | 2.11 | 78.95 | 37.22 | 87.45 | 21.74 | 102.07 | 110 | 0 | 16500 | 72.9 | 107.8 | 183.8 | 178.6 | 183 | 0 | 28.83 | 45.14 | 12029 | 80.33 | 36.3 | 31.77 | 7.75 | 36.3 | 0 | 604 | 438.1 | 457.2 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555.2 | 320.5 | 0 | 314.3 | 96.56 | 16498 | 16500 | 337
03/26/22 10:10:51.218 | 632.1984 | 1369.8115 | 55.0054 | 43.9587 | 11.0467 | 29.2609 | 50.7149 | 0 | 1798.3347 | 76.0354 | 66.7424 | 9.293 | 28.029 | 68.5051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 460.14 | 457.19 | 461.33 | 423.15 | 455.66 | 431.78 | 323.35 | 0.51147 | 3.9607 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7612136.3259 | 8376964.7486 | 8376964.7486 | 62.4268 | 62.307 | 1.0017 | 0.99864 | 685619.7284 | 899158.2883 | 459.5533 | 0.51427 | 0 | 0 | 29.2609 | 28.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017986 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 522.3181 | 1367.9337 | 52.4294 | 43.293 | 30.1953 | 1788.1383 | 60.9659 | 27.4751 | #NV | #NV | #NV | #NV | #NV | 68.5507 | 2.4213 | 1.1094 | 0.50108 | 4.6016 | 2.8577 | #NV | 0 | 100 | 555.8 | 336 | 87.52 | 102.14 | 96.66 | 314.4 | 3 | 80.39 | 36.31 | 4 | 31.79 | 44.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 85.28 | 0 | 32.64 | 64 | 64 | 82.08 | 77.05 | 67.76 | 0 | 96.63 | 2.11 | 79.03 | 37.24 | 87.58 | 21.72 | 102.14 | 110 | 0 | 16500 | 72.94 | 107.88 | 184.32 | 179.07 | 183.45 | 0 | 29.06 | 45.39 | 12033 | 80.42 | 36.31 | 31.79 | 7.75 | 36.31 | 0 | 604 | 439.6 | 457.3 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555.9 | 321.2 | 0 | 315 | 96.68 | 16499 | 16500 | 337
03/26/22 10:10:56.217 | 631.3442 | 1367.2878 | 55.0503 | 43.9981 | 11.0522 | 30.1362 | 50.7154 | 0 | 1797.1425 | 76.0935 | 66.7949 | 9.2986 | 27.2471 | 68.4902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9921 | 460.1801 | 457.2001 | 461.3501 | 423.3901 | 455.9301 | 431.9701 | 323.5301 | 0.51245 | 3.7937 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7602302.7211 | 8382090.2257 | 8382090.2257 | 62.4267 | 62.3067 | 1.0016 | 0.99864 | 684448.0382 | 899379.068 | 459.5767 | 0.51714 | 0 | 0 | 30.1362 | 27.2471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017987 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 524.0058 | 1367.9162 | 52.4551 | 43.2892 | 30.1939 | 1788.1823 | 61.0159 | 27.4707 | #NV | #NV | #NV | #NV | #NV | 68.6252 | 2.4145 | 1.1163 | 0.49296 | 4.6496 | 2.8805 | #NV | 0 | 100 | 555.6 | 338 | 87.58 | 102.21 | 96.77 | 315.6 | 3 | 80.42 | 36.31 | 4 | 31.79 | 44.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 85.38 | 0 | 32.65 | 64 | 64 | 82.25 | 77.14 | 67.83 | 0 | 96.77 | 2.11 | 79.09 | 37.24 | 87.63 | 21.8 | 102.24 | 110 | 0 | 16500 | 73.02 | 108 | 184.88 | 179.59 | 184.03 | 0 | 29.28 | 45.47 | 12038 | 80.43 | 36.31 | 31.79 | 7.77 | 36.31 | 0 | 604 | 437.6 | 457.4 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555.6 | 321.8 | 0 | 315.6 | 96.63 | 16497 | 16500 | 338
03/26/22 10:11:01.218 | 632.9977 | 1369.8012 | 55.1494 | 44.0882 | 11.0612 | 30.3604 | 50.7209 | 0 | 1792.5905 | 76.217 | 66.908 | 9.309 | 26.8821 | 68.4749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 460.2401 | 457.2201 | 461.3901 | 423.9501 | 456.5101 | 432.5301 | 323.9701 | 0.5118 | 4.2566 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7622696.0797 | 8362907.2474 | 8362907.2474 | 62.4264 | 62.3057 | 1.0016 | 0.99863 | 685607.7561 | 896269.8698 | 459.6168 | 0.52145 | 0 | 0 | 30.3604 | 26.8821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017988 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 525.641 | 1367.9238 | 52.4795 | 43.2851 | 30.1897 | 1788.1943 | 61.0682 | 27.4711 | #NV | #NV | #NV | #NV | #NV | 68.7012 | 2.4185 | 1.1267 | 0.48298 | 4.6579 | 2.9015 | #NV | 0 | 100 | 557.2 | 337 | 87.78 | 102.31 | 96.87 | 318.7 | 3 | 80.54 | 36.35 | 4 | 31.83 | 44.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 85.52 | 0 | 32.68 | 64 | 64 | 82.33 | 77.2 | 67.88 | 0 | 96.87 | 2.12 | 79.16 | 37.28 | 87.8 | 21.74 | 102.31 | 110 | 0 | 16500 | 73.08 | 108.08 | 185.41 | 180.06 | 184.61 | 0 | 29.45 | 45.51 | 12043 | 80.57 | 36.35 | 31.83 | 7.79 | 36.35 | 0 | 604 | 441.3 | 457.4 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557.1 | 323 | 0 | 316.7 | 96.89 | 16500 | 16500 | 338
03/26/22 10:11:06.218 | 632.9977 | 1368.8929 | 55.1688 | 44.1063 | 11.0625 | 30.2664 | 50.7127 | 0 | 1790.9803 | 76.2403 | 66.9294 | 9.3109 | 27.0004 | 68.4972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 460.2401 | 457.2201 | 461.3901 | 423.9501 | 456.5101 | 432.5301 | 323.9701 | 0.5118 | 4.2738 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7622696.0797 | 8362907.2474 | 8362907.2474 | 62.4264 | 62.3057 | 1.0016 | 0.99863 | 685607.7561 | 896269.8698 | 459.6168 | 0.52145 | 0 | 0 | 30.2664 | 27.0004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.01799 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 527.2508 | 1367.9339 | 52.5032 | 43.2806 | 30.1865 | 1788.2085 | 61.1214 | 27.4688 | #NV | #NV | #NV | #NV | #NV | 68.7778 | 2.4188 | 1.1382 | 0.47149 | 4.6625 | 2.9208 | #NV | 0 | 100 | 557.7 | 334 | 87.88 | 102.38 | 96.99 | 314.6 | 3 | 80.6 | 36.38 | 4 | 31.85 | 44.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 85.68 | 0 | 32.71 | 64 | 64 | 82.48 | 77.3 | 67.96 | 0 | 96.99 | 2.12 | 79.27 | 37.32 | 87.92 | 21.78 | 102.41 | 110 | 0 | 16500 | 73.14 | 108.16 | 185.98 | 180.65 | 185.2 | 0 | 29.51 | 45.37 | 12048 | 80.63 | 36.38 | 31.85 | 7.82 | 36.38 | 0 | 604 | 442.8 | 457.5 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557.5 | 325.3 | 0 | 319.1 | 96.96 | 16498 | 16500 | 339
03/26/22 10:11:11.219 | 633.5371 | 1368.929 | 55.2758 | 44.2071 | 11.0687 | 29.5041 | 50.7201 | 0 | 1790.428 | 76.3652 | 67.0449 | 9.3203 | 28.521 | 68.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.016 | 460.27 | 457.21 | 461.36 | 424.63 | 457.03 | 433.14 | 324.42 | 0.51208 | 4.4189 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7628614.1587 | 8357161.1124 | 8357161.1124 | 62.426 | 62.3047 | 1.0016 | 0.99862 | 685783.1731 | 894490.1198 | 459.6134 | 0.5229 | 0 | 0 | 29.5041 | 28.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017983 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 528.8418 | 1367.9436 | 52.5265 | 43.2763 | 30.1793 | 1788.2051 | 61.1756 | 27.4754 | #NV | #NV | #NV | #NV | #NV | 68.8553 | 2.4242 | 1.1515 | 0.45948 | 4.6616 | 2.9393 | #NV | 0 | 100 | 558 | 338 | 88 | 102.5 | 97.04 | 316.9 | 3 | 80.67 | 36.4 | 4 | 31.86 | 44.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 85.78 | 0 | 32.73 | 64 | 64 | 82.58 | 77.36 | 67.98 | 0 | 97.04 | 2.12 | 79.33 | 37.32 | 87.95 | 21.84 | 102.5 | 110 | 0 | 16500 | 73.2 | 108.24 | 186.56 | 181.12 | 185.73 | 0 | 29.58 | 45.29 | 12053 | 80.66 | 36.41 | 31.88 | 7.82 | 36.41 | 0 | 604 | 440.6 | 457.3 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558 | 325.7 | 0 | 319.5 | 97.04 | 16498 | 16500 | 338
03/26/22 10:11:16.218 | 632.702 | 1368.0464 | 55.3338 | 44.263 | 11.0708 | 29.5198 | 50.7122 | 0 | 1790.6706 | 76.4311 | 67.1065 | 9.3246 | 27.5998 | 68.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 460.2701 | 457.2101 | 461.3601 | 424.6301 | 457.0301 | 433.1401 | 324.4201 | 0.51275 | 4.1764 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7618373.7302 | 8368389.1955 | 8368389.1955 | 62.4258 | 62.3041 | 1.0016 | 0.99861 | 684720.6941 | 895290.2861 | 459.6134 | 0.5229 | 0 | 0 | 29.5198 | 27.5998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017989 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 530.4 | 1367.9287 | 52.5498 | 43.2723 | 30.1695 | 1788.2021 | 61.2306 | 27.4806 | #NV | #NV | #NV | #NV | #NV | 68.9333 | 2.4152 | 1.1656 | 0.44758 | 4.6598 | 2.9573 | #NV | 0 | 100 | 558.7 | 336 | 88.13 | 102.6 | 97.17 | 319 | 3 | 80.75 | 36.45 | 4 | 31.91 | 44.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 85.88 | 0 | 32.76 | 64 | 64 | 82.65 | 77.41 | 68.04 | 0 | 97.11 | 2.12 | 79.39 | 37.36 | 88.15 | 21.84 | 102.6 | 110 | 0 | 16500 | 73.26 | 108.31 | 187.06 | 181.64 | 186.29 | 0 | 29.66 | 45.24 | 12059 | 80.76 | 36.45 | 31.91 | 7.8 | 36.45 | 0 | 604 | 440.9 | 457.2 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558.9 | 324.3 | 0 | 318 | 97.2 | 16499 | 16500 | 338
03/26/22 10:11:21.219 | 632.9359 | 1368.3045 | 55.3884 | 44.3163 | 11.0721 | 29.5401 | 50.737 | 0 | 1785.5819 | 76.492 | 67.1637 | 9.3284 | 27.6241 | 68.4799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.022 | 460.28 | 457.2 | 461.35 | 425.01 | 457.36 | 433.52 | 324.69 | 0.51299 | 4.3932 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7621248.7593 | 8353888.7039 | 8353888.7039 | 62.4257 | 62.3037 | 1.0016 | 0.99861 | 684917.7541 | 893500.6557 | 459.61 | 0.52436 | 0 | 0 | 29.5401 | 27.6241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017994 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 531.9414 | 1367.9202 | 52.5731 | 43.2687 | 30.161 | 1788.1823 | 61.2859 | 27.4854 | #NV | #NV | #NV | #NV | #NV | 69.0115 | 2.4112 | 1.1802 | 0.4362 | 4.6634 | 2.9746 | #NV | 0 | 100 | 559.9 | 337 | 88.38 | 102.65 | 97.37 | 319.6 | 3 | 80.9 | 36.52 | 4 | 31.96 | 44.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 86.08 | 0 | 32.82 | 64 | 64 | 82.85 | 77.53 | 68.14 | 0 | 97.37 | 2.12 | 79.5 | 37.44 | 88.5 | 21.7 | 102.67 | 110 | 0 | 16500 | 73.32 | 108.39 | 187.65 | 182.17 | 186.83 | 0 | 29.6 | 45.06 | 12064 | 80.97 | 36.52 | 31.98 | 7.79 | 36.52 | 0 | 604 | 442.1 | 457.2 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560.6 | 323.9 | 0 | 317.7 | 97.5 | 16500 | 16500 | 336
03/26/22 10:11:26.217 | 632.7673 | 1367.9432 | 55.4814 | 44.4082 | 11.0732 | 30.1402 | 50.7395 | 0 | 1788.5598 | 76.5929 | 67.2582 | 9.3347 | 27.0009 | 68.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.025 | 460.3 | 457.22 | 461.34 | 425.39 | 457.65 | 433.88 | 324.96 | 0.51355 | 4.2338 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7619701.5323 | 8366620.896 | 8366620.896 | 62.4254 | 62.3028 | 1.0016 | 0.9986 | 684661.9344 | 894219.8248 | 459.62 | 0.52217 | 0 | 0 | 30.1402 | 27.0009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017983 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 533.4482 | 1367.9176 | 52.5965 | 43.2656 | 30.1557 | 1788.1698 | 61.3416 | 27.49 | #NV | #NV | #NV | #NV | #NV | 69.0896 | 2.4117 | 1.1952 | 0.42615 | 4.6679 | 2.9915 | #NV | 0 | 100 | 560.4 | 339 | 88.38 | 102.72 | 97.41 | 318.3 | 3 | 80.88 | 36.53 | 4 | 32 | 44.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 86.18 | 0 | 32.85 | 64 | 64 | 82.98 | 77.61 | 68.2 | 0 | 97.41 | 2.12 | 79.57 | 37.47 | 88.4 | 21.81 | 102.72 | 110 | 0 | 16500 | 73.36 | 108.45 | 188.16 | 182.66 | 187.34 | 0 | 29.56 | 44.92 | 12068 | 80.91 | 36.55 | 32 | 7.82 | 36.55 | 0 | 604 | 441.7 | 457.2 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560.4 | 324.6 | 0 | 318.3 | 97.46 | 16497 | 16500 | 339
03/26/22 10:11:31.217 | 632.7673 | 1368.5832 | 55.5006 | 44.4271 | 11.0735 | 30.0087 | 50.7391 | 0 | 1789.1378 | 76.6134 | 67.2772 | 9.3362 | 27.1229 | 68.4877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.025 | 460.3 | 457.22 | 461.34 | 425.39 | 457.65 | 433.88 | 324.96 | 0.51355 | 4.2338 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7619701.5323 | 8366620.896 | 8366620.896 | 62.4254 | 62.3028 | 1.0016 | 0.9986 | 684661.9344 | 894219.8248 | 459.62 | 0.52217 | 0 | 0 | 30.0087 | 27.1229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017992 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 534.9117 | 1367.9176 | 52.6199 | 43.2633 | 30.1475 | 1788.2013 | 61.3974 | 27.4963 | #NV | #NV | #NV | #NV | #NV | 69.1674 | 2.4117 | 1.2105 | 0.41887 | 4.6552 | 3.0081 | #NV | 0 | 100 | 561 | 338 | 88.5 | 102.79 | 97.48 | 317.5 | 3 | 80.97 | 36.56 | 4 | 32.01 | 44.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 86.3 | 0 | 32.88 | 64 | 64 | 83.02 | 77.64 | 68.27 | 0 | 97.48 | 2.12 | 79.65 | 37.49 | 88.53 | 21.82 | 102.79 | 110 | 0 | 16500 | 73.42 | 108.53 | 188.67 | 183.12 | 187.84 | 0 | 29.56 | 44.9 | 12073 | 80.97 | 36.56 | 32.01 | 7.86 | 36.56 | 0 | 604 | 443 | 457.3 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 325.7 | 0 | 319.4 | 97.57 | 16498 | 16500 | 335
03/26/22 10:11:36.217 | 633.8318 | 1369.8373 | 55.6054 | 44.5299 | 11.0755 | 30.4784 | 50.7032 | 0 | 1783.8271 | 76.7257 | 67.3814 | 9.3444 | 26.0155 | 68.4761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0251 | 460.2901 | 457.2401 | 461.3001 | 426.5801 | 458.6301 | 435.2601 | 325.8601 | 0.51411 | 4.6288 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7632788.0294 | 8348004.694 | 8348004.694 | 62.425 | 62.302 | 1.0015 | 0.99859 | 685713.1922 | 891533.3459 | 459.6101 | 0.51565 | 0 | 0 | 30.4784 | 26.0155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017993 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 536.3523 | 1367.9145 | 52.6437 | 43.262 | 30.1431 | 1788.1751 | 61.4534 | 27.4948 | #NV | #NV | #NV | #NV | #NV | 69.2453 | 2.4085 | 1.2265 | 0.41438 | 4.67 | 3.0248 | #NV | 0 | 100 | 562 | 340 | 88.75 | 102.87 | 97.74 | 320.6 | 3 | 81.12 | 36.61 | 4 | 32.06 | 44.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 86.5 | 0 | 32.93 | 64 | 64 | 83.25 | 77.78 | 68.38 | 0 | 97.74 | 2.12 | 79.77 | 37.55 | 88.8 | 21.74 | 102.89 | 110 | 0 | 16500 | 73.48 | 108.61 | 189.2 | 183.63 | 188.37 | 0 | 29.79 | 45.36 | 12078 | 81.15 | 36.61 | 32.06 | 7.87 | 36.61 | 0 | 604 | 443.9 | 457.2 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562.7 | 325 | 0 | 318.8 | 97.86 | 16497 | 16500 | 338
03/26/22 10:11:41.217 | 632.0114 | 1365.8891 | 55.6622 | 44.585 | 11.0772 | 29.823 | 50.7131 | 0 | 1780.9783 | 76.7872 | 67.4387 | 9.3486 | 27.0206 | 68.4852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0251 | 460.2901 | 457.2401 | 461.3001 | 426.5801 | 458.6301 | 435.2601 | 325.8601 | 0.51559 | 4.441 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7610312.3691 | 8343258.2425 | 8343258.2425 | 62.4248 | 62.3014 | 1.0015 | 0.99859 | 683625.11 | 890411.3622 | 459.6101 | 0.51565 | 0 | 0 | 29.823 | 27.0206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017999 | 0.01585 | 0.00479 | 0.0119 | 0.0119 | 537.7528 | 1367.8927 | 52.668 | 43.2615 | 30.1356 | 1788.1171 | 61.5097 | 27.4983 | #NV | #NV | #NV | #NV | #NV | 69.3229 | 2.409 | 1.2428 | 0.41292 | 4.6943 | 3.0415 | #NV | 0 | 100 | 562.8 | 337 | 88.95 | 102.96 | 97.88 | 321.1 | 3 | 81.24 | 36.65 | 4 | 32.1 | 44.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 86.6 | 0 | 32.96 | 64 | 64 | 83.35 | 77.84 | 68.44 | 0 | 97.88 | 2.13 | 79.83 | 37.59 | 88.93 | 21.76 | 102.99 | 110 | 0 | 16500 | 73.54 | 108.71 | 189.76 | 184.12 | 188.95 | 0 | 30.01 | 45.5 | 12084 | 81.23 | 36.65 | 32.1 | 7.87 | 36.65 | 0 | 604 | 443.7 | 457.2 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562.7 | 327 | 0 | 320.7 | 97.86 | 16498 | 16500 | 337
03/26/22 10:11:46.217 | 633.24 | 1368.2426 | 55.7224 | 44.6426 | 11.0798 | 28.5052 | 50.703 | 0 | 1784.271 | 76.8537 | 67.4997 | 9.354 | 28.8466 | 68.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0211 | 460.2801 | 457.2701 | 461.2901 | 427.4101 | 459.4401 | 436.2001 | 326.5201 | 0.51563 | 4.3563 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7623941.8503 | 8365535.3334 | 8365535.3334 | 62.4246 | 62.3008 | 1.0015 | 0.99858 | 684800.0493 | 892051.4603 | 459.6134 | 0.50985 | 0 | 0 | 28.5052 | 28.8466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.01799 | 0.015692 | 0.00479 | 0.0119 | 0.0119 | 539.1396 | 1367.8783 | 52.6924 | 43.2617 | 30.1223 | 1788.0839 | 61.5659 | 27.5083 | #NV | #NV | #NV | #NV | #NV | 69.4002 | 2.413 | 1.2588 | 0.41353 | 4.7127 | 3.0577 | #NV | 0 | 100 | 564 | 337 | 89.05 | 103.04 | 98 | 319.3 | 3 | 81.29 | 36.71 | 4 | 32.15 | 44.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 86.75 | 0 | 33.01 | 64 | 64 | 83.45 | 77.9 | 68.5 | 0 | 98 | 2.13 | 79.92 | 37.64 | 89.1 | 21.71 | 103.04 | 110 | 0 | 16500 | 73.6 | 108.79 | 190.26 | 184.63 | 189.46 | 0 | 30.07 | 45.41 | 12089 | 81.33 | 36.71 | 32.15 | 7.83 | 36.71 | 0 | 604 | 444.1 | 457.2 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563.9 | 326.2 | 0 | 319.9 | 98.07 | 16500 | 16500 | 336
03/26/22 10:11:51.217 | 634.7645 | 1371.3908 | 55.7858 | 44.7021 | 11.0836 | 29.491 | 50.712 | 0 | 1789.7984 | 76.926 | 67.566 | 9.36 | 27.5434 | 68.4365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0131 | 460.2801 | 457.2701 | 461.2801 | 427.8401 | 459.8601 | 436.6901 | 326.8401 | 0.5149 | 4.206 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7642938.9053 | 8396334.134 | 8396334.134 | 62.4245 | 62.3004 | 1.0015 | 0.99858 | 686269.9137 | 895010.8435 | 459.6101 | 0.50913 | 0 | 0 | 29.491 | 27.5434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017992 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 540.4714 | 1367.8469 | 52.7173 | 43.2632 | 30.1128 | 1788.0759 | 61.6221 | 27.5152 | #NV | #NV | #NV | #NV | #NV | 69.477 | 2.331 | 1.2751 | 0.41821 | 4.7079 | 3.0743 | #NV | 0 | 100 | 564.5 | 335 | 89.23 | 103.11 | 98.17 | 319.9 | 3 | 81.39 | 36.75 | 4 | 32.19 | 44.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 86.83 | 0 | 33.05 | 64 | 64 | 83.53 | 77.95 | 68.6 | 0 | 98.17 | 2.13 | 79.97 | 37.68 | 89.23 | 21.7 | 103.11 | 110 | 0 | 16500 | 73.66 | 108.9 | 190.75 | 185.1 | 189.99 | 0 | 30.06 | 45.37 | 12094 | 81.4 | 36.75 | 32.19 | 7.85 | 36.75 | 0 | 604 | 441.5 | 457.2 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564.7 | 327.6 | 0 | 321.3 | 98.21 | 16498 | 16500 | 337
03/26/22 10:11:56.216 | 634.8091 | 1370.9263 | 55.8204 | 44.7346 | 11.0858 | 30.3876 | 50.722 | 0 | 1789.4474 | 76.9663 | 67.603 | 9.3632 | 26.4764 | 68.4332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.013 | 460.28 | 457.27 | 461.28 | 427.84 | 459.86 | 436.69 | 326.84 | 0.51486 | 4.2504 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7644478.7675 | 8395132.2804 | 8395132.2804 | 62.4243 | 62.3 | 1.0015 | 0.99857 | 686138.4334 | 894629.0543 | 459.61 | 0.50913 | 0 | 0 | 30.3876 | 26.4764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017997 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 541.7843 | 1367.8378 | 52.7426 | 43.2655 | 30.1099 | 1788.0833 | 61.6783 | 27.5124 | #NV | #NV | #NV | #NV | #NV | 69.5534 | 2.3156 | 1.2913 | 0.42502 | 4.709 | 3.0907 | #NV | 0 | 100 | 564.7 | 338 | 89.35 | 103.18 | 98.28 | 321.6 | 3 | 81.49 | 36.78 | 4 | 32.21 | 44.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 86.98 | 0 | 33.06 | 64 | 64 | 83.68 | 78.04 | 68.68 | 0 | 98.28 | 2.13 | 80.06 | 37.69 | 89.38 | 21.69 | 103.18 | 110 | 0 | 16500 | 73.72 | 109 | 191.28 | 185.63 | 190.51 | 0 | 30.16 | 45.4 | 12099 | 81.49 | 36.78 | 32.21 | 7.86 | 36.78 | 0 | 603 | 443 | 457 | 25 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 565 | 325.9 | 0 | 319.6 | 98.26 | 16499 | 16500 | 336
03/26/22 10:12:01.217 | 634.6877 | 1370.1986 | 55.9184 | 44.8284 | 11.0899 | 30.1348 | 50.7123 | 0 | 1788.8281 | 77.0841 | 67.7128 | 9.3713 | 27.0634 | 68.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9911 | 460.2601 | 457.2701 | 461.2401 | 428.5201 | 460.4901 | 437.5701 | 327.3501 | 0.51577 | 4.1732 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7642785.1242 | 8399992.7143 | 8399992.7143 | 62.424 | 62.2991 | 1.0015 | 0.99857 | 685769.3995 | 894308.3433 | 459.5901 | 0.5048 | 0 | 0 | 30.1348 | 27.0634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017987 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 543.086 | 1367.8498 | 52.7683 | 43.2686 | 30.1109 | 1788.0751 | 61.7347 | 27.5055 | #NV | #NV | #NV | #NV | #NV | 69.6297 | 2.3252 | 1.3077 | 0.43416 | 4.711 | 3.1072 | #NV | 0 | 100 | 565.7 | 333 | 89.53 | 103.25 | 98.38 | 320.1 | 3 | 81.58 | 36.79 | 4 | 32.23 | 44.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 87.15 | 0 | 33.07 | 64 | 64 | 83.88 | 78.17 | 68.72 | 0 | 98.38 | 2.13 | 80.16 | 37.71 | 89.58 | 21.66 | 103.25 | 110 | 0 | 16500 | 73.78 | 109.08 | 191.78 | 186.07 | 191.02 | 0 | 30.11 | 45.2 | 12104 | 81.6 | 36.78 | 32.21 | 7.87 | 36.78 | 0 | 603 | 444.2 | 456.9 | 25 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 565.6 | 325.6 | 0 | 319.3 | 98.37 | 16501 | 16500 | 337
03/26/22 10:12:06.217 | 632.787 | 1367.0452 | 55.9632 | 44.8809 | 11.0824 | 30.5738 | 50.7106 | 0 | 1793.2821 | 77.1504 | 67.7823 | 9.3681 | 26.1287 | 68.3936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.991 | 460.26 | 457.27 | 461.24 | 428.52 | 460.49 | 437.57 | 327.35 | 0.51731 | 3.7359 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7620301.1136 | 8416838.227 | 8416838.227 | 62.4239 | 62.2985 | 1.0015 | 0.99856 | 684188.9517 | 896528.0122 | 459.59 | 0.5048 | 0 | 0 | 30.5738 | 26.1287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017982 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 544.3346 | 1367.8567 | 52.7945 | 43.2729 | 30.1108 | 1788.0922 | 61.7912 | 27.4993 | #NV | #NV | #NV | #NV | #NV | 69.7056 | 2.321 | 1.3242 | 0.44626 | 4.7243 | 3.1242 | #NV | 0 | 100 | 565.1 | 335 | 89.95 | 103.35 | 98.28 | 317.8 | 3 | 81.82 | 36.61 | 4 | 32.05 | 44.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 87.75 | 0 | 32.91 | 64 | 64 | 84.4 | 78.49 | 68.8 | 0 | 98.28 | 2.15 | 80.52 | 37.53 | 90 | 21.49 | 103.35 | 110 | 0 | 16500 | 73.82 | 109.16 | 192.25 | 186.51 | 191.5 | 0 | 30.25 | 45.23 | 12108 | 81.86 | 36.6 | 32.05 | 8.08 | 36.6 | 0 | 603 | 446.9 | 457 | 25 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 565.5 | 326.1 | 0 | 319.8 | 98.35 | 16499 | 16500 | 335
03/26/22 10:12:11.218 | 630.7235 | 1367.5871 | 55.9974 | 44.9554 | 11.042 | 31.2972 | 50.7244 | 0 | 1787.5121 | 77.2478 | 67.9109 | 9.3369 | 25.4719 | 68.4848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 460.23 | 457.25 | 461.21 | 429.51 | 461.57 | 438.69 | 328.14 | 0.52026 | 4.1565 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7596184.8901 | 8360942.1203 | 8360942.1203 | 62.4237 | 62.2976 | 1.0014 | 0.99855 | 684458.4893 | 893630.3364 | 459.5634 | 0.50338 | 0 | 0 | 31.2972 | 25.4719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017989 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 545.5669 | 1367.8656 | 52.821 | 43.2778 | 30.1167 | 1788.0851 | 61.8483 | 27.4871 | #NV | #NV | #NV | #NV | #NV | 69.7817 | 2.3167 | 1.3404 | 0.45966 | 4.7228 | 3.1414 | #NV | 0 | 100 | 568.1 | 336 | 90.6 | 103.45 | 98.8 | 323.3 | 3 | 82.22 | 36.59 | 4 | 32.04 | 44.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 88.4 | 0 | 32.91 | 64 | 64 | 85.05 | 78.89 | 69 | 0 | 98.8 | 2.17 | 80.91 | 37.53 | 90.68 | 21.2 | 103.45 | 110 | 0 | 16500 | 73.9 | 109.22 | 192.72 | 187 | 191.99 | 0 | 30.26 | 45 | 12113 | 82.25 | 36.6 | 32.06 | 8.04 | 36.6 | 0 | 603 | 445.6 | 457 | 25 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.2 | 327.7 | 0 | 321.4 | 98.82 | 16498 | 16500 | 338
03/26/22 10:12:16.218 | 629.3472 | 1366.844 | 56.0007 | 44.9913 | 11.0094 | 30.7925 | 50.7199 | 0 | 1785.329 | 77.3 | 67.9894 | 9.3106 | 25.8692 | 68.4567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 460.2301 | 457.2501 | 461.2101 | 429.5101 | 461.5701 | 438.6901 | 328.1401 | 0.5214 | 4.2605 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7579276.3807 | 8336051.4443 | 8336051.4443 | 62.4236 | 62.2973 | 1.0014 | 0.99855 | 684316.256 | 892590.3173 | 459.5634 | 0.50338 | 0 | 0 | 30.7925 | 25.8692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017991 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 546.7573 | 1367.8567 | 52.8475 | 43.2835 | 30.1184 | 1788.0477 | 61.9055 | 27.4795 | #NV | #NV | #NV | #NV | #NV | 69.8575 | 2.3175 | 1.3558 | 0.47428 | 4.7177 | 3.159 | #NV | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 91.2 | 20.95 | 103.52 | 110 | 0 | 16500 | 73.94 | 109.26 | 193.15 | 187.46 | 192.42 | 0 | 30.04 | 44.66 | 12118 | 82.57 | 36.71 | 32.15 | 7.86 | 36.71 | 0 | 603 | 449 | 457 | 25 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570.9 | 328.2 | 0 | 321.8 | 99.29 | 16501 | 16500 | 336
03/26/22 10:12:21.217 | 623.5504 | 1365.4298 | 55.9833 | 45.0496 | 10.9337 | 30.8917 | 50.717 | 0 | 1783.8271 | 77.413 | 68.1651 | 9.2479 | 25.8233 | 68.4567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 460.24 | 457.26 | 461.23 | 430.88 | 463.09 | 440.27 | 329.26 | 0.52804 | 4.3407 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7509708.6131 | 8264517.109 | 8264517.109 | 62.4235 | 62.2959 | 1.0014 | 0.99854 | 683379.4816 | 891762.2473 | 459.5767 | 0.50409 | 0 | 0 | 30.8917 | 25.8233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017997 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 547.9031 | 1367.8309 | 52.874 | 43.2898 | 30.119 | 1787.9954 | 61.963 | 27.473 | #NV | #NV | #NV | #NV | #NV | 69.933 | 2.323 | 1.3704 | 0.48973 | 4.694 | 3.1768 | #NV | 0 | 100 | 572.7 | 336 | 91.6 | 103.57 | 99.6 | 323.4 | 3 | 82.8 | 36.82 | 4 | 32.26 | 44.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 89.43 | 0 | 33.13 | 64 | 64 | 86 | 79.47 | 69.52 | 0 | 99.6 | 2.18 | 81.51 | 37.76 | 91.63 | 20.77 | 103.57 | 110 | 0 | 16500 | 73.98 | 109.28 | 193.65 | 187.88 | 192.93 | 0 | 29.79 | 44.49 | 12123 | 82.8 | 36.83 | 32.26 | 7.64 | 36.83 | 0 | 603 | 448 | 457 | 25 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572.3 | 329.1 | 0 | 322.8 | 99.53 | 16499 | 16500 | 336
03/26/22 10:12:26.216 | 620.5822 | 1365.8891 | 55.9393 | 45.0808 | 10.8585 | 31.3604 | 50.7162 | 0 | 1784.4516 | 77.5368 | 68.3514 | 9.1855 | 25.3399 | 68.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9881 | 460.2401 | 457.2601 | 461.2301 | 430.8801 | 463.0901 | 440.2701 | 329.2601 | 0.53057 | 4.421 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7474516.9877 | 8226099.7428 | 8226099.7428 | 62.4236 | 62.295 | 1.0014 | 0.99853 | 683592.7495 | 892104.4538 | 459.5767 | 0.50409 | 0 | 0 | 31.3604 | 25.3399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017994 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 548.9993 | 1367.8102 | 52.9003 | 43.2968 | 30.1218 | 1787.9582 | 62.0214 | 27.4651 | #NV | #NV | #NV | #NV | #NV | 70.0088 | 2.3239 | 1.3838 | 0.50597 | 4.6947 | 3.1961 | #NV | 0 | 100 | 573.6 | 337 | 91.9 | 103.62 | 99.76 | 325.4 | 3 | 82.98 | 36.89 | 4 | 32.31 | 44.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 89.73 | 0 | 33.19 | 64 | 64 | 86.33 | 79.67 | 69.8 | 0 | 99.76 | 2.18 | 81.7 | 37.83 | 91.93 | 20.63 | 103.62 | 110 | 0 | 16500 | 74.04 | 109.32 | 194.12 | 188.34 | 193.43 | 0 | 29.69 | 44.51 | 12128 | 82.99 | 36.9 | 32.33 | 7.45 | 36.9 | 0 | 603 | 450.5 | 457.1 | 25 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 330.2 | 0 | 323.8 | 99.83 | 16501 | 16500 | 336
03/26/22 10:12:31.217 | 617.8912 | 1365.7292 | 55.9166 | 45.0846 | 10.832 | 31.411 | 50.7094 | 0 | 1784.978 | 77.5861 | 68.4224 | 9.1638 | 25.0722 | 68.4654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 460.24 | 457.26 | 461.23 | 430.88 | 463.09 | 440.27 | 329.26 | 0.53288 | 4.4403 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7442259.8058 | 8193661.1934 | 8193661.1934 | 62.4236 | 62.2942 | 1.0014 | 0.99853 | 683532.5891 | 892311.2319 | 459.5767 | 0.50409 | 0 | 0 | 31.411 | 25.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017994 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 550.0705 | 1367.8069 | 52.9264 | 43.304 | 30.1253 | 1787.956 | 62.0804 | 27.4531 | #NV | #NV | #NV | #NV | #NV | 70.0846 | 2.3265 | 1.3962 | 0.52205 | 4.696 | 3.2159 | #NV | 0 | 100 | 576.1 | 334 | 92.35 | 103.64 | 100.14 | 324.7 | 3 | 83.24 | 37.01 | 4 | 32.43 | 44.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 90.1 | 0 | 33.3 | 64 | 64 | 86.7 | 79.89 | 70.08 | 0 | 100.14 | 2.18 | 81.92 | 37.95 | 92.48 | 20.35 | 103.64 | 110 | 0 | 16500 | 74.1 | 109.37 | 194.63 | 188.83 | 193.94 | 0 | 29.59 | 44.66 | 12133 | 83.31 | 37.03 | 32.45 | 7.18 | 37.03 | 0 | 603 | 451.6 | 456.8 | 25 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 331.1 | 0 | 324.7 | 100.19 | 16498 | 16500 | 334
03/26/22 10:12:36.217 | 612.106 | 1366.5601 | 55.7928 | 45.069 | 10.7239 | 31.0851 | 50.7244 | 0 | 1787.5534 | 77.8213 | 68.7491 | 9.0722 | 25.8666 | 68.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9981 | 460.2201 | 457.2501 | 461.2201 | 433.7601 | 466.2601 | 443.4401 | 331.5901 | 0.54172 | 4.5337 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7372568.9049 | 8124230.3474 | 8124230.3474 | 62.4238 | 62.2919 | 1.0015 | 0.99851 | 683954.5434 | 893564.81 | 459.5634 | 0.50338 | 0 | 0 | 31.0851 | 25.8666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.01799 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 551.1221 | 1367.8364 | 52.9522 | 43.3116 | 30.1289 | 1787.9558 | 62.1401 | 27.4416 | #NV | #NV | #NV | #NV | #NV | 70.1607 | 2.2956 | 1.4072 | 0.53772 | 4.6961 | 3.2365 | #NV | 0 | 100 | 577.8 | 335 | 92.68 | 103.67 | 100.49 | 326.5 | 3 | 83.43 | 37.16 | 4 | 32.56 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 90.45 | 0 | 33.45 | 64 | 64 | 87.05 | 80.1 | 70.32 | 0 | 100.49 | 2.18 | 82.13 | 38.11 | 92.78 | 20.18 | 103.67 | 110 | 0 | 16500 | 74.16 | 109.43 | 195.06 | 189.24 | 194.38 | 0 | 29.62 | 44.95 | 12138 | 83.46 | 37.17 | 32.59 | 6.98 | 37.17 | 0 | 603 | 453.8 | 456.9 | 25 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 332.4 | 0 | 326 | 100.57 | 16498 | 16500 | 336
03/26/22 10:12:41.217 | 610.3678 | 1367.2929 | 55.7234 | 45.043 | 10.6803 | 31.0923 | 50.7184 | 0 | 1787.5534 | 77.9395 | 68.9046 | 9.0349 | 25.799 | 68.4679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 460.2401 | 457.2701 | 461.2401 | 434.9501 | 467.5401 | 444.6501 | 332.5401 | 0.54482 | 4.6582 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7351705.2189 | 8096966.0401 | 8096966.0401 | 62.4239 | 62.291 | 1.0015 | 0.9985 | 684246.5145 | 893539.0018 | 459.5834 | 0.50335 | 0 | 0 | 31.0923 | 25.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017991 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 552.1283 | 1367.8453 | 52.9773 | 43.3191 | 30.1351 | 1787.9407 | 62.2011 | 27.4281 | #NV | #NV | #NV | #NV | #NV | 70.2376 | 2.2897 | 1.4163 | 0.55239 | 4.693 | 3.2593 | #NV | 0 | 100 | 578.9 | 338 | 92.95 | 103.69 | 100.64 | 328.1 | 3 | 83.59 | 37.29 | 4 | 32.69 | 44.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 90.65 | 0 | 33.54 | 64 | 64 | 87.2 | 80.19 | 70.61 | 0 | 100.64 | 2.18 | 82.25 | 38.2 | 92.98 | 20.09 | 103.69 | 110 | 0 | 16500 | 74.22 | 109.51 | 195.56 | 189.73 | 194.88 | 0 | 29.69 | 45.3 | 12143 | 83.6 | 37.29 | 32.69 | 6.78 | 37.29 | 0 | 603 | 457.2 | 456.9 | 25 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 334.4 | 0 | 328 | 100.73 | 16498 | 16500 | 335
03/26/22 10:12:46.216 | 608.6128 | 1367.3962 | 55.6771 | 45.0212 | 10.6559 | 31.1779 | 50.7139 | 0 | 1786.5573 | 78.0152 | 69.0007 | 9.0145 | 25.723 | 68.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.004 | 460.24 | 457.27 | 461.24 | 434.95 | 467.54 | 444.65 | 332.54 | 0.54639 | 4.8112 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7330748.3453 | 8067702.0951 | 8067702.0951 | 62.4241 | 62.2901 | 1.0015 | 0.99849 | 684378.6394 | 893040.6372 | 459.5833 | 0.50335 | 0 | 0 | 31.1779 | 25.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017992 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 553.0999 | 1367.8226 | 53.0021 | 43.3267 | 30.138 | 1787.9332 | 62.2627 | 27.4191 | #NV | #NV | #NV | #NV | #NV | 70.3147 | 2.2736 | 1.4244 | 0.56625 | 4.6942 | 3.2825 | #NV | 0 | 100 | 581 | 336 | 93.2 | 103.72 | 101.04 | 326.9 | 3 | 83.73 | 37.36 | 4 | 32.76 | 43.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 90.88 | 0 | 33.61 | 64 | 64 | 87.5 | 80.37 | 70.84 | 0 | 101.04 | 2.19 | 82.38 | 38.27 | 93.25 | 19.96 | 103.72 | 110 | 0 | 16500 | 74.3 | 109.61 | 196.04 | 190.2 | 195.37 | 0 | 29.78 | 45.47 | 12148 | 83.76 | 37.37 | 32.76 | 6.62 | 37.37 | 0 | 603 | 453.2 | 456.9 | 25 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581 | 333.3 | 0 | 326.9 | 101.04 | 16501 | 16500 | 336
03/26/22 10:12:51.216 | 602.994 | 1365.1666 | 55.4807 | 44.9064 | 10.5742 | 30.4212 | 50.7341 | 0 | 1786.5779 | 78.334 | 69.3863 | 8.9477 | 26.3143 | 68.4712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0061 | 460.1701 | 457.1901 | 461.1501 | 437.1901 | 469.9101 | 446.9801 | 334.2401 | 0.5543 | 4.7775 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7262614.1996 | 8008396.4213 | 8008396.4213 | 62.4246 | 62.2872 | 1.0015 | 0.99847 | 683272.259 | 893010.3792 | 459.5034 | 0.50344 | 0 | 0 | 30.4212 | 26.3143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017996 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 554.0274 | 1367.7795 | 53.0263 | 43.3343 | 30.1375 | 1787.9339 | 62.3252 | 27.4149 | #NV | #NV | #NV | #NV | #NV | 70.3921 | 2.2394 | 1.4309 | 0.57897 | 4.694 | 3.3072 | #NV | 0 | 100 | 581.6 | 337 | 93.4 | 103.72 | 101.15 | 329.1 | 3 | 83.83 | 37.44 | 4 | 32.84 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 91.1 | 0 | 33.69 | 64 | 64 | 87.73 | 80.51 | 70.98 | 0 | 101.15 | 2.19 | 82.51 | 38.36 | 93.4 | 19.87 | 103.72 | 110 | 0 | 16500 | 74.36 | 109.71 | 196.54 | 190.65 | 195.87 | 0 | 29.85 | 45.66 | 12153 | 83.85 | 37.45 | 32.84 | 6.42 | 37.45 | 0 | 602 | 459.1 | 456.4 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.8 | 334.3 | 0 | 327.9 | 101.18 | 16498 | 16500 | 336
03/26/22 10:12:56.217 | 602.6513 | 1366.9936 | 55.3865 | 44.8323 | 10.5542 | 30.3737 | 50.7308 | 0 | 1786.9547 | 78.5033 | 69.5708 | 8.9325 | 26.526 | 68.5298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0061 | 460.1701 | 457.1901 | 461.1501 | 437.1901 | 469.9101 | 446.9801 | 334.2401 | 0.55462 | 4.9334 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7258463.1065 | 7994557.8051 | 7994557.8051 | 62.4247 | 62.2863 | 1.0015 | 0.99846 | 683892.6161 | 892672.5372 | 459.5034 | 0.50344 | 0 | 0 | 30.3737 | 26.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017989 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 554.9395 | 1367.7625 | 53.0494 | 43.3414 | 30.1381 | 1787.9362 | 62.3895 | 27.41 | #NV | #NV | #NV | #NV | #NV | 70.471 | 2.2335 | 1.4352 | 0.5894 | 4.6934 | 3.3349 | #NV | 0 | 100 | 582.7 | 334 | 93.55 | 103.76 | 101.34 | 329.7 | 3 | 83.93 | 37.55 | 4 | 32.91 | 43.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 91.3 | 0 | 33.78 | 64 | 64 | 87.92 | 80.63 | 71.12 | 0 | 101.34 | 2.19 | 82.63 | 38.45 | 93.53 | 19.85 | 103.76 | 110 | 0 | 16500 | 74.44 | 109.81 | 197.03 | 191.1 | 196.3 | 0 | 29.83 | 45.66 | 12158 | 83.92 | 37.55 | 32.93 | 6.27 | 37.55 | 0 | 603 | 456.3 | 456.5 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.2 | 333.9 | 0 | 327.5 | 101.43 | 16500 | 16500 | 335
03/26/22 10:13:01.216 | 602.6406 | 1366.2814 | 55.2588 | 44.7 | 10.5588 | 30.2233 | 50.7217 | 0 | 1792.5182 | 78.7741 | 69.8328 | 8.9413 | 26.5098 | 68.5083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9971 | 460.1001 | 457.1201 | 461.0401 | 439.1001 | 471.7901 | 448.9101 | 335.6301 | 0.55693 | 4.5023 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7258222.0719 | 8028890.1341 | 8028890.1341 | 62.4252 | 62.2835 | 1.0015 | 0.99844 | 683840.8363 | 895931.9034 | 459.4201 | 0.50063 | 0 | 0 | 30.2233 | 26.5098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017984 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 555.8438 | 1367.7669 | 53.072 | 43.3481 | 30.1423 | 1787.965 | 62.4546 | 27.4007 | #NV | #NV | #NV | #NV | #NV | 70.5504 | 2.2314 | 1.4384 | 0.59843 | 4.7046 | 3.3637 | #NV | 0 | 100 | 583.6 | 336 | 93.58 | 103.79 | 101.5 | 328.8 | 3 | 83.93 | 37.61 | 4 | 32.99 | 43.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 91.43 | 0 | 33.84 | 64 | 64 | 88.05 | 80.7 | 71.32 | 0 | 101.5 | 2.19 | 82.7 | 38.52 | 93.55 | 19.86 | 103.79 | 110 | 0 | 16498 | 74.52 | 109.89 | 197.47 | 191.57 | 196.81 | 0 | 29.74 | 45.62 | 12163 | 83.93 | 37.61 | 32.99 | 6.18 | 37.61 | 0 | 603 | 459.7 | 456.5 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.4 | 337.1 | 0 | 330.7 | 101.63 | 16496 | 16498 | 335
03/26/22 10:13:06.216 | 603.0703 | 1365.9769 | 55.2119 | 44.6384 | 10.5735 | 30.1354 | 50.7186 | 0 | 1790.9441 | 78.8903 | 69.934 | 8.9563 | 26.5372 | 68.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9971 | 460.1001 | 457.1201 | 461.0401 | 439.1001 | 471.7901 | 448.9101 | 335.6301 | 0.55654 | 4.5526 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7263325.5907 | 8034254.0546 | 8034254.0546 | 62.4254 | 62.2829 | 1.0016 | 0.99844 | 683682.3323 | 895531.8044 | 459.4201 | 0.50063 | 0 | 0 | 30.1354 | 26.5372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017986 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 556.7439 | 1367.7928 | 53.0941 | 43.3545 | 30.1373 | 1787.9658 | 62.5205 | 27.4027 | #NV | #NV | #NV | #NV | #NV | 70.6305 | 2.1826 | 1.4405 | 0.60604 | 4.7051 | 3.3934 | #NV | 0 | 100 | 584.9 | 336 | 93.77 | 103.81 | 101.63 | 328.8 | 3 | 84.06 | 37.67 | 4 | 33.04 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 91.6 | 0 | 33.9 | 64 | 64 | 88.2 | 80.79 | 71.46 | 0 | 101.63 | 2.19 | 82.8 | 38.59 | 93.83 | 19.71 | 103.81 | 110 | 0 | 16496 | 74.58 | 109.99 | 197.97 | 192.04 | 197.31 | 0 | 29.8 | 45.85 | 12168 | 84.1 | 37.68 | 33.05 | 6.08 | 37.68 | 0 | 603 | 457.3 | 456.5 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.1 | 334.4 | 0 | 328 | 101.76 | 16496 | 16496 | 334
03/26/22 10:13:11.216 | 606.8295 | 1366.813 | 55.1099 | 44.4824 | 10.6275 | 29.4572 | 50.7209 | 0 | 1784.7974 | 79.1789 | 70.1686 | 9.0103 | 27.2832 | 68.5335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9921 | 460.0801 | 457.1101 | 460.9801 | 440.4701 | 473.1301 | 450.3601 | 336.6701 | 0.5548 | 4.8323 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7307826.7449 | 8056158.1485 | 8056158.1485 | 62.4258 | 62.2804 | 1.0016 | 0.99842 | 684113.9739 | 892036.8226 | 459.3901 | 0.49631 | 0 | 0 | 29.4572 | 27.2832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017987 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 557.6447 | 1367.8213 | 53.116 | 43.3608 | 30.1332 | 1787.9884 | 62.5867 | 27.4035 | #NV | #NV | #NV | #NV | #NV | 70.7109 | 2.1305 | 1.4421 | 0.61293 | 4.6969 | 3.4228 | #NV | 0 | 100 | 586.2 | 335 | 93.98 | 103.84 | 101.95 | 329.2 | 3 | 84.16 | 37.73 | 4 | 33.1 | 43.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 91.77 | 0 | 33.96 | 64 | 64 | 88.3 | 80.85 | 71.58 | 0 | 101.95 | 2.19 | 82.9 | 38.64 | 93.95 | 19.68 | 103.84 | 110 | 0 | 16491 | 74.66 | 110.1 | 198.48 | 192.53 | 197.8 | 0 | 29.89 | 46.03 | 12173 | 84.16 | 37.75 | 33.11 | 5.95 | 37.75 | 0 | 603 | 460.6 | 456.4 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.6 | 335.9 | 0 | 329.5 | 101.84 | 16493 | 16491 | 333
03/26/22 10:13:16.215 | 608.7535 | 1366.0956 | 55.0618 | 44.3951 | 10.6666 | 30.137 | 50.717 | 0 | 1790.6861 | 79.3448 | 70.2952 | 9.0496 | 26.727 | 68.5059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 460.08 | 457.11 | 460.98 | 440.47 | 473.13 | 450.36 | 336.67 | 0.55305 | 4.3774 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7331497.8839 | 8116999.3457 | 8116999.3457 | 62.426 | 62.2792 | 1.0016 | 0.99841 | 683757.1831 | 894966.2315 | 459.39 | 0.49631 | 0 | 0 | 30.137 | 26.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016242 | 0.017974 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 558.5605 | 1367.8448 | 53.1373 | 43.3661 | 30.1299 | 1788.0306 | 62.6543 | 27.4042 | #NV | #NV | #NV | #NV | #NV | 70.793 | 2.0872 | 1.4424 | 0.61773 | 4.6867 | 3.4542 | #NV | 0 | 100 | 585.8 | 336 | 94 | 103.86 | 101.93 | 329.2 | 3 | 84.18 | 37.77 | 4 | 33.14 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 91.85 | 0 | 34 | 64 | 64 | 88.42 | 80.93 | 71.7 | 0 | 101.93 | 2.19 | 82.95 | 38.69 | 94 | 19.67 | 103.86 | 110 | 0 | 16488 | 74.72 | 110.2 | 198.93 | 192.93 | 198.32 | 0 | 29.97 | 46.21 | 12178 | 84.19 | 37.79 | 33.14 | 5.88 | 37.79 | 0 | 603 | 461.1 | 456.6 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.8 | 335.6 | 0 | 329.2 | 101.88 | 16488 | 16488 | 336
03/26/22 10:13:21.216 | 609.7203 | 1364.5163 | 55.0278 | 44.325 | 10.7027 | 31.0813 | 50.717 | 0 | 1791.997 | 79.4834 | 70.3972 | 9.0862 | 25.6647 | 68.4997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.995 | 460.05 | 457.09 | 460.95 | 441.03 | 473.66 | 450.93 | 337.08 | 0.55284 | 4.1724 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7343845.6157 | 8146847.3466 | 8146847.3466 | 62.4261 | 62.2785 | 1.0016 | 0.99841 | 683301.0781 | 895995.6252 | 459.3634 | 0.49489 | 0 | 0 | 31.0813 | 25.6647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016245 | 0.017982 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 559.4534 | 1367.834 | 53.1583 | 43.3714 | 30.1315 | 1788.0546 | 62.7222 | 27.3984 | #NV | #NV | #NV | #NV | #NV | 70.8754 | 2.0995 | 1.4422 | 0.62185 | 4.696 | 3.4857 | #NV | 0 | 100 | 586.6 | 335 | 94.1 | 103.86 | 102.02 | 329.6 | 3 | 84.25 | 37.81 | 4 | 33.18 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 92 | 0 | 34.05 | 64 | 64 | 88.58 | 81.02 | 71.8 | 0 | 102.02 | 2.19 | 83.03 | 38.74 | 94.15 | 19.59 | 103.86 | 110 | 0 | 16484 | 74.8 | 110.28 | 199.39 | 193.36 | 198.77 | 0 | 30.18 | 46.5 | 12183 | 84.28 | 37.83 | 33.19 | 5.83 | 37.83 | 0 | 603 | 457.8 | 456.5 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587 | 335.5 | 0 | 329 | 102.09 | 16482 | 16484 | 336
03/26/22 10:13:26.216 | 614.5683 | 1365.6105 | 54.979 | 44.207 | 10.772 | 30.3779 | 50.7185 | 0 | 1785.0451 | 79.7318 | 70.5735 | 9.1584 | 26.4963 | 68.5208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 460.02 | 457.07 | 460.91 | 441.52 | 474.12 | 451.51 | 337.45 | 0.54908 | 4.3643 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7401476.6657 | 8187601.4334 | 8187601.4334 | 62.4264 | 62.2764 | 1.0016 | 0.99839 | 683518.2569 | 892116.6967 | 459.3333 | 0.49274 | 0 | 0 | 30.3779 | 26.4963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016245 | 0.01799 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 560.3618 | 1367.8297 | 53.1791 | 43.3762 | 30.1299 | 1788.0359 | 62.7908 | 27.3946 | #NV | #NV | #NV | #NV | #NV | 70.9586 | 2.103 | 1.4414 | 0.62502 | 4.6983 | 3.5178 | #NV | 0 | 100 | 587.5 | 335 | 94.38 | 103.91 | 102.17 | 331.4 | 3 | 84.39 | 37.87 | 4 | 33.23 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 92.17 | 0 | 34.13 | 64 | 64 | 88.75 | 81.12 | 71.88 | 0 | 102.17 | 2.19 | 83.14 | 38.82 | 94.35 | 19.51 | 103.91 | 110 | 0 | 16475 | 74.84 | 110.36 | 199.83 | 193.83 | 199.23 | 0 | 30.39 | 46.68 | 12188 | 84.4 | 37.88 | 33.24 | 5.76 | 37.88 | 0 | 603 | 459.4 | 456.7 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.4 | 337.8 | 0 | 331.3 | 102.16 | 16476 | 16475 | 335
03/26/22 10:13:31.216 | 614.5683 | 1366.1988 | 54.9717 | 44.1861 | 10.7856 | 30.0534 | 50.7164 | 0 | 1785.3548 | 79.7796 | 70.6068 | 9.1728 | 26.9663 | 68.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 460.02 | 457.07 | 460.91 | 441.52 | 474.12 | 451.51 | 337.45 | 0.54908 | 4.3643 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7401476.6657 | 8187601.4334 | 8187601.4334 | 62.4264 | 62.2764 | 1.0016 | 0.99839 | 683518.2569 | 892116.6967 | 459.3334 | 0.49274 | 0 | 0 | 30.0534 | 26.9663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017969 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 561.2545 | 1367.8226 | 53.1997 | 43.381 | 30.1303 | 1788.0057 | 62.8594 | 27.3898 | #NV | #NV | #NV | #NV | #NV | 71.0418 | 2.1063 | 1.4403 | 0.6279 | 4.6979 | 3.5491 | #NV | 0 | 100 | 587.9 | 333 | 94.48 | 103.96 | 102.24 | 330.9 | 3 | 84.46 | 37.93 | 4 | 33.29 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 92.28 | 0 | 34.19 | 64 | 64 | 88.88 | 81.2 | 71.92 | 0 | 102.24 | 2.19 | 83.19 | 38.89 | 94.45 | 19.51 | 103.96 | 110 | 0 | 16465 | 74.92 | 110.46 | 200.36 | 194.33 | 199.77 | 0 | 30.44 | 46.6 | 12193 | 84.45 | 37.93 | 33.29 | 5.7 | 37.93 | 0 | 603 | 457.1 | 456.7 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.9 | 337 | 0 | 330.5 | 102.24 | 16466 | 16465 | 335
03/26/22 10:13:36.215 | 620.5164 | 1369.218 | 54.9485 | 44.1012 | 10.8474 | 30.0912 | 50.723 | 0 | 1796.1671 | 79.9942 | 70.7561 | 9.2381 | 26.6885 | 68.5212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 460.0801 | 457.1701 | 460.9501 | 441.9901 | 474.4401 | 452.1501 | 337.8801 | 0.54451 | 3.7268 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7472672.1659 | 8309992.7172 | 8309992.7172 | 62.4266 | 62.2745 | 1.0016 | 0.99838 | 685325.3355 | 897655.039 | 459.4001 | 0.48542 | 0 | 0 | 30.0912 | 26.6885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017958 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 562.1707 | 1367.8336 | 53.2203 | 43.3855 | 30.1281 | 1788.0385 | 62.9287 | 27.3875 | #NV | #NV | #NV | #NV | #NV | 71.1259 | 2.1084 | 1.4388 | 0.63015 | 4.7342 | 3.5809 | #NV | 0 | 100 | 587.6 | 334 | 94.53 | 103.96 | 102.19 | 329.4 | 3 | 84.49 | 37.96 | 4 | 33.31 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 92.3 | 0 | 34.24 | 64 | 64 | 88.93 | 81.21 | 72 | 0 | 102.19 | 2.19 | 83.21 | 38.93 | 94.55 | 19.44 | 103.96 | 110 | 0 | 16455 | 74.98 | 110.51 | 200.81 | 194.74 | 200.2 | 0 | 30.41 | 46.49 | 12198 | 84.52 | 37.97 | 33.33 | 5.66 | 37.97 | 0 | 603 | 459.5 | 456.7 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.2 | 336.6 | 0 | 330.1 | 102.3 | 16458 | 16455 | 335
03/26/22 10:13:41.216 | 624.336 | 1371.6075 | 54.943 | 44.0479 | 10.8951 | 30.1181 | 50.7304 | 0 | 1795.8781 | 80.1591 | 70.8711 | 9.2881 | 26.6634 | 68.5459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0151 | 460.1201 | 457.2301 | 460.9901 | 442.1601 | 474.4901 | 452.3901 | 338.0501 | 0.54146 | 3.7437 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7518577.1783 | 8353228.8419 | 8353228.8419 | 62.4267 | 62.2733 | 1.0017 | 0.99837 | 686521.6165 | 897497.9066 | 459.4468 | 0.48246 | 0 | 0 | 30.1181 | 26.6634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017959 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 563.0851 | 1367.8342 | 53.2407 | 43.39 | 30.1238 | 1788.0983 | 62.9983 | 27.3869 | #NV | #NV | #NV | #NV | #NV | 71.2102 | 2.109 | 1.4369 | 0.63211 | 4.7901 | 3.6121 | #NV | 0 | 100 | 588.6 | 336 | 94.73 | 103.96 | 102.37 | 331.9 | 3 | 84.6 | 38.03 | 4 | 33.38 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 92.5 | 0 | 34.29 | 64 | 64 | 89.05 | 81.3 | 72.12 | 0 | 102.37 | 2.19 | 83.33 | 38.99 | 94.73 | 19.35 | 103.96 | 110 | 0 | 16446 | 75.06 | 110.57 | 201.24 | 195.21 | 200.66 | 0 | 30.38 | 46.39 | 12203 | 84.6 | 38.03 | 33.38 | 5.61 | 38.03 | 0 | 603 | 460.1 | 456.7 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.6 | 338.4 | 0 | 331.9 | 102.37 | 16447 | 16446 | 336
03/26/22 10:13:46.216 | 624.9904 | 1372.5159 | 54.9432 | 44.0375 | 10.9057 | 30.0921 | 50.7316 | 0 | 1793.6588 | 80.1962 | 70.8971 | 9.2991 | 26.7423 | 68.5418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.015 | 460.12 | 457.23 | 460.99 | 442.16 | 474.49 | 452.39 | 338.05 | 0.54089 | 3.8249 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7526387.1912 | 8354095.8638 | 8354095.8638 | 62.4267 | 62.2731 | 1.0017 | 0.99837 | 686903.9252 | 897047.6746 | 459.4467 | 0.48246 | 0 | 0 | 30.0921 | 26.7423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017963 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 564.0092 | 1367.8782 | 53.2612 | 43.3945 | 30.1212 | 1788.1185 | 63.068 | 27.3842 | #NV | #NV | #NV | #NV | #NV | 71.2947 | 2.1236 | 1.4348 | 0.63383 | 4.806 | 3.6429 | #NV | 0 | 100 | 588.4 | 334 | 94.85 | 103.98 | 102.33 | 330.9 | 3 | 84.68 | 38.08 | 4 | 33.43 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 92.58 | 0 | 34.32 | 64 | 64 | 89.15 | 81.36 | 72.18 | 0 | 102.33 | 2.19 | 83.37 | 39.03 | 94.88 | 19.29 | 103.98 | 110 | 0 | 16430 | 75.12 | 110.65 | 201.78 | 195.69 | 201.13 | 0 | 30.29 | 46.27 | 12208 | 84.69 | 38.08 | 33.43 | 5.56 | 38.08 | 0 | 603 | 458.5 | 456.8 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588 | 335.5 | 0 | 329 | 102.26 | 16434 | 16430 | 334
03/26/22 10:13:51.216 | 628.1499 | 1372.2475 | 54.9533 | 43.9968 | 10.9565 | 31.1533 | 50.7166 | 0 | 1788.2811 | 80.3784 | 71.0261 | 9.3523 | 25.1591 | 68.4807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.025 | 460.2 | 457.29 | 461.03 | 442.04 | 474.13 | 452.12 | 337.92 | 0.53796 | 4.0396 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7565268.7328 | 8373254.5018 | 8373254.5018 | 62.4268 | 62.2717 | 1.0017 | 0.99836 | 686841.4443 | 893684.1672 | 459.5067 | 0.4824 | 0 | 0 | 31.1533 | 25.1591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017963 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 564.9441 | 1367.9259 | 53.2816 | 43.3989 | 30.1233 | 1788.1098 | 63.1381 | 27.3749 | #NV | #NV | #NV | #NV | #NV | 71.3796 | 2.1527 | 1.4325 | 0.63532 | 4.8025 | 3.6732 | #NV | 0 | 100 | 588.5 | 332 | 94.93 | 104.01 | 102.35 | 331.3 | 3 | 84.72 | 38.09 | 4 | 33.44 | 43.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 92.68 | 0 | 34.35 | 64 | 64 | 89.27 | 81.43 | 72.24 | 0 | 102.35 | 2.19 | 83.43 | 39.06 | 94.95 | 19.28 | 104.01 | 110 | 0 | 16421 | 75.18 | 110.69 | 202.17 | 196.11 | 201.66 | 0 | 30.31 | 46.29 | 12213 | 84.73 | 38.09 | 33.45 | 5.57 | 38.09 | 0 | 603 | 456.5 | 456.9 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.4 | 335.9 | 0 | 329.4 | 102.33 | 16419 | 16421 | 333
03/26/22 10:13:56.216 | 629.0578 | 1371.8656 | 54.9615 | 43.9861 | 10.9754 | 31.1467 | 50.7141 | 0 | 1788.5082 | 80.4513 | 71.0783 | 9.3729 | 25.1434 | 68.5195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.025 | 460.2 | 457.29 | 461.03 | 442.04 | 474.13 | 452.12 | 337.92 | 0.53718 | 3.9314 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7576151.1545 | 8392614.2622 | 8392614.2622 | 62.4268 | 62.2711 | 1.0017 | 0.99836 | 686649.9039 | 893791.8762 | 459.5067 | 0.4824 | 0 | 0 | 31.1467 | 25.1434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017969 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 565.8636 | 1367.9453 | 53.3021 | 43.4034 | 30.126 | 1788.14 | 63.2084 | 27.3648 | #NV | #NV | #NV | #NV | #NV | 71.4649 | 2.1724 | 1.43 | 0.6366 | 4.7877 | 3.7034 | #NV | 0 | 100 | 589.1 | 332 | 95.2 | 104.01 | 102.45 | 326.7 | 3 | 84.88 | 38.17 | 4 | 33.51 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 92.83 | 0 | 34.41 | 64 | 64 | 89.4 | 81.51 | 72.28 | 0 | 102.45 | 2.19 | 83.51 | 39.13 | 95.18 | 19.15 | 104.01 | 110 | 0 | 16404 | 75.26 | 110.75 | 202.65 | 196.53 | 202.11 | 0 | 30.28 | 46.29 | 12218 | 84.86 | 38.17 | 33.53 | 5.52 | 38.17 | 0 | 603 | 460.4 | 456.8 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.9 | 336.9 | 0 | 330.4 | 102.42 | 16406 | 16404 | 335
03/26/22 10:14:01.215 | 630.4655 | 1372.041 | 54.9758 | 43.9773 | 10.9985 | 30.4749 | 50.7195 | 0 | 1786.0102 | 80.5451 | 71.1464 | 9.3988 | 25.9646 | 68.5678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.025 | 460.2 | 457.29 | 461.03 | 442.04 | 474.13 | 452.12 | 337.92 | 0.53598 | 3.9738 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7592454.4614 | 8404724.4975 | 8404724.4975 | 62.4268 | 62.2704 | 1.0017 | 0.99835 | 686737.0502 | 892536.0219 | 459.5067 | 0.4824 | 0 | 0 | 30.4749 | 25.9646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017965 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 566.7845 | 1367.9704 | 53.3226 | 43.408 | 30.126 | 1788.1443 | 63.2789 | 27.3569 | #NV | #NV | #NV | #NV | #NV | 71.5503 | 2.1934 | 1.4274 | 0.63776 | 4.7854 | 3.7331 | #NV | 0 | 100 | 588.6 | 333 | 95.2 | 104.03 | 102.37 | 327.6 | 3 | 84.88 | 38.23 | 4 | 33.56 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 92.92 | 0 | 34.48 | 64 | 64 | 89.5 | 81.57 | 72.38 | 0 | 102.37 | 2.19 | 83.57 | 39.19 | 95.18 | 19.17 | 104.03 | 110 | 0 | 16387 | 75.3 | 110.81 | 203.15 | 197 | 202.59 | 0 | 30.23 | 46.25 | 12223 | 84.86 | 38.23 | 33.56 | 5.46 | 38.23 | 0 | 603 | 457.5 | 456.9 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.4 | 336.4 | 0 | 329.9 | 102.33 | 16389 | 16387 | 335
03/26/22 10:14:06.215 | 631.9432 | 1371.6643 | 55.0036 | 43.9762 | 11.0274 | 29.7239 | 50.7313 | 0 | 1786.0154 | 80.6688 | 71.2374 | 9.4314 | 27.3148 | 68.5294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.033 | 460.3 | 457.32 | 461.07 | 441.63 | 473.46 | 451.45 | 337.54 | 0.53413 | 3.7915 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7609517.8294 | 8435248.1237 | 8435248.1237 | 62.4267 | 62.2695 | 1.0017 | 0.99835 | 686547.1833 | 892528.4972 | 459.5633 | 0.48814 | 0 | 0 | 29.7239 | 27.3148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017965 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 567.7132 | 1367.995 | 53.3432 | 43.4126 | 30.1212 | 1788.1446 | 63.35 | 27.3578 | #NV | #NV | #NV | #NV | #NV | 71.6363 | 2.21 | 1.4246 | 0.63886 | 4.7853 | 3.7622 | #NV | 0 | 100 | 588.5 | 332 | 95.25 | 104.03 | 102.35 | 329.2 | 3 | 84.9 | 38.25 | 4 | 33.59 | 43.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 92.98 | 0 | 34.51 | 64 | 64 | 89.53 | 81.58 | 72.44 | 0 | 102.35 | 2.19 | 83.6 | 39.23 | 95.28 | 19.13 | 104.03 | 110 | 0 | 16375 | 75.36 | 110.85 | 203.65 | 197.43 | 203.07 | 0 | 30.16 | 46.21 | 12228 | 84.9 | 38.25 | 33.59 | 5.46 | 38.25 | 0 | 603 | 457.8 | 456.9 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.8 | 333.7 | 0 | 327.2 | 102.4 | 16379 | 16375 | 332
03/26/22 10:14:11.215 | 633.5558 | 1373.2797 | 55.0231 | 43.9806 | 11.0426 | 29.9939 | 50.7366 | 0 | 1788.4462 | 80.7377 | 71.2892 | 9.4485 | 26.9197 | 68.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0311 | 460.3201 | 457.3101 | 461.0601 | 441.3601 | 473.0401 | 450.9601 | 337.2501 | 0.53231 | 3.694 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7629137.5803 | 8461433.9009 | 8461433.9009 | 62.4267 | 62.269 | 1.0016 | 0.99834 | 687354.8008 | 893737.4909 | 459.5634 | 0.49032 | 0 | 0 | 29.9939 | 26.9197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017958 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 568.6387 | 1368.0326 | 53.364 | 43.4174 | 30.1205 | 1788.1764 | 63.421 | 27.352 | #NV | #NV | #NV | #NV | #NV | 71.7223 | 2.2419 | 1.4217 | 0.63988 | 4.7681 | 3.7908 | #NV | 0 | 100 | 588.4 | 332 | 95.38 | 103.99 | 102.33 | 329.6 | 3 | 84.98 | 38.31 | 4 | 33.64 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.05 | 0 | 34.55 | 64 | 64 | 89.63 | 81.64 | 72.48 | 0 | 102.33 | 2.19 | 83.63 | 39.27 | 95.4 | 19 | 103.99 | 110 | 0 | 16365 | 75.42 | 110.91 | 204.05 | 197.91 | 203.49 | 0 | 30.15 | 46.26 | 12233 | 84.99 | 38.31 | 33.64 | 5.42 | 38.31 | 0 | 603 | 457.6 | 456.8 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.6 | 333.6 | 0 | 327.1 | 102.37 | 16363 | 16365 | 331
03/26/22 10:14:16.215 | 633.452 | 1371.3959 | 55.0443 | 43.9881 | 11.0562 | 30.5922 | 50.7259 | 0 | 1790.7687 | 80.8037 | 71.3396 | 9.4641 | 26.1321 | 68.5373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0281 | 460.3501 | 457.3001 | 461.0701 | 441.0601 | 472.7201 | 450.5501 | 337.0001 | 0.53201 | 3.4295 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7628353.3487 | 8482266.4488 | 8482266.4488 | 62.4267 | 62.2686 | 1.0016 | 0.99834 | 686599.7685 | 894924.8059 | 459.5734 | 0.49466 | 0 | 0 | 30.5922 | 26.1321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017955 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 569.551 | 1368.044 | 53.3848 | 43.4223 | 30.1207 | 1788.1896 | 63.4922 | 27.3437 | #NV | #NV | #NV | #NV | #NV | 71.8084 | 2.2538 | 1.4188 | 0.64085 | 4.772 | 3.8186 | #NV | 0 | 100 | 588.3 | 330 | 95.4 | 103.97 | 102.31 | 327.6 | 3 | 84.99 | 38.33 | 4 | 33.66 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.18 | 0 | 34.59 | 64 | 64 | 89.78 | 81.73 | 72.56 | 0 | 102.31 | 2.19 | 83.72 | 39.31 | 95.42 | 18.96 | 103.97 | 110 | 0 | 16350 | 75.48 | 110.97 | 204.53 | 198.29 | 204 | 0 | 30.13 | 46.32 | 12238 | 85 | 38.35 | 33.68 | 5.38 | 38.35 | 0 | 603 | 455.5 | 456.8 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.2 | 333.1 | 0 | 326.7 | 102.3 | 16352 | 16350 | 330
03/26/22 10:14:21.215 | 633.6747 | 1368.9858 | 55.0919 | 44.0125 | 11.0794 | 30.6129 | 50.7279 | 0 | 1789.8964 | 80.9278 | 71.4361 | 9.4917 | 26.2449 | 68.5872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0291 | 460.3701 | 457.2901 | 461.1001 | 440.2401 | 471.9001 | 449.5601 | 336.3601 | 0.53081 | 3.1694 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7631026.6145 | 8505865.1082 | 8505865.1082 | 62.4266 | 62.2675 | 1.0016 | 0.99833 | 685202.3397 | 894445.8097 | 459.5867 | 0.49972 | 0 | 0 | 30.6129 | 26.2449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016215 | 0.017957 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 570.4541 | 1368.0356 | 53.4057 | 43.4274 | 30.1178 | 1788.1907 | 63.5635 | 27.3402 | #NV | #NV | #NV | #NV | #NV | 71.8946 | 2.2471 | 1.4157 | 0.64181 | 4.7726 | 3.8458 | #NV | 0 | 100 | 588.4 | 331 | 95.55 | 103.97 | 102.33 | 327.6 | 3 | 85.07 | 38.4 | 4 | 33.71 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.3 | 0 | 34.63 | 64 | 64 | 89.83 | 81.74 | 72.64 | 0 | 102.33 | 2.19 | 83.79 | 39.35 | 95.55 | 18.89 | 103.97 | 110 | 0 | 16341 | 75.52 | 111.03 | 204.93 | 198.72 | 204.43 | 0 | 30.07 | 46.27 | 12243 | 85.07 | 38.4 | 33.73 | 5.35 | 38.4 | 0 | 603 | 456.5 | 456.8 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.2 | 332.3 | 0 | 325.8 | 102.3 | 16343 | 16341 | 330
03/26/22 10:14:26.215 | 633.9433 | 1368.5729 | 55.1129 | 44.0253 | 11.0875 | 30.4005 | 50.7222 | 0 | 1786.9856 | 80.975 | 71.4739 | 9.5011 | 26.3809 | 68.5748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.029 | 460.37 | 457.29 | 461.1 | 440.24 | 471.9 | 449.56 | 336.36 | 0.53058 | 3.2544 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7634053.7855 | 8500544.9195 | 8500544.9195 | 62.4265 | 62.2671 | 1.0016 | 0.99833 | 684994.6941 | 892986.9932 | 459.5867 | 0.49972 | 0 | 0 | 30.4005 | 26.3809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016214 | 0.017963 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 571.357 | 1368.0291 | 53.4268 | 43.4326 | 30.1124 | 1788.1827 | 63.6352 | 27.3393 | #NV | #NV | #NV | #NV | #NV | 71.9812 | 2.2439 | 1.4126 | 0.64281 | 4.7734 | 3.8724 | #NV | 0 | 100 | 588.9 | 331 | 95.68 | 103.97 | 102.38 | 325.6 | 3 | 85.12 | 38.43 | 4 | 33.75 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.38 | 0 | 34.66 | 64 | 64 | 89.9 | 81.79 | 72.68 | 0 | 102.38 | 2.19 | 83.83 | 39.37 | 95.68 | 18.84 | 103.97 | 110 | 0 | 16331 | 75.58 | 111.07 | 205.44 | 199.17 | 204.85 | 0 | 29.99 | 46.25 | 12248 | 85.15 | 38.44 | 33.76 | 5.35 | 38.44 | 0 | 603 | 455.9 | 456.9 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.3 | 333.8 | 0 | 327.3 | 102.31 | 16331 | 16331 | 332
03/26/22 10:14:31.215 | 633.5541 | 1365.6776 | 55.1651 | 44.0607 | 11.1044 | 30.293 | 50.7213 | 0 | 1789.0965 | 81.083 | 71.5614 | 9.5216 | 26.6943 | 68.5604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.026 | 460.35 | 457.27 | 461.12 | 439.36 | 471.22 | 448.67 | 335.72 | 0.5299 | 2.84 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7629232.4072 | 8529045.9902 | 8529045.9902 | 62.4264 | 62.2663 | 1.0016 | 0.99833 | 683543.0625 | 894032.0509 | 459.58 | 0.50263 | 0 | 0 | 30.293 | 26.6943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017954 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 572.2504 | 1368.0157 | 53.4482 | 43.4382 | 30.1142 | 1788.1954 | 63.7071 | 27.3279 | #NV | #NV | #NV | #NV | #NV | 72.0679 | 2.2488 | 1.4097 | 0.64387 | 4.7702 | 3.8987 | #NV | 0 | 100 | 588.9 | 329 | 95.83 | 103.97 | 102.42 | 327.4 | 3 | 85.23 | 38.51 | 4 | 33.83 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.5 | 0 | 34.73 | 64 | 64 | 89.98 | 81.85 | 72.72 | 0 | 102.42 | 2.19 | 83.89 | 39.45 | 95.85 | 18.72 | 103.97 | 110 | 0 | 16317 | 75.62 | 111.12 | 205.84 | 199.57 | 205.28 | 0 | 30.03 | 46.54 | 12253 | 85.24 | 38.51 | 33.83 | 5.3 | 38.51 | 0 | 603 | 456.6 | 456.9 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.9 | 331.7 | 0 | 325.3 | 102.42 | 16319 | 16317 | 331
03/26/22 10:14:36.215 | 633.7791 | 1366.4878 | 55.1883 | 44.0777 | 11.1106 | 29.4516 | 50.7294 | 0 | 1790.6758 | 81.1268 | 71.5975 | 9.5292 | 27.5041 | 68.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0231 | 460.3301 | 457.2601 | 461.1301 | 438.7901 | 470.8201 | 448.2201 | 335.3601 | 0.52914 | 2.7071 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7631217.7145 | 8542318.4925 | 8542318.4925 | 62.4263 | 62.266 | 1.0016 | 0.99832 | 683490.571 | 894763.9401 | 459.5734 | 0.50337 | 0 | 0 | 29.4516 | 27.5041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.01795 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 573.1428 | 1368.0098 | 53.4696 | 43.4439 | 30.1105 | 1788.1929 | 63.7791 | 27.3238 | #NV | #NV | #NV | #NV | #NV | 72.1547 | 2.2538 | 1.4065 | 0.64493 | 4.7688 | 3.924 | #NV | 0 | 100 | 588.3 | 332 | 95.85 | 103.97 | 102.31 | 325.4 | 3 | 85.24 | 38.56 | 4 | 33.89 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.53 | 0 | 34.79 | 64 | 64 | 90.02 | 81.88 | 72.78 | 0 | 102.31 | 2.19 | 83.92 | 39.52 | 95.85 | 18.72 | 103.97 | 110 | 0 | 16300 | 75.68 | 111.18 | 206.28 | 199.97 | 205.76 | 0 | 30.11 | 46.66 | 12258 | 85.24 | 38.57 | 33.89 | 5.26 | 38.57 | 0 | 603 | 451.7 | 456.8 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.3 | 332.6 | 0 | 326.1 | 102.31 | 16301 | 16300 | 330
03/26/22 10:14:41.215 | 636.7969 | 1371.2979 | 55.2273 | 44.1067 | 11.1206 | 29.6466 | 50.7224 | 0 | 1791.7338 | 81.1958 | 71.6554 | 9.5404 | 27.3485 | 68.5724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0191 | 460.2901 | 457.2501 | 461.1201 | 438.3101 | 470.4601 | 447.8101 | 335.0301 | 0.52612 | 2.9368 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7667660.6727 | 8556910.6908 | 8556910.6908 | 62.4262 | 62.2655 | 1.0016 | 0.99832 | 686162.3738 | 895312.2122 | 459.5534 | 0.50121 | 0 | 0 | 29.6466 | 27.3485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016211 | 0.017941 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 574.0404 | 1368.0248 | 53.4911 | 43.4498 | 30.1053 | 1788.1817 | 63.8512 | 27.3222 | #NV | #NV | #NV | #NV | #NV | 72.2415 | 2.2641 | 1.4034 | 0.64603 | 4.7582 | 3.9486 | #NV | 0 | 100 | 588.1 | 330 | 95.98 | 103.97 | 102.28 | 326.9 | 3 | 85.32 | 38.61 | 4 | 33.93 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.58 | 0 | 34.81 | 64 | 64 | 90.13 | 81.94 | 72.86 | 0 | 102.28 | 2.19 | 83.95 | 39.54 | 95.95 | 18.67 | 103.97 | 110 | 0 | 16290 | 75.72 | 111.24 | 206.7 | 200.43 | 206.19 | 0 | 30.04 | 46.58 | 12263 | 85.3 | 38.61 | 33.93 | 5.22 | 38.61 | 0 | 603 | 455.3 | 456.9 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.1 | 334.1 | 0 | 327.6 | 102.28 | 16290 | 16290 | 329
03/26/22 10:14:46.214 | 636.8178 | 1369.3728 | 55.2731 | 44.1413 | 11.1318 | 29.5928 | 50.7329 | 0 | 1797.3283 | 81.2719 | 71.7198 | 9.5521 | 27.4069 | 68.5414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 460.3101 | 457.2701 | 461.1601 | 437.7801 | 470.0101 | 447.3301 | 334.6801 | 0.52555 | 2.4678 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7667852.8645 | 8596235.1696 | 8596235.1696 | 62.4261 | 62.2648 | 1.0016 | 0.99832 | 685387.4687 | 898127.6873 | 459.5801 | 0.50263 | 0 | 0 | 29.5928 | 27.4069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017928 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 574.9398 | 1368.0464 | 53.5129 | 43.456 | 30.102 | 1788.19 | 63.9235 | 27.3188 | #NV | #NV | #NV | #NV | #NV | 72.3285 | 2.2762 | 1.4003 | 0.6472 | 4.7685 | 3.9725 | #NV | 0 | 100 | 588.3 | 328 | 95.95 | 103.94 | 102.31 | 325 | 3 | 85.3 | 38.65 | 4 | 33.96 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.63 | 0 | 34.86 | 64 | 64 | 90.2 | 81.98 | 72.88 | 0 | 102.31 | 2.19 | 83.97 | 39.6 | 95.92 | 18.66 | 103.94 | 110 | 0 | 16281 | 75.78 | 111.28 | 207.02 | 200.75 | 206.54 | 0 | 29.97 | 46.59 | 12268 | 85.29 | 38.65 | 33.96 | 5.2 | 38.65 | 0 | 603 | 451.9 | 456.9 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.1 | 331.3 | 0 | 324.9 | 102.28 | 16283 | 16281 | 331
03/26/22 10:14:51.215 | 636.8651 | 1368.4542 | 55.3132 | 44.1731 | 11.1402 | 29.302 | 50.7257 | 0 | 1799.8469 | 81.3354 | 71.774 | 9.5614 | 27.3282 | 68.5212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.021 | 460.33 | 457.29 | 461.19 | 437.26 | 469.52 | 446.74 | 334.29 | 0.5249 | 2.2072 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7668148.0535 | 8616484.2612 | 8616484.2612 | 62.426 | 62.2642 | 1.0016 | 0.99831 | 684925.7544 | 899380.0699 | 459.6034 | 0.50333 | 0 | 0 | 29.302 | 27.3282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017921 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 575.8154 | 1368.0251 | 53.5348 | 43.4625 | 30.0972 | 1788.1997 | 63.996 | 27.3143 | #NV | #NV | #NV | #NV | #NV | 72.4156 | 2.2563 | 1.3972 | 0.64847 | 4.7908 | 3.996 | #NV | 0 | 100 | 587 | 330 | 95.95 | 103.94 | 102.1 | 325.8 | 3 | 85.29 | 38.67 | 4 | 33.98 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.63 | 0 | 34.88 | 64 | 64 | 90.2 | 81.98 | 72.96 | 0 | 102.1 | 2.19 | 83.97 | 39.61 | 95.92 | 18.63 | 103.92 | 110 | 0 | 16271 | 75.82 | 111.34 | 207.44 | 201.13 | 206.95 | 0 | 30.03 | 46.71 | 12272 | 85.3 | 38.67 | 33.99 | 5.22 | 38.67 | 0 | 603 | 452.7 | 457.1 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.7 | 330.8 | 0 | 324.4 | 102.21 | 16273 | 16271 | 330
03/26/22 10:14:56.214 | 636.207 | 1365.7756 | 55.3497 | 44.2035 | 11.1462 | 29.8584 | 50.7224 | 0 | 1796.3993 | 81.3895 | 71.8207 | 9.5688 | 26.6189 | 68.5567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.021 | 460.33 | 457.29 | 461.19 | 437.26 | 469.52 | 446.74 | 334.29 | 0.52544 | 2.2091 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7660602.1039 | 8608937.9494 | 8608937.9494 | 62.4259 | 62.2639 | 1.0016 | 0.99831 | 683906.5243 | 898070.6474 | 459.6034 | 0.50333 | 0 | 0 | 29.8584 | 26.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017924 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 576.6835 | 1367.99 | 53.557 | 43.4691 | 30.0926 | 1788.2166 | 64.0687 | 27.3102 | #NV | #NV | #NV | #NV | #NV | 72.5029 | 2.2316 | 1.3941 | 0.64984 | 4.8174 | 4.0186 | #NV | 0 | 100 | 587.3 | 328 | 95.98 | 103.92 | 102.14 | 325 | 3 | 85.32 | 38.69 | 4 | 34 | 43.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.7 | 0 | 34.9 | 64 | 64 | 90.25 | 82.01 | 72.98 | 0 | 102.14 | 2.19 | 84.02 | 39.64 | 95.98 | 18.6 | 103.92 | 110 | 0 | 16262 | 75.86 | 111.38 | 207.79 | 201.52 | 207.3 | 0 | 30.07 | 46.81 | 12277 | 85.32 | 38.69 | 34 | 5.24 | 38.69 | 0 | 604 | 454.1 | 457.2 | 25 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.8 | 332 | 0 | 325.5 | 102.05 | 16262 | 16262 | 327
03/26/22 10:15:01.215 | 634.9241 | 1363.2312 | 55.369 | 44.2201 | 11.1489 | 30.4187 | 50.7317 | 0 | 1793.8601 | 81.4169 | 71.8446 | 9.5723 | 26.0048 | 68.5624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.021 | 460.33 | 457.29 | 461.19 | 437.26 | 469.52 | 446.74 | 334.29 | 0.5265 | 2.1913 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7645734.9179 | 8595925.866 | 8595925.866 | 62.4258 | 62.2636 | 1.0016 | 0.99831 | 682308.9447 | 896380.4995 | 459.6034 | 0.50333 | 0 | 0 | 30.4187 | 26.0048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017926 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 577.5452 | 1367.9531 | 53.5792 | 43.476 | 30.0895 | 1788.226 | 64.1414 | 27.3046 | #NV | #NV | #NV | #NV | #NV | 72.5902 | 2.255 | 1.3909 | 0.65123 | 4.8267 | 4.0403 | #NV | 0 | 100 | 587.2 | 328 | 96.15 | 103.89 | 102.1 | 322.2 | 3 | 85.41 | 38.72 | 4 | 34.04 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.85 | 0 | 34.94 | 64 | 64 | 90.4 | 82.08 | 73.02 | 0 | 102.1 | 2.19 | 84.1 | 39.66 | 96.18 | 18.47 | 103.89 | 110 | 0 | 16252 | 75.92 | 111.44 | 208.22 | 201.92 | 207.74 | 0 | 30.09 | 46.89 | 12283 | 85.43 | 38.73 | 34.04 | 5.22 | 38.73 | 0 | 604 | 451.6 | 457.2 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.2 | 328.7 | 0 | 322.2 | 102.12 | 16253 | 16252 | 328
03/26/22 10:15:06.214 | 637.7137 | 1368.3251 | 55.4326 | 44.2761 | 11.1564 | 30.5101 | 50.7271 | 0 | 1785.6645 | 81.5023 | 71.9203 | 9.582 | 25.549 | 68.5959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0011 | 460.3201 | 457.3101 | 461.2101 | 435.9201 | 468.0901 | 445.3801 | 333.2201 | 0.52252 | 2.9104 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7679390.2623 | 8564664.4822 | 8564664.4822 | 62.4256 | 62.2629 | 1.0016 | 0.9983 | 684855.4303 | 892276.6524 | 459.6134 | 0.50115 | 0 | 0 | 30.5101 | 25.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017939 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 578.4101 | 1367.9398 | 53.6017 | 43.4831 | 30.0901 | 1788.2467 | 64.2143 | 27.2922 | #NV | #NV | #NV | #NV | #NV | 72.6776 | 2.2599 | 1.3877 | 0.65276 | 4.8244 | 4.0613 | #NV | 0 | 100 | 587.2 | 328 | 96.33 | 103.89 | 102.12 | 324.8 | 3 | 85.51 | 38.77 | 4 | 34.07 | 43.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 93.98 | 0 | 34.98 | 64 | 64 | 90.48 | 82.14 | 73.1 | 0 | 102.12 | 2.19 | 84.18 | 39.71 | 96.33 | 18.38 | 103.89 | 110 | 0 | 16242 | 75.96 | 111.48 | 208.57 | 202.3 | 208.08 | 0 | 30.08 | 46.87 | 12288 | 85.51 | 38.77 | 34.07 | 5.16 | 38.77 | 0 | 603 | 454.3 | 457.1 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.4 | 331.3 | 0 | 324.8 | 102.16 | 16242 | 16242 | 329
03/26/22 10:15:11.214 | 637.7769 | 1368.0877 | 55.4633 | 44.3038 | 11.1596 | 29.6365 | 50.7292 | 0 | 1782.124 | 81.542 | 71.9558 | 9.5862 | 26.7148 | 68.5835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0011 | 460.3201 | 457.3101 | 461.2101 | 435.9201 | 468.0901 | 445.3801 | 333.2201 | 0.52247 | 3.0362 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7679376.1484 | 8552692.8966 | 8552692.8966 | 62.4255 | 62.2625 | 1.0016 | 0.9983 | 684735.1403 | 890503.5152 | 459.6134 | 0.50115 | 0 | 0 | 29.6365 | 26.7148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017933 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 579.2716 | 1367.9289 | 53.6243 | 43.4906 | 30.0848 | 1788.1906 | 64.2873 | 27.2896 | #NV | #NV | #NV | #NV | #NV | 72.7649 | 2.2544 | 1.3846 | 0.65441 | 4.8367 | 4.0818 | #NV | 0 | 100 | 587.4 | 328 | 96.38 | 103.89 | 102.16 | 323.6 | 3 | 85.54 | 38.82 | 4 | 34.13 | 43.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.08 | 0 | 35.03 | 64 | 64 | 90.58 | 82.2 | 73.12 | 0 | 102.16 | 2.19 | 84.23 | 39.77 | 96.35 | 18.37 | 103.89 | 110 | 0 | 16233 | 76.02 | 111.52 | 208.92 | 202.6 | 208.53 | 0 | 30 | 46.79 | 12293 | 85.53 | 38.82 | 34.13 | 5.11 | 38.82 | 0 | 603 | 449.8 | 456.9 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.6 | 331.2 | 0 | 324.8 | 102.19 | 16235 | 16233 | 328
03/26/22 10:15:16.214 | 637.8883 | 1367.68 | 55.514 | 44.349 | 11.165 | 30.0705 | 50.7532 | 0 | 1787.6153 | 81.6054 | 72.0126 | 9.5928 | 26.3149 | 68.6587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.982 | 460.34 | 457.34 | 461.23 | 435.26 | 467.12 | 444.59 | 332.61 | 0.52142 | 2.674 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7681086.8072 | 8584362.3239 | 8584362.3239 | 62.4254 | 62.262 | 1.0016 | 0.9983 | 684528.6396 | 893241.0226 | 459.6367 | 0.49967 | 0 | 0 | 30.0705 | 26.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017927 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 580.1328 | 1367.9289 | 53.6472 | 43.4984 | 30.0799 | 1788.1762 | 64.3604 | 27.2871 | #NV | #NV | #NV | #NV | #NV | 72.8524 | 2.2544 | 1.3815 | 0.65621 | 4.8356 | 4.1016 | #NV | 0 | 100 | 587.3 | 328 | 96.43 | 103.89 | 102.14 | 323.9 | 3 | 85.57 | 38.89 | 4 | 34.19 | 43.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.13 | 0 | 35.09 | 64 | 64 | 90.65 | 82.25 | 73.14 | 0 | 102.14 | 2.19 | 84.26 | 39.83 | 96.45 | 18.31 | 103.89 | 110 | 0 | 16222 | 76.06 | 111.56 | 209.35 | 203 | 208.88 | 0 | 29.9 | 46.73 | 12298 | 85.58 | 38.89 | 34.2 | 5.04 | 38.89 | 0 | 603 | 452.1 | 457 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.3 | 330.3 | 0 | 323.9 | 102.14 | 16223 | 16222 | 328
03/26/22 10:15:21.214 | 637.3387 | 1366.1524 | 55.5412 | 44.3732 | 11.1679 | 30.1052 | 50.7389 | 0 | 1788.3636 | 81.6387 | 72.0421 | 9.5966 | 26.5805 | 68.6533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.978 | 460.36 | 457.36 | 461.24 | 434.91 | 466.63 | 444.17 | 332.3 | 0.52139 | 2.5034 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7674492.8761 | 8591600.7542 | 8591600.7542 | 62.4253 | 62.2617 | 1.0016 | 0.9983 | 683762.7135 | 893611.5901 | 459.6533 | 0.49893 | 0 | 0 | 30.1052 | 26.5805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017933 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 580.9866 | 1367.9249 | 53.6702 | 43.5064 | 30.0758 | 1788.187 | 64.4336 | 27.2848 | #NV | #NV | #NV | #NV | #NV | 72.9399 | 2.2569 | 1.3783 | 0.65807 | 4.8338 | 4.1205 | #NV | 0 | 100 | 587 | 328 | 96.48 | 103.89 | 102.12 | 324.5 | 3 | 85.6 | 38.93 | 4 | 34.23 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.17 | 0 | 35.13 | 64 | 64 | 90.7 | 82.28 | 73.22 | 0 | 102.12 | 2.19 | 84.29 | 39.87 | 96.48 | 18.3 | 103.89 | 110 | 0 | 16213 | 76.1 | 111.6 | 209.7 | 203.39 | 209.26 | 0 | 29.89 | 46.85 | 12303 | 85.6 | 38.93 | 34.23 | 5.02 | 38.93 | 0 | 603 | 449.6 | 457 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.2 | 330.8 | 0 | 324.3 | 102.12 | 16212 | 16213 | 330
03/26/22 10:15:26.214 | 637.5711 | 1366.1317 | 55.5723 | 44.401 | 11.1713 | 30.2786 | 50.73 | 0 | 1785.8605 | 81.6763 | 72.0753 | 9.6011 | 26.5078 | 68.6264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.978 | 460.36 | 457.36 | 461.24 | 434.91 | 466.63 | 444.17 | 332.3 | 0.5212 | 2.6168 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7677354.8393 | 8583615.3593 | 8583615.3593 | 62.4252 | 62.2615 | 1.0015 | 0.9983 | 683862.3168 | 892476.641 | 459.6534 | 0.49893 | 0 | 0 | 30.2786 | 26.5078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017932 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 581.8275 | 1367.8974 | 53.6934 | 43.5146 | 30.0726 | 1788.2084 | 64.5069 | 27.2826 | #NV | #NV | #NV | #NV | #NV | 73.0273 | 2.2484 | 1.3751 | 0.65997 | 4.8147 | 4.1386 | #NV | 0 | 100 | 586.8 | 326 | 96.48 | 103.89 | 102.05 | 323.5 | 3 | 85.57 | 38.97 | 4 | 34.26 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.23 | 0 | 35.18 | 64 | 64 | 90.78 | 82.32 | 73.26 | 0 | 102.05 | 2.18 | 84.32 | 39.92 | 96.48 | 18.3 | 103.89 | 110 | 0 | 16204 | 76.14 | 111.64 | 210.06 | 203.72 | 209.61 | 0 | 29.83 | 46.81 | 12308 | 85.6 | 38.98 | 34.27 | 4.99 | 38.98 | 0 | 604 | 452.5 | 457.2 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.5 | 329.2 | 0 | 322.8 | 102 | 16205 | 16204 | 330
03/26/22 10:15:31.214 | 637.6379 | 1365.7446 | 55.6235 | 44.4468 | 11.1768 | 30.7592 | 50.7494 | 0 | 1783.5071 | 81.7359 | 72.1271 | 9.6087 | 25.7391 | 68.6615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9781 | 460.3601 | 457.3601 | 461.2401 | 434.9101 | 466.6301 | 444.1701 | 332.3001 | 0.52114 | 2.6971 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7678648.9232 | 8577980.1918 | 8577980.1918 | 62.4251 | 62.2609 | 1.0015 | 0.99829 | 683554.6515 | 891175.2572 | 459.6534 | 0.49893 | 0 | 0 | 30.7592 | 25.7391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017939 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 582.6616 | 1367.8635 | 53.7168 | 43.5231 | 30.0711 | 1788.2466 | 64.5803 | 27.2799 | #NV | #NV | #NV | #NV | #NV | 73.1149 | 2.2345 | 1.3719 | 0.66207 | 4.7492 | 4.156 | #NV | 0 | 100 | 586.6 | 329 | 96.5 | 103.87 | 102 | 323.5 | 3 | 85.61 | 39.03 | 4 | 34.32 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.27 | 0 | 35.23 | 64 | 64 | 90.8 | 82.33 | 73.28 | 0 | 102 | 2.18 | 84.35 | 39.97 | 96.5 | 18.26 | 103.87 | 110 | 0 | 16193 | 76.18 | 111.66 | 210.33 | 204.04 | 209.98 | 0 | 29.71 | 46.69 | 12313 | 85.61 | 39.05 | 34.34 | 4.96 | 39.05 | 0 | 604 | 452.5 | 457.2 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.7 | 330.7 | 0 | 324.3 | 102.03 | 16192 | 16193 | 329
03/26/22 10:15:36.214 | 637.567 | 1365.1098 | 55.6598 | 44.479 | 11.1808 | 30.1459 | 50.7387 | 0 | 1783.3368 | 81.7761 | 72.162 | 9.6141 | 26.3269 | 68.6661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9741 | 460.3201 | 457.3601 | 461.2001 | 434.3601 | 465.8401 | 443.5801 | 331.7901 | 0.5204 | 2.6277 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7677247.2174 | 8582577.4127 | 8582577.4127 | 62.425 | 62.2606 | 1.0015 | 0.99829 | 683235.1844 | 891086.2199 | 459.6267 | 0.49315 | 0 | 0 | 30.1459 | 26.3269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017934 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 583.4922 | 1367.8374 | 53.7403 | 43.5318 | 30.0673 | 1788.2638 | 64.6537 | 27.2766 | #NV | #NV | #NV | #NV | #NV | 73.2024 | 2.2391 | 1.3687 | 0.66424 | 4.7256 | 4.1725 | #NV | 0 | 100 | 587 | 327 | 96.7 | 103.87 | 102.09 | 323.6 | 3 | 85.72 | 39.14 | 4 | 34.41 | 44.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.38 | 0 | 35.28 | 64 | 64 | 90.88 | 82.39 | 73.3 | 0 | 102.07 | 2.18 | 84.4 | 40.02 | 96.7 | 18.15 | 103.87 | 110 | 0 | 16184 | 76.2 | 111.71 | 210.7 | 204.37 | 210.26 | 0 | 29.57 | 46.8 | 12318 | 85.72 | 39.14 | 34.43 | 4.91 | 39.14 | 0 | 603 | 451.2 | 457 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.7 | 330 | 0 | 323.6 | 102.03 | 16185 | 16184 | 327
03/26/22 10:15:41.214 | 638.6707 | 1366.6117 | 55.7158 | 44.5278 | 11.188 | 30.338 | 50.7484 | 0 | 1787.4089 | 81.8351 | 72.2127 | 9.6224 | 25.9548 | 68.6368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.973 | 460.3 | 457.33 | 461.16 | 433.79 | 465.08 | 442.88 | 331.25 | 0.51866 | 2.4318 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7690689.9306 | 8609034.2894 | 8609034.2894 | 62.4248 | 62.2601 | 1.0015 | 0.99829 | 683984.1208 | 893115.1319 | 459.5967 | 0.49319 | 0 | 0 | 30.338 | 25.9548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017935 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 584.3286 | 1367.8326 | 53.7641 | 43.5409 | 30.0629 | 1788.2982 | 64.7274 | 27.2731 | #NV | #NV | #NV | #NV | #NV | 73.2901 | 2.2426 | 1.3655 | 0.66661 | 4.6966 | 4.1883 | #NV | 0 | 100 | 586.1 | 327 | 96.65 | 103.85 | 101.93 | 322.6 | 3 | 85.68 | 39.19 | 4 | 34.48 | 44.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.38 | 0 | 35.32 | 64 | 64 | 90.85 | 82.36 | 73.34 | 0 | 101.93 | 2.18 | 84.4 | 40.08 | 96.67 | 18.13 | 103.85 | 110 | 0 | 16176 | 76.26 | 111.75 | 210.97 | 204.7 | 210.62 | 0 | 29.57 | 46.91 | 12323 | 85.7 | 39.19 | 34.48 | 4.88 | 39.19 | 0 | 603 | 450.8 | 457 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.1 | 329 | 0 | 322.6 | 101.93 | 16178 | 16176 | 327
03/26/22 10:15:46.214 | 639.6785 | 1368.8 | 55.7457 | 44.5533 | 11.1924 | 30.572 | 50.7513 | 0 | 1785.427 | 81.8655 | 72.2387 | 9.6268 | 25.9745 | 68.6463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.973 | 460.3 | 457.33 | 461.16 | 433.79 | 465.08 | 442.88 | 331.25 | 0.51784 | 2.6022 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7703143.7863 | 8606504.261 | 8606504.261 | 62.4247 | 62.2599 | 1.0015 | 0.99829 | 684858.6365 | 892553.2029 | 459.5967 | 0.49319 | 0 | 0 | 30.572 | 25.9745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017942 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 585.1725 | 1367.8573 | 53.788 | 43.5501 | 30.0621 | 1788.3099 | 64.801 | 27.2673 | #NV | #NV | #NV | #NV | #NV | 73.3777 | 2.2286 | 1.3623 | 0.66906 | 4.6867 | 4.2032 | #NV | 0 | 100 | 587.1 | 327 | 96.73 | 103.85 | 102.1 | 322.3 | 3 | 85.72 | 39.24 | 4 | 34.52 | 44.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.5 | 0 | 35.38 | 64 | 64 | 90.98 | 82.44 | 73.36 | 0 | 102.1 | 2.18 | 84.48 | 40.13 | 96.73 | 18.11 | 103.85 | 110 | 0 | 16168 | 76.28 | 111.79 | 211.33 | 205.02 | 210.9 | 0 | 29.54 | 47.01 | 12328 | 85.74 | 39.24 | 34.52 | 4.86 | 39.24 | 0 | 604 | 451.7 | 457.2 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587 | 329.7 | 0 | 323.3 | 102.09 | 16170 | 16168 | 329
03/26/22 10:15:51.214 | 640.0055 | 1368.0052 | 55.7978 | 44.5976 | 11.2003 | 29.798 | 50.7513 | 0 | 1780.8389 | 81.9174 | 72.283 | 9.6344 | 27.0302 | 68.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 460.36 | 457.39 | 461.21 | 433.05 | 464.22 | 442.02 | 330.67 | 0.51667 | 2.8281 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7706260.0528 | 8589185.609 | 8589185.609 | 62.4246 | 62.2594 | 1.0015 | 0.99828 | 684677.552 | 889824.3435 | 459.6534 | 0.4924 | 0 | 0 | 29.798 | 27.0302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017949 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 586.0131 | 1367.8807 | 53.812 | 43.5595 | 30.0597 | 1788.321 | 64.8747 | 27.267 | #NV | #NV | #NV | #NV | #NV | 73.4653 | 2.2181 | 1.359 | 0.67154 | 4.6677 | 4.2172 | #NV | 0 | 100 | 586.5 | 328 | 96.77 | 103.85 | 102 | 322.4 | 3 | 85.78 | 39.27 | 4 | 34.55 | 44.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.58 | 0 | 35.41 | 64 | 64 | 91.05 | 82.48 | 73.4 | 0 | 102 | 2.18 | 84.52 | 40.17 | 96.8 | 18.06 | 103.85 | 110 | 0 | 16159 | 76.32 | 111.85 | 211.59 | 205.34 | 211.26 | 0 | 29.52 | 47.16 | 12333 | 85.78 | 39.28 | 34.56 | 4.86 | 39.28 | 0 | 604 | 445.9 | 457.2 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.7 | 329.6 | 0 | 323.1 | 102.03 | 16160 | 16159 | 327
03/26/22 10:15:56.214 | 639.527 | 1365.6724 | 55.8526 | 44.6447 | 11.2079 | 30.2707 | 50.7554 | 0 | 1785.1277 | 81.9712 | 72.3291 | 9.6421 | 25.868 | 68.6809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 460.36 | 457.39 | 461.21 | 433.05 | 464.22 | 442.02 | 330.67 | 0.51705 | 2.5094 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7701009.4261 | 8610484.7001 | 8610484.7001 | 62.4244 | 62.2591 | 1.0015 | 0.99828 | 683792.0093 | 891591.7568 | 459.6534 | 0.4924 | 0 | 0 | 30.2707 | 25.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017944 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 586.8492 | 1367.8849 | 53.8364 | 43.5693 | 30.0605 | 1788.3407 | 64.9486 | 27.2598 | #NV | #NV | #NV | #NV | #NV | 73.5531 | 2.2143 | 1.3558 | 0.67436 | 4.6433 | 4.2305 | #NV | 0 | 100 | 585.8 | 325 | 96.83 | 103.85 | 101.88 | 323.3 | 3 | 85.79 | 39.34 | 4 | 34.61 | 44.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.63 | 0 | 35.45 | 64 | 64 | 91.13 | 82.52 | 73.46 | 0 | 101.88 | 2.18 | 84.53 | 40.21 | 96.83 | 18.04 | 103.85 | 110 | 0 | 16151 | 76.4 | 111.89 | 211.97 | 205.68 | 211.56 | 0 | 29.59 | 47.42 | 12338 | 85.81 | 39.34 | 34.61 | 4.87 | 39.34 | 0 | 604 | 451.3 | 457.3 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.1 | 330.1 | 0 | 323.6 | 101.93 | 16150 | 16151 | 325
03/26/22 10:16:01.215 | 639.14 | 1365.0015 | 55.8702 | 44.6602 | 11.2099 | 30.2403 | 50.7513 | 0 | 1784.5394 | 81.9882 | 72.3437 | 9.6445 | 26.0302 | 68.6966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 460.36 | 457.39 | 461.21 | 433.05 | 464.22 | 442.02 | 330.67 | 0.51737 | 2.4049 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7696203.7364 | 8614794.7917 | 8614794.7917 | 62.4244 | 62.2588 | 1.0015 | 0.99828 | 683170.662 | 891666.4064 | 459.6533 | 0.4924 | 0 | 0 | 30.2403 | 26.0302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017955 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 587.6682 | 1367.8731 | 53.8608 | 43.5792 | 30.0621 | 1788.3148 | 65.0225 | 27.2478 | #NV | #NV | #NV | #NV | #NV | 73.6408 | 2.224 | 1.3527 | 0.67723 | 4.6515 | 4.243 | #NV | 0 | 100 | 586.6 | 327 | 96.93 | 103.85 | 102.02 | 321.3 | 3 | 85.85 | 39.36 | 4 | 34.64 | 44.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.7 | 0 | 35.49 | 64 | 64 | 91.2 | 82.57 | 73.54 | 0 | 102.02 | 2.18 | 84.59 | 40.24 | 96.93 | 17.99 | 103.85 | 110 | 0 | 16146 | 76.42 | 111.95 | 204.37 | 205.93 | 211.86 | 0 | 29.71 | 47.53 | 12342 | 85.85 | 39.37 | 34.65 | 4.85 | 39.37 | 0 | 604 | 449.6 | 457.3 | 25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.7 | 327.5 | 0 | 321.1 | 102.03 | 16148 | 16146 | 326
03/26/22 10:16:06.213 | 638.4797 | 1362.8493 | 55.9405 | 44.7243 | 11.2163 | 30.7608 | 50.7583 | 0 | 1781.2157 | 82.0543 | 72.4016 | 9.6527 | 25.5353 | 68.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0031 | 460.4201 | 457.4201 | 461.2601 | 432.0801 | 463.2601 | 441.0701 | 329.9501 | 0.51677 | 2.4092 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7688693.8208 | 8605399.8761 | 8605399.8761 | 62.4241 | 62.2583 | 1.0015 | 0.99828 | 682090.0873 | 889999.0933 | 459.7001 | 0.49598 | 0 | 0 | 30.7608 | 25.5353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016243 | 0.017958 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 588.4801 | 1367.8553 | 53.8852 | 43.5893 | 30.065 | 1788.2596 | 65.0964 | 27.2359 | #NV | #NV | #NV | #NV | #NV | 73.7285 | 2.2456 | 1.3496 | 0.68021 | 4.6695 | 4.2546 | #NV | 0 | 100 | 587 | 327 | 97.08 | 103.85 | 102.09 | 322.2 | 3 | 85.94 | 39.41 | 4 | 34.69 | 44.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.8 | 0 | 35.54 | 64 | 64 | 91.27 | 82.6 | 73.56 | 0 | 102.09 | 2.18 | 84.65 | 40.3 | 97.08 | 17.91 | 103.85 | 110 | 0 | 16140 | 76.48 | 111.97 | 204.64 | 206.2 | 204.28 | 0 | 29.61 | 47.4 | 12347 | 85.94 | 39.41 | 34.7 | 4.87 | 39.41 | 0 | 604 | 447.3 | 457.2 | 26 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.9 | 328.2 | 0 | 321.8 | 102.07 | 16141 | 16140 | 328
03/26/22 10:16:11.213 | 638.7159 | 1363.1796 | 55.9646 | 44.7468 | 11.2178 | 30.5184 | 50.7519 | 0 | 1779.3268 | 82.0762 | 72.4214 | 9.6548 | 25.9151 | 68.7049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0031 | 460.4201 | 457.4201 | 461.2601 | 432.0801 | 463.2601 | 441.0701 | 329.9501 | 0.51658 | 2.5107 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7691322.9048 | 8598531.4085 | 8598531.4085 | 62.4241 | 62.2581 | 1.0015 | 0.99828 | 682254.2137 | 889053.0271 | 459.7001 | 0.49598 | 0 | 0 | 30.5184 | 25.9151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016242 | 0.017963 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 589.2811 | 1367.8307 | 53.9099 | 43.5997 | 30.0648 | 1788.2083 | 65.1704 | 27.2273 | #NV | #NV | #NV | #NV | #NV | 73.8162 | 2.2725 | 1.3467 | 0.68351 | 4.7166 | 4.2655 | #NV | 0 | 100 | 586.4 | 328 | 97.13 | 103.85 | 101.97 | 321.4 | 3 | 85.95 | 39.45 | 4 | 34.73 | 44.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.88 | 0 | 35.57 | 64 | 64 | 91.38 | 82.67 | 73.58 | 0 | 101.97 | 2.18 | 84.69 | 40.33 | 97.1 | 17.88 | 103.85 | 110 | 0 | 16134 | 76.5 | 112.01 | 204.91 | 206.54 | 204.56 | 0 | 29.55 | 47.4 | 12353 | 85.96 | 39.47 | 34.74 | 4.88 | 39.47 | 0 | 603 | 447 | 457.1 | 26 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.2 | 328 | 0 | 321.6 | 101.95 | 16136 | 16134 | 326
03/26/22 10:16:16.213 | 640.5103 | 1366.7614 | 56.0185 | 44.7986 | 11.22 | 30.6706 | 50.7428 | 0 | 1783.7136 | 82.1252 | 72.4673 | 9.6578 | 25.7471 | 68.6793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.002 | 460.44 | 457.43 | 461.29 | 431.58 | 462.79 | 440.59 | 329.58 | 0.51456 | 2.4686 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7713059.9671 | 8622125.6324 | 8622125.6324 | 62.4239 | 62.2577 | 1.0015 | 0.99827 | 684044.159 | 891239.6885 | 459.72 | 0.49813 | 0 | 0 | 30.6706 | 25.7471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017955 | 0.01427 | 0.00479 | 0.0119 | 0.0119 | 590.089 | 1367.8312 | 53.9348 | 43.6104 | 30.0651 | 1788.1952 | 65.2447 | 27.2194 | #NV | #NV | #NV | #NV | #NV | 73.9041 | 2.2722 | 1.344 | 0.68712 | 4.7259 | 4.2756 | #NV | 0 | 100 | 586.9 | 327 | 97.2 | 103.85 | 102.09 | 320.1 | 3 | 86.01 | 39.5 | 4 | 34.79 | 44.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 94.95 | 0 | 35.63 | 64 | 64 | 91.45 | 82.71 | 73.64 | 0 | 102.09 | 2.18 | 84.73 | 40.39 | 97.15 | 17.87 | 103.85 | 110 | 0 | 16126 | 76.54 | 112.05 | 205.19 | 206.79 | 204.84 | 0 | 29.51 | 47.48 | 12358 | 85.98 | 39.52 | 34.79 | 4.87 | 39.52 | 0 | 603 | 447.7 | 457.1 | 26 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.7 | 327.9 | 0 | 321.5 | 102.03 | 16126 | 16126 | 326
03/26/22 10:16:21.213 | 640.7306 | 1368.0774 | 56.0312 | 44.811 | 11.2202 | 30.9456 | 50.7488 | 0 | 1783.5071 | 82.1368 | 72.4788 | 9.658 | 25.3543 | 68.6731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.002 | 460.44 | 457.43 | 461.29 | 431.58 | 462.79 | 440.59 | 329.58 | 0.51438 | 2.465 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7715908.052 | 8625217.2594 | 8625217.2594 | 62.4239 | 62.2576 | 1.0015 | 0.99827 | 684273.7303 | 891584.5761 | 459.72 | 0.49813 | 0 | 0 | 30.9456 | 25.3543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017966 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 590.8866 | 1367.8448 | 53.9596 | 43.6212 | 30.069 | 1788.1636 | 65.3188 | 27.2047 | #NV | #NV | #NV | #NV | #NV | 73.9918 | 2.2663 | 1.3414 | 0.69068 | 4.7381 | 4.2847 | #NV | 0 | 100 | 586.9 | 328 | 97.33 | 103.87 | 102.07 | 320.4 | 3 | 86.09 | 39.56 | 4 | 34.84 | 44.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 95.08 | 0 | 35.68 | 64 | 64 | 91.6 | 82.8 | 73.64 | 0 | 102.07 | 2.18 | 84.8 | 40.44 | 97.33 | 17.79 | 103.87 | 110 | 0 | 16116 | 76.56 | 112.07 | 205.46 | 207.05 | 205.12 | 0 | 29.6 | 47.73 | 12362 | 86.09 | 39.56 | 34.84 | 4.87 | 39.56 | 0 | 603 | 450.7 | 457 | 26 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.3 | 325.9 | 0 | 319.5 | 101.97 | 16120 | 16116 | 326
03/26/22 10:16:26.213 | 641.4156 | 1368.8361 | 56.1047 | 44.8857 | 11.2191 | 30.8102 | 50.7519 | 0 | 1780.7202 | 82.2076 | 72.5512 | 9.6564 | 25.3519 | 68.7218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0001 | 460.4501 | 457.4101 | 461.2901 | 431.3601 | 462.5801 | 440.2901 | 329.3801 | 0.51352 | 2.7751 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7724087.0801 | 8605801.9003 | 8605801.9003 | 62.4236 | 62.2569 | 1.0014 | 0.99827 | 685078.2383 | 889734.4622 | 459.7167 | 0.50176 | 0 | 0 | 30.8102 | 25.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017971 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 591.6785 | 1367.8531 | 53.9845 | 43.6323 | 30.0727 | 1788.1262 | 65.3932 | 27.1905 | #NV | #NV | #NV | #NV | #NV | 74.0797 | 2.2699 | 1.3392 | 0.69475 | 4.7722 | 4.2933 | #NV | 0 | 100 | 586.3 | 326 | 97.45 | 103.87 | 101.97 | 322.6 | 3 | 86.15 | 39.61 | 4 | 34.88 | 44.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 95.15 | 0 | 35.73 | 64 | 64 | 91.65 | 82.83 | 73.76 | 0 | 101.97 | 2.18 | 84.85 | 40.49 | 97.43 | 17.74 | 103.87 | 110 | 0 | 16109 | 76.6 | 112.11 | 205.73 | 207.3 | 205.39 | 0 | 29.73 | 47.94 | 12367 | 86.13 | 39.62 | 34.89 | 4.8 | 39.62 | 0 | 603 | 449 | 457.1 | 26 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.3 | 328.4 | 0 | 322 | 101.97 | 16110 | 16109 | 326
03/26/22 10:16:31.213 | 640.3425 | 1366.9368 | 56.1509 | 44.9349 | 11.216 | 31.4022 | 50.7765 | 0 | 1780.8079 | 82.2565 | 72.6037 | 9.6527 | 24.6305 | 68.7755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 460.42 | 457.36 | 461.25 | 430.99 | 462.18 | 439.85 | 329.04 | 0.51385 | 2.6781 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7711691.3803 | 8602084.597 | 8602084.597 | 62.4235 | 62.2565 | 1.0014 | 0.99827 | 684125.4011 | 889772.2602 | 459.6767 | 0.50398 | 0 | 0 | 31.4022 | 24.6305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017969 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 592.4638 | 1367.8589 | 54.0094 | 43.6435 | 30.0776 | 1788.0988 | 65.4676 | 27.1748 | #NV | #NV | #NV | #NV | #NV | 74.1674 | 2.2696 | 1.3369 | 0.69877 | 4.7999 | 4.3009 | #NV | 0 | 100 | 587 | 324 | 97.52 | 103.89 | 102.03 | 319.6 | 3 | 86.19 | 39.66 | 4 | 34.93 | 44.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 95.25 | 0 | 35.77 | 64 | 64 | 91.75 | 82.89 | 73.76 | 0 | 102.03 | 2.18 | 84.9 | 40.54 | 97.52 | 17.71 | 103.89 | 110 | 0 | 16103 | 76.62 | 112.13 | 206 | 207.64 | 205.67 | 0 | 29.74 | 47.86 | 12372 | 86.19 | 39.66 | 34.93 | 4.78 | 39.66 | 0 | 603 | 449.9 | 457 | 26 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587 | 326 | 0 | 319.6 | 102.09 | 16106 | 16103 | 324
03/26/22 10:16:36.213 | 640.9341 | 1368.7896 | 56.1786 | 44.9674 | 11.2113 | 31.3611 | 50.78 | 0 | 1784.2916 | 82.29 | 72.6417 | 9.6483 | 25.1865 | 68.7664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9971 | 460.4001 | 457.3301 | 461.2301 | 430.6501 | 461.7501 | 439.4101 | 328.7201 | 0.51288 | 2.5893 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7718792.6225 | 8615514.2417 | 8615514.2417 | 62.4234 | 62.2562 | 1.0014 | 0.99827 | 685051.308 | 891508.4984 | 459.6534 | 0.50545 | 0 | 0 | 31.3611 | 25.1865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017974 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 593.2329 | 1367.8707 | 54.0343 | 43.6549 | 30.0852 | 1788.065 | 65.5422 | 27.1588 | #NV | #NV | #NV | #NV | #NV | 74.2553 | 2.2647 | 1.3352 | 0.70336 | 4.8058 | 4.3081 | #NV | 0 | 100 | 585.9 | 326 | 97.73 | 103.92 | 101.9 | 321.4 | 3 | 86.31 | 39.67 | 4 | 34.95 | 44.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 95.5 | 0 | 35.77 | 64 | 64 | 92.03 | 83.03 | 73.84 | 0 | 101.9 | 2.18 | 85.05 | 40.54 | 97.73 | 17.61 | 103.92 | 110 | 0 | 16094 | 76.66 | 112.15 | 206.28 | 207.89 | 205.95 | 0 | 29.59 | 47.67 | 12377 | 86.31 | 39.67 | 34.93 | 4.77 | 39.67 | 0 | 604 | 446.5 | 457.2 | 26 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.3 | 324 | 0 | 317.7 | 101.79 | 16096 | 16094 | 324
03/26/22 10:16:41.214 | 642.6578 | 1374.668 | 56.2049 | 45.0115 | 11.1934 | 30.5644 | 50.7628 | 0 | 1780.9679 | 82.3378 | 72.7052 | 9.6326 | 26.0552 | 68.7544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.995 | 460.38 | 457.32 | 461.2 | 430.39 | 461.42 | 439.06 | 328.47 | 0.51111 | 3.1416 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7738891.6803 | 8586475.4462 | 8586475.4462 | 62.4233 | 62.2557 | 1.0014 | 0.99826 | 687991.9917 | 889840.567 | 459.6334 | 0.5033 | 0 | 0 | 30.5644 | 26.0552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.01799 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 593.9978 | 1367.8884 | 54.0591 | 43.6665 | 30.0939 | 1788.0176 | 65.6168 | 27.1419 | #NV | #NV | #NV | #NV | #NV | 74.3432 | 2.266 | 1.3333 | 0.70789 | 4.8043 | 4.3142 | #NV | 0 | 100 | 584.1 | 324 | 98.18 | 103.97 | 101.58 | 317.3 | 3 | 86.55 | 39.58 | 4 | 34.85 | 44.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 95.92 | 0 | 35.7 | 64 | 64 | 92.38 | 83.25 | 73.9 | 0 | 101.58 | 2.19 | 85.29 | 40.46 | 98.23 | 17.42 | 103.97 | 110 | 0 | 16090 | 76.7 | 112.15 | 206.46 | 208.14 | 206.13 | 0 | 29.53 | 47.45 | 12383 | 86.58 | 39.58 | 34.85 | 4.88 | 39.58 | 0 | 604 | 446.6 | 457.2 | 26 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.6 | 326.1 | 0 | 319.8 | 101.67 | 16090 | 16090 | 326
03/26/22 10:16:46.213 | 640.9988 | 1373.4552 | 56.215 | 45.0507 | 11.1643 | 30.4695 | 50.7684 | 0 | 1780.2506 | 82.3841 | 72.7768 | 9.6073 | 26.1459 | 68.7664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.993 | 460.38 | 457.31 | 461.18 | 430.3 | 461.19 | 438.82 | 328.32 | 0.5122 | 3.1646 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7718864.6508 | 8564271.8836 | 8564271.8836 | 62.4232 | 62.2552 | 1.0014 | 0.99826 | 687686.7193 | 889444.3269 | 459.6233 | 0.50331 | 0 | 0 | 30.4695 | 26.1459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017981 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 594.7544 | 1367.9302 | 54.0839 | 43.6783 | 30.0962 | 1787.9341 | 65.6919 | 27.1317 | #NV | #NV | #NV | #NV | #NV | 74.4312 | 2.3196 | 1.3317 | 0.71295 | 4.8178 | 4.3202 | #NV | 0 | 100 | 585.8 | 325 | 98.4 | 104.01 | 101.88 | 322.1 | 3 | 86.68 | 39.62 | 4 | 34.89 | 44.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 96.18 | 0 | 35.73 | 64 | 64 | 92.6 | 83.38 | 74.04 | 0 | 101.88 | 2.2 | 85.41 | 40.49 | 98.42 | 17.34 | 104.03 | 110 | 0 | 16087 | 76.72 | 112.15 | 206.74 | 208.39 | 206.41 | 0 | 29.4 | 47.34 | 12388 | 86.69 | 39.62 | 34.89 | 4.82 | 39.62 | 0 | 604 | 448.2 | 457.2 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.8 | 328.5 | 0 | 322.1 | 101.88 | 16085 | 16087 | 325
03/26/22 10:16:51.213 | 636.3723 | 1370.2812 | 56.2117 | 45.0922 | 11.1196 | 30.3499 | 50.7548 | 0 | 1788.6165 | 82.4447 | 72.8752 | 9.5694 | 26.0214 | 68.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9901 | 460.3801 | 457.2801 | 461.1701 | 430.1501 | 461.0101 | 438.5301 | 328.1601 | 0.51567 | 2.4992 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7663191.1683 | 8566659.8149 | 8566659.8149 | 62.4231 | 62.2544 | 1.0014 | 0.99826 | 685796.1224 | 893642.4464 | 459.6101 | 0.50695 | 0 | 0 | 30.3499 | 26.0214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017971 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 595.4827 | 1367.961 | 54.1085 | 43.6903 | 30.0978 | 1787.91 | 65.7674 | 27.1201 | #NV | #NV | #NV | #NV | #NV | 74.5194 | 2.3152 | 1.3299 | 0.71838 | 4.8071 | 4.3261 | #NV | 0 | 100 | 587 | 327 | 98.68 | 104.03 | 102.1 | 319.9 | 3 | 86.82 | 39.7 | 4 | 34.96 | 44.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 96.43 | 0 | 35.8 | 64 | 64 | 92.9 | 83.56 | 74.24 | 0 | 102.1 | 2.2 | 85.57 | 40.57 | 98.7 | 17.19 | 104.03 | 110 | 0 | 16080 | 76.76 | 112.15 | 207.02 | 208.64 | 206.69 | 0 | 29.33 | 47.53 | 12393 | 86.84 | 39.71 | 34.98 | 4.66 | 39.71 | 0 | 603 | 449 | 457.1 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.1 | 327.3 | 0 | 320.9 | 102.1 | 16081 | 16080 | 326
03/26/22 10:16:56.213 | 634.0217 | 1368.1548 | 56.2002 | 45.115 | 11.0851 | 30.5409 | 50.7501 | 0 | 1789.1171 | 82.4936 | 72.9535 | 9.5401 | 25.7701 | 68.7375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9901 | 460.3801 | 457.2801 | 461.1701 | 430.1501 | 461.0101 | 438.5301 | 328.1601 | 0.51758 | 2.3849 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7635102.5266 | 8548499.3464 | 8548499.3464 | 62.4231 | 62.254 | 1.0014 | 0.99825 | 684977.7606 | 893983.2641 | 459.6101 | 0.50695 | 0 | 0 | 30.5409 | 25.7701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017974 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 596.1819 | 1367.9646 | 54.1328 | 43.7023 | 30.1046 | 1787.9016 | 65.8431 | 27.1024 | #NV | #NV | #NV | #NV | #NV | 74.6076 | 2.3157 | 1.328 | 0.72393 | 4.8033 | 4.3317 | #NV | 0 | 100 | 586.5 | 326 | 98.9 | 104.03 | 102 | 321.2 | 3 | 86.95 | 39.77 | 4 | 35.03 | 44.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 96.65 | 0 | 35.86 | 64 | 64 | 93.08 | 83.66 | 74.37 | 0 | 102 | 2.2 | 85.7 | 40.63 | 98.9 | 17.09 | 104.03 | 110 | 0 | 16071 | 76.8 | 112.17 | 207.2 | 208.9 | 206.89 | 0 | 29.41 | 47.76 | 12398 | 86.94 | 39.77 | 35.03 | 4.55 | 39.77 | 0 | 603 | 448 | 457.1 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.7 | 326.5 | 0 | 320.1 | 102.03 | 16072 | 16071 | 324
03/26/22 10:17:01.213 | 629.4097 | 1366.0543 | 56.1688 | 45.1369 | 11.0319 | 30.6514 | 50.7707 | 0 | 1790.2939 | 82.5776 | 73.0829 | 9.4947 | 26.0321 | 68.7693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9841 | 460.3201 | 457.2301 | 461.0901 | 429.8701 | 460.6001 | 438.0701 | 327.8501 | 0.52088 | 2.2176 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7579821.6677 | 8507707.2025 | 8507707.2025 | 62.4231 | 62.2529 | 1.0014 | 0.99825 | 683682.8132 | 894456.3543 | 459.5467 | 0.50412 | 0 | 0 | 30.6514 | 26.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017969 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 596.8517 | 1367.9629 | 54.1567 | 43.7144 | 30.1128 | 1787.8386 | 65.9194 | 27.0861 | #NV | #NV | #NV | #NV | #NV | 74.6959 | 2.3172 | 1.3258 | 0.72958 | 4.7101 | 4.3374 | #NV | 0 | 100 | 586.2 | 324 | 99 | 104.03 | 101.95 | 317.2 | 3 | 87.02 | 39.78 | 4 | 35.04 | 44.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 96.8 | 0 | 35.89 | 64 | 64 | 93.2 | 83.74 | 74.48 | 0 | 101.95 | 2.2 | 85.78 | 40.66 | 98.98 | 17.03 | 104.03 | 110 | 0 | 16065 | 76.82 | 112.2 | 207.49 | 209.07 | 207.17 | 0 | 29.46 | 47.84 | 12402 | 87 | 39.79 | 35.05 | 4.5 | 39.79 | 0 | 604 | 448.7 | 457.2 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.3 | 325.7 | 0 | 319.3 | 101.97 | 16063 | 16065 | 325
03/26/22 10:17:06.213 | 628.7356 | 1368.5419 | 56.1412 | 45.1428 | 10.9984 | 31.0149 | 50.7762 | 0 | 1790.6758 | 82.6365 | 73.1697 | 9.4668 | 25.5052 | 68.7499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.978 | 460.29 | 457.18 | 461.03 | 429.89 | 460.46 | 437.92 | 327.76 | 0.5213 | 2.3534 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7571945.1576 | 8488465.5116 | 8488465.5116 | 62.4231 | 62.2524 | 1.0014 | 0.99825 | 684613.7483 | 894572.0904 | 459.5 | 0.5049 | 0 | 0 | 31.0149 | 25.5052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017966 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 597.5049 | 1367.952 | 54.1802 | 43.7265 | 30.1217 | 1787.7861 | 65.9958 | 27.0676 | #NV | #NV | #NV | #NV | #NV | 74.7843 | 2.3128 | 1.3233 | 0.73514 | 4.6256 | 4.343 | #NV | 0 | 100 | 587.4 | 324 | 99.15 | 104.01 | 102.16 | 320.7 | 3 | 87.09 | 39.87 | 4 | 35.14 | 44.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 96.98 | 0 | 35.99 | 64 | 64 | 93.4 | 83.85 | 74.64 | 0 | 102.16 | 2.2 | 85.88 | 40.76 | 99.17 | 16.9 | 104.01 | 110 | 0 | 16058 | 76.86 | 112.2 | 207.67 | 209.34 | 207.35 | 0 | 29.46 | 47.96 | 12407 | 87.11 | 39.88 | 35.14 | 4.35 | 39.88 | 0 | 603 | 450 | 456.5 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.6 | 326.4 | 0 | 320 | 102.19 | 16058 | 16058 | 323
03/26/22 10:17:11.213 | 626.2422 | 1369.5277 | 56.0882 | 45.1398 | 10.9484 | 30.7966 | 50.7707 | 0 | 1783.8168 | 82.7363 | 73.3107 | 9.4256 | 25.5505 | 68.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9731 | 460.2401 | 457.1401 | 460.9801 | 429.8601 | 460.3301 | 437.7901 | 327.6701 | 0.52323 | 2.8756 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7542007.9405 | 8414569.0032 | 8414569.0032 | 62.4232 | 62.2512 | 1.0014 | 0.99824 | 685425.1916 | 891193.8108 | 459.4534 | 0.5035 | 0 | 0 | 30.7966 | 25.5505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017977 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 598.1398 | 1367.9484 | 54.2034 | 43.7385 | 30.1305 | 1787.706 | 66.0729 | 27.0472 | #NV | #NV | #NV | #NV | #NV | 74.8731 | 2.3095 | 1.32 | 0.74047 | 4.5408 | 4.3486 | #NV | 0 | 100 | 587.8 | 324 | 99.33 | 103.99 | 102.24 | 320.1 | 3 | 87.19 | 39.96 | 4 | 35.21 | 44.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 97.13 | 0 | 36.06 | 64 | 64 | 93.55 | 83.93 | 74.78 | 0 | 102.24 | 2.2 | 85.96 | 40.83 | 99.38 | 16.79 | 103.99 | 110 | 0 | 16049 | 76.9 | 112.22 | 207.86 | 209.6 | 207.55 | 0 | 29.47 | 48.03 | 12412 | 87.2 | 39.96 | 35.21 | 4.25 | 39.96 | 0 | 603 | 447.1 | 456.7 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.8 | 328.5 | 0 | 322 | 102.23 | 16051 | 16049 | 324
03/26/22 10:17:16.213 | 624.2122 | 1368.3613 | 56.0446 | 45.1296 | 10.9149 | 30.5318 | 50.775 | 0 | 1783.7652 | 82.8112 | 73.4131 | 9.3981 | 25.9978 | 68.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.973 | 460.24 | 457.14 | 460.98 | 429.86 | 460.33 | 437.79 | 327.67 | 0.52493 | 2.8305 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7517499.1801 | 8394537.3606 | 8394537.3606 | 62.4233 | 62.2505 | 1.0014 | 0.99824 | 684910.317 | 891163.5071 | 459.4534 | 0.5035 | 0 | 0 | 30.5318 | 25.9978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017979 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 598.7524 | 1367.943 | 54.2261 | 43.7504 | 30.1337 | 1787.6588 | 66.1504 | 27.0376 | #NV | #NV | #NV | #NV | #NV | 74.9619 | 2.3074 | 1.3164 | 0.74553 | 4.5374 | 4.3545 | #NV | 0 | 100 | 587.4 | 324 | 99.53 | 103.99 | 102.09 | 318.5 | 3 | 87.3 | 40 | 4 | 35.25 | 44.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 97.28 | 0 | 36.11 | 64 | 64 | 93.68 | 84 | 74.92 | 0 | 102.09 | 2.2 | 86.05 | 40.89 | 99.55 | 16.68 | 103.99 | 110 | 0 | 16039 | 76.94 | 112.24 | 208.05 | 209.79 | 207.74 | 0 | 29.37 | 47.94 | 12417 | 87.31 | 40.01 | 35.26 | 4.18 | 40.01 | 0 | 603 | 446.8 | 456.8 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.1 | 327.4 | 0 | 321 | 102.1 | 16038 | 16039 | 324
03/26/22 10:17:21.212 | 620.8128 | 1367.969 | 55.9655 | 45.1 | 10.8656 | 31.1861 | 50.7694 | 0 | 1789.0862 | 82.9373 | 73.5794 | 9.3579 | 25.4753 | 68.7371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9681 | 460.1501 | 457.0401 | 460.8801 | 429.9901 | 460.4801 | 437.8801 | 327.7001 | 0.52786 | 2.5546 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7477166.9073 | 8378582.5691 | 8378582.5691 | 62.4235 | 62.249 | 1.0014 | 0.99823 | 684651.2031 | 893794.8316 | 459.3567 | 0.50433 | 0 | 0 | 31.1861 | 25.4753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017971 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 599.3491 | 1367.935 | 54.2484 | 43.7622 | 30.139 | 1787.6483 | 66.2282 | 27.0251 | #NV | #NV | #NV | #NV | #NV | 75.0508 | 2.3052 | 1.3122 | 0.75023 | 4.5375 | 4.3602 | #NV | 0 | 100 | 587.3 | 326 | 99.58 | 103.97 | 102.14 | 318 | 3 | 87.33 | 40.08 | 4 | 35.32 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 97.35 | 0 | 36.19 | 64 | 64 | 93.77 | 84.06 | 75.02 | 0 | 102.14 | 2.2 | 86.09 | 40.96 | 99.6 | 16.63 | 103.97 | 110 | 0 | 16029 | 76.96 | 112.26 | 208.24 | 210.06 | 208.04 | 0 | 29.37 | 48.06 | 12422 | 87.34 | 40.09 | 35.34 | 4.08 | 40.09 | 0 | 603 | 447.6 | 456.8 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.4 | 324.3 | 0 | 317.9 | 102.16 | 16031 | 16029 | 324
03/26/22 10:17:26.213 | 619.151 | 1368.5367 | 55.8981 | 45.0663 | 10.8318 | 30.7186 | 50.7692 | 0 | 1793.9014 | 83.045 | 73.7133 | 9.3317 | 26.2147 | 68.7334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.968 | 460.15 | 457.04 | 460.88 | 429.99 | 460.48 | 437.88 | 327.7 | 0.52927 | 2.3205 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7456825.9091 | 8378282.6181 | 8378282.6181 | 62.4237 | 62.2479 | 1.0014 | 0.99822 | 684938.6633 | 896184.5655 | 459.3567 | 0.50433 | 0 | 0 | 30.7186 | 26.2147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017961 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 599.9207 | 1367.9273 | 54.27 | 43.7738 | 30.1431 | 1787.6667 | 66.3069 | 27.0153 | #NV | #NV | #NV | #NV | #NV | 75.1403 | 2.3008 | 1.3071 | 0.75425 | 4.5562 | 4.3667 | #NV | 0 | 100 | 587.7 | 324 | 99.7 | 103.92 | 102.21 | 318.7 | 3 | 87.4 | 40.15 | 4 | 35.4 | 44.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 97.48 | 0 | 36.25 | 64 | 64 | 93.9 | 84.13 | 75.08 | 0 | 102.21 | 2.2 | 86.16 | 41.03 | 99.73 | 16.51 | 103.92 | 110 | 0 | 16020 | 77 | 112.26 | 208.44 | 210.23 | 208.23 | 0 | 29.32 | 48.07 | 12427 | 87.4 | 40.15 | 35.4 | 3.98 | 40.15 | 0 | 603 | 447.7 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.7 | 325.1 | 0 | 318.7 | 102.21 | 16025 | 16020 | 324
03/26/22 10:17:31.212 | 617.3865 | 1367.5304 | 55.8201 | 45.0114 | 10.8087 | 31.0187 | 50.7593 | 0 | 1792.8485 | 83.1871 | 73.8711 | 9.316 | 25.4498 | 68.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9701 | 460.0501 | 456.9901 | 460.8301 | 429.5801 | 460.0701 | 437.6701 | 327.4001 | 0.5303 | 2.3039 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7435895.8821 | 8358224.4225 | 8358224.4225 | 62.4239 | 62.2466 | 1.0015 | 0.99822 | 684438.8159 | 895639.888 | 459.2901 | 0.50077 | 0 | 0 | 31.0187 | 25.4498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017957 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 600.4701 | 1367.9069 | 54.2911 | 43.785 | 30.1512 | 1787.6899 | 66.3861 | 26.9979 | #NV | #NV | #NV | #NV | #NV | 75.2301 | 2.2898 | 1.3015 | 0.75763 | 4.5795 | 4.3737 | #NV | 0 | 100 | 587.2 | 326 | 99.78 | 103.89 | 102.12 | 320.9 | 3 | 87.44 | 40.22 | 4 | 35.46 | 44.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 97.6 | 0 | 36.31 | 64 | 64 | 93.98 | 84.18 | 75.12 | 0 | 102.12 | 2.2 | 86.23 | 41.09 | 99.8 | 16.44 | 103.89 | 110 | 0 | 16010 | 77.04 | 112.28 | 208.73 | 210.41 | 208.43 | 0 | 29.24 | 48.06 | 12432 | 87.45 | 40.22 | 35.48 | 3.85 | 40.22 | 0 | 603 | 448.2 | 456.8 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.2 | 325.9 | 0 | 319.5 | 102.12 | 16010 | 16010 | 325
03/26/22 10:17:36.212 | 617.3865 | 1367.6026 | 55.8032 | 44.9962 | 10.807 | 30.8899 | 50.7519 | 0 | 1792.6524 | 83.2218 | 73.9064 | 9.3155 | 25.6754 | 68.7449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.97 | 460.05 | 456.99 | 460.83 | 429.58 | 460.07 | 437.67 | 327.4 | 0.5303 | 2.3039 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7435895.8821 | 8358224.4225 | 8358224.4225 | 62.4239 | 62.2466 | 1.0015 | 0.99822 | 684438.8159 | 895639.888 | 459.29 | 0.50077 | 0 | 0 | 30.8899 | 25.6754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017959 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 601.0203 | 1367.8988 | 54.3119 | 43.7961 | 30.1591 | 1787.7006 | 66.4654 | 26.9847 | #NV | #NV | #NV | #NV | #NV | 75.32 | 2.2884 | 1.2954 | 0.76064 | 4.5889 | 4.3799 | #NV | 0 | 100 | 587 | 322 | 99.95 | 103.87 | 102.12 | 320.2 | 3 | 87.53 | 40.3 | 4 | 35.54 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 97.7 | 0 | 36.38 | 64 | 64 | 94.1 | 84.23 | 75.18 | 0 | 102.12 | 2.2 | 86.29 | 41.15 | 99.95 | 16.34 | 103.87 | 110 | 0 | 16000 | 77.08 | 112.3 | 208.93 | 210.68 | 208.62 | 0 | 29.27 | 48.29 | 12437 | 87.53 | 40.3 | 35.54 | 3.72 | 40.3 | 0 | 603 | 447.2 | 456.8 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.3 | 323.6 | 0 | 317.2 | 102.14 | 16001 | 16000 | 324
03/26/22 10:17:41.213 | 617.0611 | 1365.9149 | 55.7284 | 44.913 | 10.8155 | 30.8857 | 50.7746 | 0 | 1790.01 | 83.3938 | 74.0678 | 9.326 | 25.4075 | 68.7458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9691 | 459.9801 | 456.9601 | 460.7701 | 429.4201 | 459.8601 | 437.6601 | 327.2701 | 0.53037 | 2.3068 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7431841.2098 | 8353583.4404 | 8353583.4404 | 62.4242 | 62.2447 | 1.0015 | 0.99821 | 683634.788 | 894198.4657 | 459.2368 | 0.49575 | 0 | 0 | 30.8857 | 25.4075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017955 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 601.5607 | 1367.8892 | 54.3322 | 43.8068 | 30.1652 | 1787.7066 | 66.5453 | 26.9704 | #NV | #NV | #NV | #NV | #NV | 75.4102 | 2.2931 | 1.2889 | 0.76276 | 4.5912 | 4.3867 | #NV | 0 | 100 | 587.1 | 322 | 100.02 | 103.85 | 102.1 | 319.1 | 3 | 87.58 | 40.36 | 4 | 35.6 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 97.8 | 0 | 36.45 | 64 | 64 | 94.17 | 84.29 | 75.28 | 0 | 102.1 | 2.2 | 86.34 | 41.23 | 100.02 | 16.27 | 103.85 | 110 | 0 | 15990 | 77.15 | 112.32 | 209.12 | 210.85 | 208.81 | 0 | 29.28 | 48.35 | 12442 | 87.58 | 40.36 | 35.6 | 3.61 | 40.36 | 0 | 603 | 447 | 456.7 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.1 | 325.5 | 0 | 319.1 | 102.1 | 15991 | 15990 | 322
03/26/22 10:17:46.213 | 617.6571 | 1365.8943 | 55.6972 | 44.8712 | 10.826 | 30.1068 | 50.7614 | 0 | 1788.4204 | 83.4761 | 74.1389 | 9.3371 | 26.8592 | 68.7243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.97 | 459.99 | 456.99 | 460.78 | 429.08 | 459.46 | 437.43 | 327.03 | 0.52947 | 2.3242 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7438310.214 | 8357653.815 | 8357653.815 | 62.4243 | 62.244 | 1.0015 | 0.9982 | 683625.9727 | 893395.906 | 459.2534 | 0.49283 | 0 | 0 | 30.1068 | 26.8592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017954 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 602.1007 | 1367.8849 | 54.3522 | 43.8173 | 30.1706 | 1787.7277 | 66.6254 | 26.9585 | #NV | #NV | #NV | #NV | #NV | 75.5007 | 2.2961 | 1.2819 | 0.76439 | 4.5857 | 4.393 | #NV | 0 | 100 | 586.7 | 323 | 100 | 103.85 | 102.03 | 317.1 | 3 | 87.56 | 40.41 | 4 | 35.65 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 97.83 | 0 | 36.5 | 64 | 64 | 94.2 | 84.3 | 75.38 | 0 | 102.03 | 2.2 | 86.36 | 41.28 | 100 | 16.26 | 103.82 | 110 | 0 | 15981 | 77.19 | 112.34 | 209.32 | 211.03 | 209 | 0 | 29.25 | 48.39 | 12447 | 87.56 | 40.41 | 35.65 | 3.56 | 40.41 | 0 | 603 | 446.3 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.6 | 324 | 0 | 317.6 | 102.02 | 15982 | 15981 | 323
03/26/22 10:17:51.213 | 619.4478 | 1366.9575 | 55.6543 | 44.8055 | 10.8488 | 30.5672 | 50.748 | 0 | 1790.3093 | 83.6113 | 74.25 | 9.3612 | 25.8555 | 68.7697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9791 | 459.9901 | 457.0301 | 460.7601 | 428.3301 | 458.5801 | 436.8601 | 326.4901 | 0.52707 | 2.2216 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7460223.2058 | 8386691.479 | 8386691.479 | 62.4245 | 62.2429 | 1.0015 | 0.9982 | 684160.1833 | 894326.2247 | 459.2601 | 0.48556 | 0 | 0 | 30.5672 | 25.8555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017949 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 602.6364 | 1367.8816 | 54.3719 | 43.8275 | 30.1793 | 1787.7221 | 66.7057 | 26.9401 | #NV | #NV | #NV | #NV | #NV | 75.5913 | 2.2981 | 1.2747 | 0.76557 | 4.5831 | 4.3989 | #NV | 0 | 100 | 586.8 | 323 | 99.93 | 103.8 | 102.05 | 316.6 | 3 | 87.52 | 40.48 | 4 | 35.71 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 97.8 | 0 | 36.56 | 64 | 64 | 94.17 | 84.29 | 75.44 | 0 | 102.05 | 2.19 | 86.34 | 41.34 | 99.93 | 16.28 | 103.8 | 110 | 0 | 15970 | 77.23 | 112.36 | 209.51 | 211.31 | 209.2 | 0 | 29.25 | 48.51 | 12452 | 87.52 | 40.48 | 35.71 | 3.5 | 40.48 | 0 | 603 | 447.3 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.6 | 323 | 0 | 316.6 | 102.02 | 15973 | 15970 | 324
03/26/22 10:17:56.212 | 619.6677 | 1365.5537 | 55.6354 | 44.7717 | 10.8637 | 30.8834 | 50.7407 | 0 | 1792.2963 | 83.6846 | 74.3078 | 9.3768 | 25.1246 | 68.7813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9791 | 459.9901 | 457.0301 | 460.7601 | 428.3301 | 458.5801 | 436.8601 | 326.4901 | 0.52688 | 1.9804 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7463112.3404 | 8408948.2303 | 8408948.2303 | 62.4245 | 62.2423 | 1.0015 | 0.9982 | 683458.5083 | 895311.8678 | 459.2601 | 0.48556 | 0 | 0 | 30.8834 | 25.1246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017947 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 603.1681 | 1367.8643 | 54.3913 | 43.8374 | 30.1887 | 1787.6764 | 66.7862 | 26.9192 | #NV | #NV | #NV | #NV | #NV | 75.6822 | 2.3039 | 1.2671 | 0.76618 | 4.4948 | 4.4046 | #NV | 0 | 100 | 587 | 323 | 99.93 | 103.75 | 102.09 | 317 | 3 | 87.52 | 40.54 | 4 | 35.77 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 97.9 | 0 | 36.63 | 64 | 64 | 94.27 | 84.35 | 75.5 | 0 | 102.09 | 2.19 | 86.4 | 41.41 | 99.95 | 16.21 | 103.75 | 110 | 0 | 15963 | 77.28 | 112.36 | 209.71 | 211.5 | 209.49 | 0 | 29.31 | 48.74 | 12457 | 87.53 | 40.55 | 35.79 | 3.42 | 40.55 | 0 | 603 | 444.5 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.9 | 324.2 | 0 | 317.8 | 102.07 | 15965 | 15963 | 324
03/26/22 10:18:01.213 | 620.8253 | 1365.724 | 55.6176 | 44.735 | 10.8826 | 30.7664 | 50.75 | 0 | 1791.4293 | 83.7679 | 74.3716 | 9.3962 | 25.0542 | 68.7784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9791 | 459.9901 | 457.0301 | 460.7601 | 428.3301 | 458.5801 | 436.8601 | 326.4901 | 0.5259 | 1.985 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7476904.0032 | 8422083.6426 | 8422083.6426 | 62.4246 | 62.2416 | 1.0015 | 0.99819 | 683544.6155 | 894871.0924 | 459.2601 | 0.48556 | 0 | 0 | 30.7664 | 25.0542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017949 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 603.6995 | 1367.8529 | 54.4104 | 43.8471 | 30.192 | 1787.6477 | 66.8669 | 26.9066 | #NV | #NV | #NV | #NV | #NV | 75.7731 | 2.3094 | 1.2594 | 0.76641 | 4.4539 | 4.4099 | #NV | 0 | 100 | 586.4 | 324 | 100.05 | 103.72 | 101.98 | 315.7 | 3 | 87.59 | 40.59 | 4 | 35.83 | 43.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 97.98 | 0 | 36.66 | 64 | 64 | 94.33 | 84.38 | 75.54 | 0 | 101.98 | 2.19 | 86.44 | 41.45 | 100.1 | 16.12 | 103.72 | 110 | 0 | 15954 | 77.34 | 112.4 | 209.9 | 211.69 | 209.59 | 0 | 29.46 | 49.02 | 12462 | 87.6 | 40.6 | 35.83 | 3.34 | 40.6 | 0 | 603 | 444.7 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.2 | 322.9 | 0 | 316.6 | 101.95 | 15955 | 15954 | 324
03/26/22 10:18:06.212 | 623.59 | 1367.6233 | 55.5994 | 44.6831 | 10.9163 | 30.3874 | 50.7453 | 0 | 1788.694 | 83.9044 | 74.4726 | 9.4317 | 25.9016 | 68.8056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.98 | 459.98 | 457.09 | 460.69 | 427.31 | 457.15 | 436 | 325.67 | 0.52225 | 2.1638 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7509596.2969 | 8437054.7278 | 8437054.7278 | 62.4247 | 62.2406 | 1.0015 | 0.99819 | 684772.4009 | 893453.0612 | 459.2533 | 0.47105 | 0 | 0 | 30.3874 | 25.9016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017947 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 604.2409 | 1367.8616 | 54.4294 | 43.8566 | 30.1946 | 1787.655 | 66.9478 | 26.8959 | #NV | #NV | #NV | #NV | #NV | 75.8643 | 2.3076 | 1.2515 | 0.76623 | 4.4544 | 4.4149 | #NV | 0 | 100 | 586.3 | 323 | 100.15 | 103.7 | 101.97 | 314.4 | 3 | 87.64 | 40.63 | 4 | 35.86 | 43.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.02 | 0 | 36.71 | 64 | 64 | 94.38 | 84.4 | 75.6 | 0 | 101.97 | 2.19 | 86.47 | 41.5 | 100.15 | 16.05 | 103.7 | 110 | 0 | 15950 | 77.38 | 112.42 | 210 | 211.79 | 209.79 | 0 | 29.6 | 49.12 | 12467 | 87.64 | 40.63 | 35.86 | 3.28 | 40.63 | 0 | 603 | 445 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.5 | 324.4 | 0 | 318 | 102 | 15949 | 15950 | 320
03/26/22 10:18:11.212 | 624.3772 | 1367.102 | 55.5964 | 44.6628 | 10.9337 | 30.4291 | 50.7506 | 0 | 1789.2049 | 83.9708 | 74.5214 | 9.4494 | 25.9223 | 68.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.981 | 459.99 | 457.11 | 460.68 | 427.03 | 456.71 | 435.73 | 325.43 | 0.52121 | 1.9973 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7519257.6249 | 8459816.8674 | 8459816.8674 | 62.4248 | 62.24 | 1.0015 | 0.99818 | 684235.3324 | 893741.9346 | 459.26 | 0.46814 | 0 | 0 | 30.4291 | 25.9223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017945 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 604.7691 | 1367.8527 | 54.4481 | 43.866 | 30.2005 | 1787.6751 | 67.0285 | 26.8807 | #NV | #NV | #NV | #NV | #NV | 75.9553 | 2.3052 | 1.2435 | 0.76589 | 4.4527 | 4.419 | #NV | 0 | 100 | 586.9 | 321 | 100.23 | 103.68 | 102.07 | 317.1 | 3 | 87.69 | 40.71 | 4 | 35.94 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.1 | 0 | 36.79 | 64 | 64 | 94.48 | 84.46 | 75.64 | 0 | 102.07 | 2.19 | 86.51 | 41.57 | 100.23 | 15.99 | 103.68 | 110 | 0 | 15942 | 77.43 | 112.44 | 210.2 | 204.2 | 209.98 | 0 | 29.57 | 48.98 | 12472 | 87.69 | 40.71 | 35.94 | 3.19 | 40.71 | 0 | 603 | 446.6 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.9 | 323.4 | 0 | 317.1 | 102.07 | 15944 | 15942 | 321
03/26/22 10:18:16.211 | 624.8624 | 1366.751 | 55.5965 | 44.6515 | 10.945 | 30.089 | 50.7554 | 0 | 1790.4745 | 84.0127 | 74.5521 | 9.4606 | 26.5108 | 68.8201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.981 | 459.99 | 457.11 | 460.68 | 427.03 | 456.71 | 435.73 | 325.43 | 0.5208 | 1.8557 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7524773.7201 | 8476419.1047 | 8476419.1047 | 62.4248 | 62.2396 | 1.0015 | 0.99818 | 684059.678 | 894372.4338 | 459.26 | 0.46814 | 0 | 0 | 30.089 | 26.5108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016243 | 0.017946 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 605.2953 | 1367.8359 | 54.4667 | 43.8752 | 30.2045 | 1787.6809 | 67.1094 | 26.8685 | #NV | #NV | #NV | #NV | #NV | 76.0465 | 2.3021 | 1.2354 | 0.76529 | 4.4557 | 4.4228 | #NV | 0 | 100 | 586.2 | 323 | 100.25 | 103.68 | 101.95 | 318 | 3 | 87.7 | 40.76 | 4 | 35.99 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.1 | 0 | 36.84 | 64 | 64 | 94.45 | 84.45 | 75.68 | 0 | 101.95 | 2.19 | 86.51 | 41.62 | 100.23 | 15.99 | 103.68 | 110 | 0 | 15933 | 77.45 | 112.44 | 210.4 | 204.39 | 210.18 | 0 | 29.42 | 48.75 | 12477 | 87.69 | 40.77 | 36 | 3.12 | 40.77 | 0 | 603 | 448.5 | 457 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.5 | 324.5 | 0 | 318.1 | 102 | 15932 | 15933 | 322
03/26/22 10:18:21.211 | 624.9021 | 1363.9538 | 55.6029 | 44.6348 | 10.9681 | 30.8635 | 50.7659 | 0 | 1787.8424 | 84.0959 | 74.612 | 9.4839 | 25.3419 | 68.8283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9801 | 460.0101 | 457.1401 | 460.6901 | 426.4201 | 456.0601 | 435.1501 | 324.9801 | 0.52005 | 1.7691 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7525875.2689 | 8483330.6709 | 8483330.6709 | 62.4248 | 62.239 | 1.0015 | 0.99818 | 682659.3415 | 893050.4288 | 459.2801 | 0.46595 | 0 | 0 | 30.8635 | 25.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01624 | 0.017954 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 605.8146 | 1367.8116 | 54.4852 | 43.8844 | 30.2105 | 1787.6565 | 67.1902 | 26.8544 | #NV | #NV | #NV | #NV | #NV | 76.1375 | 2.3203 | 1.2273 | 0.76455 | 4.4342 | 4.4258 | #NV | 0 | 100 | 586 | 320 | 100.25 | 103.65 | 101.91 | 317.1 | 3 | 87.69 | 40.8 | 4 | 36.03 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.13 | 0 | 36.88 | 64 | 64 | 94.5 | 84.48 | 75.7 | 0 | 101.91 | 2.19 | 86.52 | 41.66 | 100.25 | 15.95 | 103.65 | 110 | 0 | 15928 | 77.49 | 112.46 | 210.6 | 204.58 | 210.38 | 0 | 29.3 | 48.69 | 12482 | 87.7 | 40.8 | 36.03 | 3.08 | 40.8 | 0 | 603 | 443.4 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 323.4 | 0 | 317.1 | 101.91 | 15928 | 15928 | 320
03/26/22 10:18:26.211 | 626.5541 | 1365.8531 | 55.6106 | 44.6288 | 10.9818 | 30.5292 | 50.7661 | 0 | 1786.3302 | 84.1457 | 74.6477 | 9.4979 | 25.707 | 68.8449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.98 | 460.01 | 457.14 | 460.69 | 426.42 | 456.06 | 435.15 | 324.98 | 0.51868 | 1.9284 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7545443.4474 | 8489028.1602 | 8489028.1602 | 62.4248 | 62.2386 | 1.0015 | 0.99818 | 683609.5484 | 892290.7723 | 459.28 | 0.46595 | 0 | 0 | 30.5292 | 25.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016242 | 0.017945 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 606.3392 | 1367.7963 | 54.5035 | 43.8934 | 30.214 | 1787.6422 | 67.2712 | 26.8435 | #NV | #NV | #NV | #NV | #NV | 76.2287 | 2.3241 | 1.2192 | 0.76368 | 4.4343 | 4.4282 | #NV | 0 | 100 | 586.5 | 321 | 100.33 | 103.63 | 102 | 315.3 | 3 | 87.74 | 40.86 | 4 | 36.09 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.25 | 0 | 36.93 | 64 | 64 | 94.58 | 84.52 | 75.74 | 0 | 102 | 2.19 | 86.59 | 41.71 | 100.33 | 15.89 | 103.63 | 110 | 0 | 15923 | 77.53 | 112.48 | 210.8 | 204.78 | 210.48 | 0 | 29.31 | 48.82 | 12487 | 87.74 | 40.86 | 36.09 | 2.99 | 40.86 | 0 | 603 | 444.7 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.5 | 322.9 | 0 | 316.5 | 102 | 15923 | 15923 | 322
03/26/22 10:18:31.213 | 627.1587 | 1364.4905 | 55.6286 | 44.6252 | 11.0034 | 30.0314 | 50.7651 | 0 | 1791.806 | 84.2265 | 74.7066 | 9.5199 | 26.735 | 68.8556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9771 | 459.9901 | 457.1501 | 460.6901 | 425.9001 | 455.5201 | 434.7101 | 324.5901 | 0.51756 | 1.4584 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7552235.5223 | 8535718.0764 | 8535718.0764 | 62.4248 | 62.2379 | 1.0015 | 0.99818 | 682926.7419 | 895018.8644 | 459.2767 | 0.46305 | 0 | 0 | 30.0314 | 26.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016246 | 0.01794 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 606.8609 | 1367.7843 | 54.5218 | 43.9024 | 30.2108 | 1787.7092 | 67.3521 | 26.8458 | #NV | #NV | #NV | #NV | #NV | 76.3198 | 2.3333 | 1.2112 | 0.76275 | 4.3626 | 4.4301 | #NV | 0 | 100 | 586.5 | 321 | 100.28 | 103.63 | 102 | 317.4 | 3 | 87.73 | 40.91 | 4 | 36.13 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.18 | 0 | 36.98 | 64 | 64 | 94.53 | 84.48 | 75.78 | 0 | 102 | 2.18 | 86.55 | 41.75 | 100.25 | 15.93 | 103.63 | 110 | 0 | 15914 | 77.58 | 112.5 | 210.9 | 204.96 | 210.69 | 0 | 29.29 | 48.85 | 12492 | 87.7 | 40.91 | 36.14 | 2.96 | 40.91 | 0 | 603 | 444.4 | 457 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.8 | 323.3 | 0 | 316.9 | 101.88 | 15915 | 15914 | 322
03/26/22 10:18:36.211 | 628.6208 | 1366.2556 | 55.6426 | 44.6278 | 11.0148 | 30.8301 | 50.7637 | 0 | 1788.9004 | 84.2702 | 74.7383 | 9.5319 | 25.1804 | 68.8477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9741 | 459.9901 | 457.1401 | 460.6901 | 425.7501 | 455.3401 | 434.5201 | 324.4501 | 0.51613 | 1.7065 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7570515.6085 | 8530752.6398 | 8530752.6398 | 62.4248 | 62.2376 | 1.0015 | 0.99817 | 683809.4617 | 893563.6455 | 459.2734 | 0.4645 | 0 | 0 | 30.8301 | 25.1804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016245 | 0.017944 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 607.3848 | 1367.7801 | 54.5399 | 43.9113 | 30.2176 | 1787.7743 | 67.4329 | 26.8316 | #NV | #NV | #NV | #NV | #NV | 76.4108 | 2.3353 | 1.2033 | 0.76178 | 4.3033 | 4.4312 | #NV | 0 | 100 | 586 | 322 | 100.28 | 103.6 | 101.91 | 314.4 | 3 | 87.71 | 40.94 | 4 | 36.18 | 43.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.2 | 0 | 37.02 | 64 | 64 | 94.53 | 84.49 | 75.8 | 0 | 101.91 | 2.18 | 86.56 | 41.81 | 100.28 | 15.89 | 103.6 | 110 | 0 | 15909 | 77.62 | 112.52 | 211.1 | 205.05 | 210.79 | 0 | 29.22 | 48.81 | 12497 | 87.71 | 40.95 | 36.18 | 2.96 | 40.95 | 0 | 603 | 441.1 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 320.8 | 0 | 314.4 | 101.91 | 15910 | 15909 | 322
03/26/22 10:18:41.211 | 629.4185 | 1367.5407 | 55.6558 | 44.632 | 11.0238 | 30.7143 | 50.7641 | 0 | 1785.7883 | 84.3044 | 74.7631 | 9.5413 | 25.5507 | 68.8395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9721 | 459.9901 | 457.1401 | 460.7001 | 425.5401 | 455.1501 | 434.2901 | 324.2801 | 0.51521 | 1.8751 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7579968.3458 | 8525661.3748 | 8525661.3748 | 62.4247 | 62.2373 | 1.0015 | 0.99817 | 684263.6187 | 892336.9165 | 459.2767 | 0.46522 | 0 | 0 | 30.7143 | 25.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016244 | 0.017948 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 607.9097 | 1367.7827 | 54.558 | 43.9202 | 30.2214 | 1787.8143 | 67.5138 | 26.8209 | #NV | #NV | #NV | #NV | #NV | 76.5018 | 2.3344 | 1.1953 | 0.76078 | 4.2569 | 4.4314 | #NV | 0 | 100 | 586.5 | 321 | 100.48 | 103.58 | 102 | 317.8 | 3 | 87.8 | 41.01 | 4 | 36.24 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.3 | 0 | 37.08 | 64 | 64 | 94.65 | 84.56 | 75.82 | 0 | 102 | 2.18 | 86.62 | 41.86 | 100.48 | 15.77 | 103.58 | 110 | 0 | 15903 | 77.66 | 112.54 | 211.2 | 205.23 | 210.99 | 0 | 29.15 | 48.84 | 12502 | 87.81 | 41.01 | 36.24 | 2.95 | 41.01 | 0 | 603 | 441.7 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.6 | 322.3 | 0 | 316 | 102.02 | 15904 | 15903 | 320
03/26/22 10:18:46.211 | 631.0201 | 1368.7432 | 55.6797 | 44.6428 | 11.0369 | 30.9905 | 50.7738 | 0 | 1780.9009 | 84.3569 | 74.8015 | 9.5554 | 25.0788 | 68.8403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9741 | 459.9901 | 457.1501 | 460.7201 | 425.2601 | 454.9501 | 434.0201 | 324.1001 | 0.51361 | 2.2312 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7599498.3977 | 8513279.5446 | 8513279.5446 | 62.4247 | 62.2369 | 1.0015 | 0.99817 | 685052.7008 | 889560.247 | 459.2867 | 0.46521 | 0 | 0 | 30.9905 | 25.0788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016242 | 0.01796 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 608.443 | 1367.8026 | 54.5762 | 43.9291 | 30.2256 | 1787.8277 | 67.5947 | 26.8096 | #NV | #NV | #NV | #NV | #NV | 76.5929 | 2.3281 | 1.1872 | 0.75975 | 4.2341 | 4.4306 | #NV | 0 | 100 | 585.8 | 321 | 100.5 | 103.58 | 101.9 | 314.4 | 3 | 87.82 | 41.05 | 4 | 36.28 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.3 | 0 | 37.13 | 64 | 64 | 94.67 | 84.58 | 75.84 | 0 | 101.9 | 2.18 | 86.62 | 41.9 | 100.5 | 15.74 | 103.58 | 110 | 0 | 15898 | 77.7 | 112.58 | 211.41 | 205.41 | 211.21 | 0 | 29.11 | 48.9 | 12507 | 87.84 | 41.05 | 36.28 | 2.96 | 41.05 | 0 | 603 | 441.2 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.8 | 320.7 | 0 | 314.4 | 101.88 | 15896 | 15898 | 321
03/26/22 10:18:51.211 | 631.5477 | 1369.378 | 55.6953 | 44.6514 | 11.0439 | 30.5228 | 50.7721 | 0 | 1780.1835 | 84.3867 | 74.8231 | 9.5636 | 25.9728 | 68.8692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9751 | 459.9701 | 457.1301 | 460.7101 | 425.1001 | 454.7801 | 433.8201 | 323.9601 | 0.51296 | 2.3084 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7605561.6818 | 8512635.8351 | 8512635.8351 | 62.4247 | 62.2367 | 1.0015 | 0.99817 | 685276.8263 | 888800.2333 | 459.2701 | 0.46596 | 0 | 0 | 30.5228 | 25.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016242 | 0.017955 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 608.9719 | 1367.8325 | 54.5941 | 43.938 | 30.2302 | 1787.7999 | 67.6753 | 26.7994 | #NV | #NV | #NV | #NV | #NV | 76.6835 | 2.3111 | 1.1795 | 0.75877 | 4.2731 | 4.4293 | #NV | 0 | 100 | 586.5 | 322 | 100.55 | 103.58 | 101.95 | 315.9 | 3 | 87.86 | 41.12 | 4 | 36.34 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.38 | 0 | 37.16 | 64 | 64 | 94.7 | 84.59 | 75.86 | 0 | 101.95 | 2.18 | 86.65 | 41.95 | 100.55 | 15.71 | 103.58 | 110 | 0 | 15894 | 77.75 | 112.6 | 211.51 | 205.5 | 211.31 | 0 | 29.18 | 49.16 | 12512 | 87.86 | 41.12 | 36.34 | 2.91 | 41.12 | 0 | 603 | 443.6 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.5 | 322.5 | 0 | 316.1 | 102 | 15896 | 15894 | 322
03/26/22 10:18:56.212 | 632.1913 | 1368.6245 | 55.7321 | 44.6736 | 11.0585 | 30.2947 | 50.7756 | 0 | 1794.113 | 84.4454 | 74.8655 | 9.5799 | 26.7616 | 68.8688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.975 | 459.97 | 457.13 | 460.71 | 425.1 | 454.78 | 433.82 | 323.96 | 0.51244 | 1.3638 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7612938.3404 | 8600236.4508 | 8600236.4508 | 62.4245 | 62.2361 | 1.0015 | 0.99817 | 684990.733 | 896151.9207 | 459.27 | 0.46596 | 0 | 0 | 30.2947 | 26.7616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016241 | 0.01793 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 609.4914 | 1367.8487 | 54.6121 | 43.9469 | 30.2301 | 1787.8066 | 67.7558 | 26.7984 | #NV | #NV | #NV | #NV | #NV | 76.774 | 2.3022 | 1.1717 | 0.75778 | 4.2657 | 4.427 | #NV | 0 | 100 | 586.7 | 321 | 100.45 | 103.55 | 102.03 | 315 | 3 | 87.81 | 41.17 | 4 | 36.39 | 44.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.35 | 0 | 37.23 | 64 | 64 | 94.7 | 84.59 | 75.88 | 0 | 102.03 | 2.18 | 86.65 | 42.01 | 100.4 | 15.76 | 103.55 | 110 | 0 | 15889 | 77.77 | 112.64 | 211.71 | 205.69 | 211.52 | 0 | 29.23 | 49.3 | 12517 | 87.8 | 41.17 | 36.39 | 2.9 | 41.17 | 0 | 603 | 441.5 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.7 | 320.7 | 0 | 314.4 | 102.03 | 15892 | 15889 | 322
03/26/22 10:19:01.211 | 631.9285 | 1367.4736 | 55.7449 | 44.6817 | 11.0632 | 31.0743 | 50.7678 | 0 | 1797.0909 | 84.4632 | 74.8783 | 9.5849 | 25.5685 | 68.8477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.975 | 459.97 | 457.13 | 460.71 | 425.1 | 454.78 | 433.82 | 323.96 | 0.51265 | 1.1337 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7610446.5071 | 8617587.8414 | 8617587.8414 | 62.4245 | 62.236 | 1.0015 | 0.99817 | 684414.0843 | 897637.806 | 459.27 | 0.46596 | 0 | 0 | 31.0743 | 25.5685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016246 | 0.01793 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 610.0036 | 1367.8433 | 54.63 | 43.9559 | 30.238 | 1787.8838 | 67.8364 | 26.7843 | #NV | #NV | #NV | #NV | #NV | 76.8645 | 2.3019 | 1.164 | 0.75685 | 4.3073 | 4.424 | #NV | 0 | 100 | 585.8 | 322 | 100.42 | 103.55 | 101.88 | 315.2 | 3 | 87.8 | 41.18 | 4 | 36.4 | 44.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.3 | 0 | 37.25 | 64 | 64 | 94.67 | 84.58 | 75.88 | 0 | 101.88 | 2.18 | 86.62 | 42.04 | 100.48 | 15.73 | 103.55 | 110 | 0 | 15884 | 77.81 | 112.68 | 211.92 | 205.87 | 211.62 | 0 | 29.32 | 49.46 | 12522 | 87.82 | 41.19 | 36.41 | 2.93 | 41.19 | 0 | 603 | 441.8 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.9 | 321.2 | 0 | 314.8 | 101.9 | 15884 | 15884 | 322
03/26/22 10:19:06.211 | 633.5113 | 1369.5483 | 55.7791 | 44.7049 | 11.0742 | 31.3455 | 50.7717 | 0 | 1792.9156 | 84.5062 | 74.9105 | 9.5957 | 24.6155 | 68.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9801 | 459.9801 | 457.0901 | 460.6801 | 424.7401 | 454.2101 | 433.1201 | 323.5401 | 0.51071 | 1.4778 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7629720.9853 | 8606039.4624 | 8606039.4624 | 62.4244 | 62.2356 | 1.0015 | 0.99817 | 685450.7965 | 895548.3738 | 459.2501 | 0.47033 | 0 | 0 | 31.3455 | 24.6155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017932 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 610.502 | 1367.829 | 54.6479 | 43.9649 | 30.2483 | 1787.9139 | 67.9166 | 26.7628 | #NV | #NV | #NV | #NV | #NV | 76.9546 | 2.2971 | 1.1566 | 0.75595 | 4.3385 | 4.4203 | #NV | 0 | 100 | 585.9 | 322 | 100.6 | 103.53 | 101.9 | 314.8 | 3 | 87.89 | 41.22 | 4 | 36.45 | 44.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.48 | 0 | 37.3 | 64 | 64 | 94.85 | 84.66 | 75.88 | 0 | 101.9 | 2.18 | 86.7 | 42.09 | 100.63 | 15.62 | 103.53 | 110 | 0 | 15881 | 77.85 | 112.7 | 212.02 | 205.97 | 211.82 | 0 | 29.41 | 49.6 | 12527 | 87.91 | 41.23 | 36.45 | 2.98 | 41.23 | 0 | 603 | 442.4 | 457 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.9 | 321.2 | 0 | 314.8 | 101.9 | 15881 | 15881 | 322
03/26/22 10:19:11.211 | 633.4898 | 1369.1045 | 55.7884 | 44.7118 | 11.0766 | 31.1477 | 50.7787 | 0 | 1791.1919 | 84.5169 | 74.919 | 9.5979 | 24.9256 | 68.8601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.98 | 459.98 | 457.09 | 460.68 | 424.74 | 454.21 | 433.12 | 323.54 | 0.51073 | 1.5008 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7629370.8258 | 8603239.8772 | 8603239.8772 | 62.4244 | 62.2356 | 1.0015 | 0.99816 | 685339.4637 | 895117.2818 | 459.25 | 0.47033 | 0 | 0 | 31.1477 | 24.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016245 | 0.017935 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 611.0045 | 1367.8293 | 54.6658 | 43.9739 | 30.2522 | 1787.9368 | 67.9968 | 26.748 | #NV | #NV | #NV | #NV | #NV | 77.0446 | 2.2972 | 1.1492 | 0.75506 | 4.3449 | 4.4157 | #NV | 0 | 100 | 586 | 319 | 100.65 | 103.53 | 101.91 | 315.8 | 3 | 87.91 | 41.26 | 4 | 36.48 | 44.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.55 | 0 | 37.33 | 64 | 64 | 94.9 | 84.7 | 75.9 | 0 | 101.91 | 2.18 | 86.76 | 42.11 | 100.65 | 15.61 | 103.53 | 110 | 0 | 15877 | 77.89 | 112.74 | 212.22 | 206.15 | 211.93 | 0 | 29.42 | 49.48 | 12532 | 87.92 | 41.26 | 36.48 | 2.95 | 41.26 | 0 | 603 | 444.7 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 322.3 | 0 | 316 | 101.91 | 15877 | 15877 | 321
03/26/22 10:19:16.211 | 632.8055 | 1366.7252 | 55.8312 | 44.7463 | 11.0849 | 30.6501 | 50.7977 | 0 | 1787.3573 | 84.562 | 74.956 | 9.606 | 25.8839 | 68.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 459.9701 | 457.0501 | 460.6501 | 424.5601 | 453.9701 | 432.8601 | 323.3701 | 0.51101 | 1.5484 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7620583.3801 | 8589924.2346 | 8589924.2346 | 62.4243 | 62.2352 | 1.0015 | 0.99816 | 684035.3125 | 892766.4773 | 459.2234 | 0.47326 | 0 | 0 | 30.6501 | 25.8839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017936 | 0.01348 | 0.00479 | 0.0119 | 0.0119 | 611.4974 | 1367.8256 | 54.6836 | 43.9831 | 30.2544 | 1787.9534 | 68.0767 | 26.739 | #NV | #NV | #NV | #NV | #NV | 77.1343 | 2.2999 | 1.1419 | 0.75424 | 4.3403 | 4.4105 | #NV | 0 | 100 | 586.3 | 322 | 100.58 | 103.55 | 101.97 | 316.5 | 3 | 87.88 | 41.29 | 4 | 36.5 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.55 | 0 | 37.35 | 64 | 64 | 94.88 | 84.69 | 75.96 | 0 | 101.97 | 2.18 | 86.76 | 42.14 | 100.55 | 15.68 | 103.55 | 110 | 0 | 15874 | 77.92 | 112.74 | 212.33 | 206.25 | 212.13 | 0 | 29.26 | 49.25 | 12537 | 87.86 | 41.29 | 36.51 | 2.88 | 41.29 | 0 | 603 | 442.3 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.3 | 320.5 | 0 | 314.2 | 101.97 | 15873 | 15874 | 319
03/26/22 10:19:21.211 | 633.2501 | 1369.0632 | 55.8392 | 44.7532 | 11.086 | 30.9037 | 50.7969 | 0 | 1786.7379 | 84.5702 | 74.9627 | 9.6075 | 25.4354 | 68.9274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 459.9701 | 457.0501 | 460.6501 | 424.5601 | 453.9701 | 432.8601 | 323.3701 | 0.51065 | 1.6119 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7626066.2034 | 8589861.0633 | 8589861.0633 | 62.4243 | 62.2351 | 1.0015 | 0.99816 | 684479.4 | 892717.0887 | 459.2234 | 0.47326 | 0 | 0 | 30.9037 | 25.4354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.01794 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 611.9863 | 1367.8434 | 54.7014 | 43.9923 | 30.2613 | 1787.9217 | 68.1564 | 26.7243 | #NV | #NV | #NV | #NV | #NV | 77.2235 | 2.297 | 1.1348 | 0.75344 | 4.3282 | 4.4046 | #NV | 0 | 100 | 586.9 | 320 | 100.7 | 103.55 | 102.07 | 315.3 | 3 | 87.96 | 41.33 | 4 | 36.55 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.65 | 0 | 37.4 | 64 | 64 | 95 | 84.76 | 76 | 0 | 102.03 | 2.18 | 86.8 | 42.18 | 100.7 | 15.59 | 103.55 | 110 | 0 | 15869 | 77.96 | 112.76 | 212.53 | 206.43 | 212.23 | 0 | 29.18 | 49.2 | 12542 | 87.96 | 41.33 | 36.55 | 2.84 | 41.33 | 0 | 603 | 442.4 | 456.8 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.9 | 321.7 | 0 | 315.3 | 102.07 | 15872 | 15869 | 320
03/26/22 10:19:26.211 | 635.6228 | 1372.1649 | 55.8831 | 44.7929 | 11.0902 | 30.2133 | 50.7917 | 0 | 1787.5121 | 84.6147 | 75.0011 | 9.6136 | 26.3633 | 68.9208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9891 | 459.9601 | 457.0101 | 460.6101 | 424.5401 | 453.8501 | 432.7301 | 323.2901 | 0.50862 | 1.8356 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7654112.7384 | 8597934.7363 | 8597934.7363 | 62.4241 | 62.2347 | 1.0015 | 0.99816 | 686755.2692 | 892838.3285 | 459.1934 | 0.47547 | 0 | 0 | 30.2133 | 26.3633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017933 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 612.4797 | 1367.8683 | 54.7192 | 44.0017 | 30.2658 | 1787.8698 | 68.236 | 26.7125 | #NV | #NV | #NV | #NV | #NV | 77.3126 | 2.3184 | 1.1278 | 0.75271 | 4.309 | 4.3979 | #NV | 0 | 100 | 585.4 | 322 | 100.8 | 103.55 | 101.81 | 315.4 | 3 | 88 | 41.36 | 4 | 36.57 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.68 | 0 | 37.41 | 64 | 64 | 95.02 | 84.78 | 76.04 | 0 | 101.81 | 2.18 | 86.83 | 42.2 | 100.8 | 15.55 | 103.55 | 110 | 0 | 15861 | 77.98 | 112.78 | 212.64 | 206.53 | 212.44 | 0 | 29.08 | 49.14 | 12547 | 88 | 41.36 | 36.57 | 2.81 | 41.36 | 0 | 603 | 442.2 | 456.8 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.7 | 322.2 | 0 | 315.9 | 101.86 | 15862 | 15861 | 319
03/26/22 10:19:31.211 | 634.3075 | 1369.2283 | 55.9087 | 44.8176 | 11.0911 | 30.5088 | 50.7985 | 0 | 1788.1985 | 84.641 | 75.0253 | 9.6157 | 25.8634 | 68.9431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 459.95 | 456.94 | 460.55 | 424.38 | 453.47 | 432.26 | 323.02 | 0.50925 | 1.5939 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7638532.5709 | 8602504.3136 | 8602504.3136 | 62.424 | 62.2345 | 1.0015 | 0.99816 | 685284.268 | 893178.2391 | 459.1467 | 0.4806 | 0 | 0 | 30.5088 | 25.8634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01624 | 0.017933 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 612.9634 | 1367.8918 | 54.7369 | 44.0111 | 30.2703 | 1787.8399 | 68.3153 | 26.7006 | #NV | #NV | #NV | #NV | #NV | 77.4014 | 2.3333 | 1.121 | 0.75201 | 4.2889 | 4.3906 | #NV | 0 | 100 | 586 | 322 | 100.78 | 103.55 | 101.91 | 314 | 3 | 87.99 | 41.4 | 4 | 36.61 | 44.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.68 | 0 | 37.46 | 64 | 64 | 95.02 | 84.78 | 76.06 | 0 | 101.91 | 2.17 | 86.83 | 42.25 | 100.78 | 15.57 | 103.55 | 110 | 0 | 15857 | 78 | 112.78 | 212.74 | 206.71 | 212.54 | 0 | 28.99 | 49.13 | 12552 | 87.99 | 41.41 | 36.63 | 2.74 | 41.41 | 0 | 603 | 440.8 | 456.8 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 320 | 0 | 313.7 | 101.91 | 15857 | 15857 | 321
03/26/22 10:19:36.210 | 633.575 | 1367.6542 | 55.9367 | 44.8465 | 11.0902 | 30.3667 | 50.7913 | 0 | 1787.2282 | 84.6721 | 75.0549 | 9.6172 | 26.0662 | 68.9406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.991 | 459.95 | 456.92 | 460.55 | 424.13 | 453.18 | 431.94 | 322.8 | 0.50949 | 1.5203 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7629553.4969 | 8599997.2321 | 8599997.2321 | 62.424 | 62.2342 | 1.0015 | 0.99816 | 684515.9421 | 892744.8185 | 459.14 | 0.48351 | 0 | 0 | 30.3667 | 26.0662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017936 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 613.4302 | 1367.901 | 54.7547 | 44.0208 | 30.2714 | 1787.8173 | 68.3944 | 26.6929 | #NV | #NV | #NV | #NV | #NV | 77.4899 | 2.3292 | 1.1144 | 0.75147 | 4.2807 | 4.3828 | #NV | 0 | 100 | 585.2 | 321 | 100.83 | 103.55 | 101.77 | 313.2 | 3 | 88.02 | 41.42 | 4 | 36.64 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.77 | 0 | 37.48 | 64 | 64 | 95.1 | 84.82 | 76.1 | 0 | 101.95 | 2.17 | 86.88 | 42.26 | 100.85 | 15.52 | 103.55 | 110 | 0 | 15854 | 78.02 | 112.79 | 212.95 | 206.8 | 212.65 | 0 | 28.98 | 49.27 | 12557 | 88.03 | 41.42 | 36.63 | 2.77 | 41.42 | 0 | 603 | 443.8 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585 | 322.5 | 0 | 316.1 | 101.74 | 15855 | 15854 | 322
03/26/22 10:19:41.211 | 634.6478 | 1370.3069 | 55.9475 | 44.8591 | 11.0884 | 30.6095 | 50.7814 | 0 | 1787.0166 | 84.6856 | 75.0691 | 9.6165 | 25.7898 | 68.9154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9911 | 459.9501 | 456.9201 | 460.5501 | 424.1301 | 453.1801 | 431.9401 | 322.8001 | 0.50863 | 1.6931 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7642725.9193 | 8597358.6774 | 8597358.6774 | 62.4239 | 62.2341 | 1.0015 | 0.99816 | 685822.1864 | 892582.5738 | 459.1401 | 0.48351 | 0 | 0 | 30.6095 | 25.7898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017935 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 613.8935 | 1367.9304 | 54.7723 | 44.0305 | 30.2791 | 1787.795 | 68.4733 | 26.677 | #NV | #NV | #NV | #NV | #NV | 77.5779 | 2.326 | 1.108 | 0.75096 | 4.2743 | 4.3744 | #NV | 0 | 100 | 583.9 | 320 | 100.98 | 103.55 | 101.55 | 312.9 | 3 | 88.1 | 41.36 | 4 | 36.57 | 44.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.93 | 0 | 37.43 | 64 | 64 | 95.25 | 84.9 | 76.14 | 0 | 101.55 | 2.18 | 86.95 | 42.21 | 100.98 | 15.46 | 103.55 | 110 | 0 | 15851 | 78.04 | 112.81 | 213.05 | 206.99 | 212.75 | 0 | 29.01 | 49.25 | 12562 | 88.1 | 41.36 | 36.57 | 2.85 | 41.36 | 0 | 603 | 440.3 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.9 | 319.2 | 0 | 312.9 | 101.55 | 15852 | 15851 | 320
03/26/22 10:19:46.211 | 633.2343 | 1369.3677 | 55.9705 | 44.8991 | 11.0714 | 30.2966 | 50.7936 | 0 | 1785.7264 | 84.7284 | 75.1227 | 9.6056 | 25.8106 | 68.9989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 459.92 | 456.91 | 460.55 | 423.53 | 452.63 | 431.36 | 322.35 | 0.50905 | 1.6722 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7625469.7548 | 8581419.3952 | 8581419.3952 | 62.4238 | 62.2336 | 1.0015 | 0.99816 | 685350.9485 | 891931.5897 | 459.1267 | 0.4828 | 0 | 0 | 30.2966 | 25.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.01794 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 614.3439 | 1367.9471 | 54.7898 | 44.0403 | 30.29 | 1787.7384 | 68.552 | 26.6564 | #NV | #NV | #NV | #NV | #NV | 77.6656 | 2.3364 | 1.1017 | 0.75056 | 4.2285 | 4.3655 | #NV | 0 | 100 | 583.6 | 320 | 101.1 | 103.58 | 101.5 | 313.1 | 3 | 88.17 | 41.33 | 4 | 36.55 | 44.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.05 | 0 | 37.39 | 64 | 64 | 95.35 | 84.96 | 76.2 | 0 | 101.57 | 2.18 | 87.02 | 42.18 | 101.1 | 15.41 | 103.58 | 110 | 0 | 15849 | 78.07 | 112.83 | 213.16 | 207.08 | 212.96 | 0 | 28.95 | 49.2 | 12567 | 88.17 | 41.33 | 36.55 | 2.87 | 41.33 | 0 | 603 | 442.2 | 457 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.8 | 320.4 | 0 | 314.1 | 101.53 | 15850 | 15849 | 322
03/26/22 10:19:51.210 | 631.7013 | 1368.1187 | 55.9757 | 44.921 | 11.0547 | 30.2829 | 50.8041 | 0 | 1787.0063 | 84.7535 | 75.1592 | 9.5944 | 25.9165 | 68.9972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 459.92 | 456.91 | 460.55 | 423.53 | 452.63 | 431.36 | 322.35 | 0.51029 | 1.4967 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7607038.0568 | 8577593.8558 | 8577593.8558 | 62.4238 | 62.2333 | 1.0014 | 0.99816 | 684725.6065 | 892566.4526 | 459.1267 | 0.4828 | 0 | 0 | 30.2829 | 25.9165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017937 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 614.7589 | 1367.9343 | 54.8072 | 44.0502 | 30.2929 | 1787.7312 | 68.6306 | 26.6455 | 459.7437 | 0.0061636 | 59.9913 | 0.49316 | 3.2656 | 77.753 | 2.3291 | 1.0957 | 0.75032 | 4.2286 | 4.3563 | 0.40082 | 0 | 100 | 584.3 | 319 | 101.23 | 103.6 | 101.62 | 316.1 | 3 | 88.25 | 41.36 | 4 | 36.57 | 44.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.15 | 0 | 37.43 | 64 | 64 | 95.48 | 85.03 | 76.26 | 0 | 101.62 | 2.18 | 87.09 | 42.21 | 101.25 | 15.35 | 103.6 | 110 | 0 | 15847 | 78.09 | 112.85 | 213.26 | 207.28 | 213.07 | 0 | 28.96 | 49.33 | 12572 | 88.25 | 41.37 | 36.59 | 2.84 | 41.37 | 0 | 603 | 438.7 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585 | 319.8 | 0 | 313.5 | 101.74 | 15847 | 15847 | 320
03/26/22 10:19:56.211 | 629.7556 | 1366.9781 | 55.9756 | 44.9457 | 11.0299 | 30.7553 | 50.7851 | 0 | 1783.7497 | 84.7895 | 75.212 | 9.5775 | 25.9455 | 69.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9991 | 459.9301 | 456.9001 | 460.5601 | 423.2801 | 452.3801 | 431.0201 | 322.1401 | 0.51153 | 1.5821 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7584082.0527 | 8546968.4341 | 8546968.4341 | 62.4237 | 62.2329 | 1.0014 | 0.99815 | 684154.7791 | 890933.4374 | 459.1301 | 0.4857 | 0 | 0 | 30.7553 | 25.9455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017945 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 615.1612 | 1367.9188 | 54.8243 | 44.0602 | 30.2995 | 1787.742 | 68.7092 | 26.6316 | 459.7352 | 0.006167 | 59.9914 | 0.49379 | 3.2528 | 77.8401 | 2.32 | 1.0896 | 0.75011 | 4.2213 | 4.3464 | 0.39758 | 0 | 100 | 584.2 | 318 | 101.33 | 103.63 | 101.6 | 313.8 | 3 | 88.29 | 41.38 | 4 | 36.6 | 44.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.27 | 0 | 37.44 | 64 | 64 | 95.6 | 85.1 | 76.32 | 0 | 101.6 | 2.19 | 87.16 | 42.23 | 101.33 | 15.34 | 103.63 | 110 | 0 | 15844 | 78.13 | 112.85 | 213.37 | 207.37 | 213.17 | 0 | 29 | 49.41 | 12577 | 88.29 | 41.38 | 36.6 | 2.82 | 41.38 | 0 | 603 | 443.1 | 457 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.9 | 318.7 | 0 | 312.3 | 101.55 | 15848 | 15844 | 322
03/26/22 10:20:01.210 | 627.5685 | 1364.7847 | 55.9697 | 44.9604 | 11.0093 | 30.4249 | 50.8 | 0 | 1784.4103 | 84.8224 | 75.2587 | 9.5638 | 26.6846 | 69.0001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 459.95 | 456.92 | 460.6 | 422.64 | 451.76 | 430.33 | 321.66 | 0.51255 | 1.3728 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7557504.2645 | 8538665.1208 | 8538665.1208 | 62.4237 | 62.2325 | 1.0014 | 0.99815 | 683057.2837 | 891257.6874 | 459.1567 | 0.48712 | 0 | 0 | 30.4249 | 26.6846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01624 | 0.017942 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 615.5405 | 1367.9015 | 54.8412 | 44.0702 | 30.3026 | 1787.754 | 68.7876 | 26.628 | 459.7267 | 0.0061487 | 59.9915 | 0.49444 | 3.2399 | 77.9268 | 2.3318 | 1.0837 | 0.75 | 4.2087 | 4.3364 | 0.39412 | 0 | 100 | 583.6 | 320 | 101.45 | 103.63 | 101.5 | 313.6 | 3 | 88.36 | 41.37 | 4 | 36.59 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.35 | 0 | 37.41 | 64 | 64 | 95.68 | 85.15 | 76.36 | 0 | 101.5 | 2.19 | 87.2 | 42.2 | 101.48 | 15.26 | 103.63 | 110 | 0 | 15842 | 78.13 | 112.89 | 213.48 | 207.48 | 213.28 | 0 | 28.92 | 49.27 | 12582 | 88.37 | 41.37 | 36.59 | 2.64 | 41.37 | 0 | 603 | 439.1 | 457 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.4 | 321.7 | 0 | 315.4 | 101.46 | 15842 | 15842 | 320
03/26/22 10:20:06.210 | 626.9869 | 1365.6362 | 55.9606 | 44.9701 | 10.9905 | 31.1449 | 50.8103 | 0 | 1784.7303 | 84.8544 | 75.3039 | 9.5506 | 25.5043 | 68.9894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9961 | 459.9501 | 456.9201 | 460.6001 | 422.6401 | 451.7601 | 430.3301 | 321.6601 | 0.51303 | 1.3806 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7551022.2507 | 8529990.7082 | 8529990.7082 | 62.4237 | 62.2322 | 1.0014 | 0.99815 | 683367.5846 | 891454.2912 | 459.1567 | 0.48712 | 0 | 0 | 31.1449 | 25.5043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017949 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 615.9059 | 1367.8837 | 54.8578 | 44.0803 | 30.3098 | 1787.7782 | 68.866 | 26.6177 | 459.7186 | 0.0061311 | 59.9917 | 0.49507 | 3.2264 | 78.0133 | 2.3368 | 1.0777 | 0.74988 | 4.1784 | 4.3259 | 0.39067 | 0 | 100 | 583.8 | 318 | 101.53 | 103.63 | 101.53 | 313.3 | 3 | 88.38 | 41.38 | 4 | 36.61 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.4 | 0 | 37.44 | 64 | 64 | 95.75 | 85.19 | 76.38 | 0 | 101.53 | 2.19 | 87.23 | 42.23 | 101.53 | 15.23 | 103.63 | 110 | 0 | 15840 | 78.15 | 112.89 | 213.58 | 207.57 | 213.38 | 0 | 28.75 | 49.02 | 12587 | 88.4 | 41.4 | 36.61 | 2.48 | 41.4 | 0 | 603 | 437 | 457.1 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.7 | 319.9 | 0 | 313.6 | 101.51 | 15841 | 15840 | 319
03/26/22 10:20:11.210 | 627.1396 | 1368.867 | 55.9445 | 44.9777 | 10.9668 | 31.3221 | 50.8157 | 0 | 1785.4322 | 84.8974 | 75.3646 | 9.5328 | 24.8697 | 68.9968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9931 | 459.9401 | 456.9201 | 460.6001 | 422.4401 | 451.6101 | 430.1701 | 321.5201 | 0.51268 | 1.5556 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7553211.5493 | 8516757.2903 | 8516757.2903 | 62.4237 | 62.2317 | 1.0014 | 0.99815 | 685008.5585 | 891815.5436 | 459.1534 | 0.4864 | 0 | 0 | 31.3221 | 24.8697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017945 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 616.2532 | 1367.8696 | 54.874 | 44.0903 | 30.3167 | 1787.7806 | 68.9443 | 26.6032 | 459.7107 | 0.0061141 | 59.9918 | 0.49571 | 3.2143 | 78.0994 | 2.323 | 1.072 | 0.74977 | 4.1769 | 4.3152 | 0.38764 | 0 | 100 | 584.3 | 317 | 101.65 | 103.63 | 101.62 | 314.6 | 3 | 88.47 | 41.43 | 4 | 36.65 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.53 | 0 | 37.48 | 64 | 64 | 95.85 | 85.24 | 76.48 | 0 | 101.62 | 2.19 | 87.3 | 42.26 | 101.67 | 15.16 | 103.63 | 110 | 0 | 15838 | 78.17 | 112.89 | 213.69 | 207.67 | 213.49 | 0 | 28.52 | 48.87 | 12591 | 88.47 | 41.43 | 36.65 | 2.46 | 41.43 | 0 | 603 | 441.7 | 456.9 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.4 | 320 | 0 | 313.7 | 101.63 | 15840 | 15838 | 320
03/26/22 10:20:16.210 | 625.7206 | 1369.8219 | 55.9172 | 44.9807 | 10.9364 | 30.7415 | 50.8144 | 0 | 1785.2774 | 84.9575 | 75.4479 | 9.5096 | 25.8036 | 69.0088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.989 | 459.96 | 456.95 | 460.63 | 422.13 | 451.31 | 429.9 | 321.31 | 0.5135 | 1.6225 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7535706.4295 | 8493270.2236 | 8493270.2236 | 62.4238 | 62.231 | 1.0014 | 0.99815 | 685580.9139 | 891667.5701 | 459.18 | 0.48565 | 0 | 0 | 30.7415 | 25.8036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017946 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 616.5902 | 1367.8647 | 54.8899 | 44.1003 | 30.3243 | 1787.7753 | 69.0226 | 26.5876 | 459.7029 | 0.0060972 | 59.9919 | 0.49634 | 3.2033 | 78.1852 | 2.3175 | 1.0662 | 0.74959 | 4.1797 | 4.3039 | 0.3844 | 0 | 100 | 584.1 | 317 | 101.63 | 103.65 | 101.58 | 313.9 | 3 | 88.45 | 41.45 | 4 | 36.66 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.58 | 0 | 37.49 | 64 | 64 | 95.88 | 85.26 | 76.56 | 0 | 101.58 | 2.19 | 87.33 | 42.28 | 101.65 | 15.18 | 103.65 | 110 | 0 | 15835 | 78.19 | 112.93 | 213.79 | 207.77 | 213.59 | 0 | 28.46 | 48.96 | 12597 | 88.47 | 41.46 | 36.68 | 2.49 | 41.46 | 0 | 603 | 441 | 457 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.1 | 320.2 | 0 | 313.9 | 101.58 | 15834 | 15835 | 317
03/26/22 10:20:21.210 | 624.5364 | 1369.9664 | 55.8853 | 44.9764 | 10.909 | 30.5492 | 50.8066 | 0 | 1786.7741 | 85.0174 | 75.5287 | 9.4887 | 26.2903 | 69.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 459.98 | 456.95 | 460.63 | 422.14 | 451.24 | 429.83 | 321.29 | 0.51445 | 1.588 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7521237.0942 | 8481825.5027 | 8481825.5027 | 62.4238 | 62.2305 | 1.0015 | 0.99814 | 685649.2904 | 891920.1106 | 459.1867 | 0.48709 | 0 | 0 | 30.5492 | 26.2903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017942 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 616.9083 | 1367.8672 | 54.9054 | 44.1102 | 30.3285 | 1787.7612 | 69.1011 | 26.5822 | 459.6954 | 0.0060809 | 59.992 | 0.49697 | 3.1938 | 78.2709 | 2.3196 | 1.0603 | 0.74931 | 4.182 | 4.2927 | 0.3812 | 0 | 100 | 584.3 | 318 | 101.65 | 103.65 | 101.62 | 311.9 | 3 | 88.47 | 41.47 | 4 | 36.69 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.55 | 0 | 37.51 | 64 | 64 | 95.85 | 85.24 | 76.62 | 0 | 101.62 | 2.19 | 87.31 | 42.3 | 101.67 | 15.17 | 103.65 | 110 | 0 | 15833 | 78.24 | 112.95 | 213.9 | 207.97 | 213.7 | 0 | 28.35 | 48.95 | 12602 | 88.48 | 41.47 | 36.69 | 2.48 | 41.47 | 0 | 603 | 436.8 | 457.1 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.5 | 319 | 0 | 312.7 | 101.65 | 15832 | 15833 | 318
03/26/22 10:20:26.210 | 623.6716 | 1369.8477 | 55.8737 | 44.9734 | 10.9003 | 30.9109 | 50.8134 | 0 | 1786.9083 | 85.0382 | 75.5562 | 9.482 | 25.5102 | 69.0492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 459.9801 | 456.9501 | 460.6301 | 422.1401 | 451.2401 | 429.8301 | 321.2901 | 0.51516 | 1.5404 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7511268.148 | 8475981.2703 | 8475981.2703 | 62.4238 | 62.2301 | 1.0015 | 0.99814 | 685595.9674 | 892468.8188 | 459.1867 | 0.48709 | 0 | 0 | 30.9109 | 25.5102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017947 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 617.2111 | 1367.8766 | 54.9206 | 44.12 | 30.3342 | 1787.7617 | 69.1793 | 26.5709 | 459.688 | 0.0060648 | 59.9921 | 0.49761 | 3.184 | 78.3561 | 2.3242 | 1.0546 | 0.74895 | 4.1819 | 4.2812 | 0.37799 | 0 | 100 | 584.3 | 318 | 101.75 | 103.65 | 101.62 | 315.9 | 3 | 88.51 | 41.5 | 4 | 36.71 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.6 | 0 | 37.54 | 64 | 64 | 95.95 | 85.3 | 76.68 | 0 | 101.62 | 2.19 | 87.34 | 42.33 | 101.8 | 15.1 | 103.65 | 110 | 0 | 15831 | 78.26 | 112.99 | 214.01 | 208.06 | 213.8 | 0 | 28.2 | 48.85 | 12607 | 88.55 | 41.51 | 36.73 | 2.31 | 41.51 | 0 | 604 | 438.5 | 457.2 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.9 | 322.2 | 0 | 315.9 | 101.72 | 15832 | 15831 | 320
03/26/22 10:20:31.210 | 620.534 | 1366.2814 | 55.8279 | 44.9543 | 10.8737 | 30.7915 | 50.8142 | 0 | 1784.0129 | 85.128 | 75.6653 | 9.4627 | 25.6485 | 69.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.984 | 460.01 | 456.99 | 460.64 | 422.1 | 451.07 | 429.8 | 321.25 | 0.5177 | 1.465 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7473441.3518 | 8445096.8714 | 8445096.8714 | 62.424 | 62.2292 | 1.0015 | 0.99814 | 683813.3292 | 891009.3291 | 459.2134 | 0.48416 | 0 | 0 | 30.7915 | 25.6485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01624 | 0.017949 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 617.5084 | 1367.8834 | 54.9355 | 44.1298 | 30.3426 | 1787.7623 | 69.2578 | 26.556 | 459.6805 | 0.0060488 | 59.9921 | 0.49825 | 3.1746 | 78.4413 | 2.3275 | 1.0486 | 0.74841 | 4.1817 | 4.2689 | 0.3746 | 0 | 100 | 585.2 | 320 | 101.83 | 103.65 | 101.77 | 315.3 | 3 | 88.56 | 41.53 | 4 | 36.75 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.67 | 0 | 37.59 | 64 | 64 | 96.03 | 85.34 | 76.74 | 0 | 101.77 | 2.19 | 87.38 | 42.38 | 101.8 | 15.1 | 103.65 | 110 | 0 | 15828 | 78.28 | 113.03 | 214.11 | 208.16 | 213.91 | 0 | 28.02 | 48.79 | 12612 | 88.55 | 41.55 | 36.76 | 2.23 | 41.55 | 0 | 603 | 438.3 | 457.1 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.8 | 318.8 | 0 | 312.5 | 101.7 | 15827 | 15828 | 319
03/26/22 10:20:36.210 | 619.5043 | 1364.7383 | 55.809 | 44.9412 | 10.8678 | 30.4756 | 50.8219 | 0 | 1787.3417 | 85.1731 | 75.7138 | 9.4593 | 26.1818 | 69.0158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 460.01 | 457 | 460.63 | 422.14 | 451.03 | 429.86 | 321.26 | 0.51858 | 1.1594 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7460777.2086 | 8458326.1528 | 8458326.1528 | 62.424 | 62.2287 | 1.0015 | 0.99814 | 683041.9316 | 892665.8958 | 459.2133 | 0.48198 | 0 | 0 | 30.4756 | 26.1818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017947 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 617.7656 | 1367.8544 | 54.9499 | 44.1395 | 30.342 | 1787.7814 | 69.3362 | 26.5519 | 459.6734 | 0.0060334 | 59.9922 | 0.4989 | 3.161 | 78.5262 | 2.3346 | 1.0427 | 0.74768 | 4.1651 | 4.2568 | 0.37126 | 0 | 100 | 584.4 | 320 | 101.83 | 103.65 | 101.63 | 311.5 | 3 | 88.55 | 41.56 | 4 | 36.77 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.73 | 0 | 37.6 | 64 | 64 | 96.03 | 85.36 | 76.8 | 0 | 101.67 | 2.19 | 87.4 | 42.39 | 101.85 | 15.09 | 103.65 | 110 | 0 | 15825 | 78.32 | 113.08 | 214.22 | 208.25 | 214.02 | 0 | 27.84 | 48.75 | 12617 | 88.58 | 41.56 | 36.77 | 2.23 | 41.56 | 0 | 604 | 439.6 | 457.2 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.3 | 320.4 | 0 | 314.1 | 101.62 | 15822 | 15825 | 318
03/26/22 10:20:41.210 | 619.9466 | 1366.4156 | 55.7874 | 44.9217 | 10.8657 | 30.4981 | 50.8219 | 0 | 1786.996 | 85.2321 | 75.7735 | 9.4587 | 26.0671 | 69.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 460.0301 | 457.0201 | 460.6201 | 422.2001 | 450.9901 | 429.9001 | 321.2801 | 0.51824 | 1.2427 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7466199.6246 | 8456636.8134 | 8456636.8134 | 62.4241 | 62.2283 | 1.0015 | 0.99813 | 683649.8175 | 892567.1068 | 459.2234 | 0.4798 | 0 | 0 | 30.4981 | 26.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017949 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 618.0235 | 1367.8482 | 54.964 | 44.149 | 30.345 | 1787.7908 | 69.4146 | 26.5431 | 459.6665 | 0.0060184 | 59.9922 | 0.49952 | 3.1495 | 78.611 | 2.3381 | 1.0368 | 0.74673 | 4.1618 | 4.2443 | 0.368 | 0 | 100 | 585.1 | 319 | 101.88 | 103.65 | 101.76 | 313.6 | 3 | 88.59 | 41.6 | 4 | 36.81 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.75 | 0 | 37.64 | 64 | 64 | 96.08 | 85.37 | 76.84 | 0 | 101.76 | 2.19 | 87.42 | 42.43 | 101.93 | 15.03 | 103.65 | 110 | 0 | 15822 | 78.34 | 113.13 | 214.33 | 208.35 | 214.12 | 0 | 27.74 | 48.85 | 12621 | 88.62 | 41.6 | 36.81 | 2.27 | 41.6 | 0 | 603 | 438.4 | 457 | 26 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585 | 320 | 0 | 313.6 | 101.74 | 15823 | 15822 | 320
03/26/22 10:20:46.210 | 620.2657 | 1366.6117 | 55.7774 | 44.9112 | 10.8662 | 30.6979 | 50.8206 | 0 | 1785.618 | 85.2626 | 75.8032 | 9.4594 | 25.6731 | 69.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 460.0301 | 457.0201 | 460.6201 | 422.2001 | 450.9901 | 429.9001 | 321.2801 | 0.51797 | 1.3735 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7470145.6769 | 8449544.7618 | 8449544.7618 | 62.4241 | 62.2279 | 1.0015 | 0.99813 | 683981.1288 | 891793.9362 | 459.2234 | 0.4798 | 0 | 0 | 30.6979 | 25.6731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017952 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 618.2781 | 1367.8534 | 54.9778 | 44.1584 | 30.3462 | 1787.7505 | 69.4926 | 26.534 | 459.6596 | 0.0060036 | 59.9923 | 0.50013 | 3.1412 | 78.6952 | 2.3343 | 1.0308 | 0.74561 | 4.1474 | 4.2319 | 0.36475 | 0 | 100 | 585.2 | 320 | 101.95 | 103.65 | 101.77 | 312.5 | 3 | 88.63 | 41.62 | 4 | 36.84 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.8 | 0 | 37.68 | 64 | 64 | 96.13 | 85.4 | 76.9 | 0 | 101.77 | 2.19 | 87.45 | 42.46 | 101.95 | 15.02 | 103.65 | 110 | 0 | 15819 | 78.36 | 113.2 | 214.43 | 208.45 | 214.23 | 0 | 27.69 | 49.06 | 12627 | 88.63 | 41.62 | 36.84 | 2.21 | 41.62 | 0 | 604 | 439.1 | 457.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.2 | 318.5 | 0 | 312.1 | 101.77 | 15818 | 15819 | 318
03/26/22 10:20:51.210 | 621.423 | 1368.3355 | 55.7565 | 44.8838 | 10.8727 | 31.3089 | 50.8058 | 0 | 1785.6025 | 85.3446 | 75.88 | 9.4645 | 25.0051 | 69.0129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9961 | 460.1501 | 457.1601 | 460.7101 | 422.0701 | 450.6501 | 429.8201 | 321.2001 | 0.51688 | 1.498 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7484604.1016 | 8453170.1463 | 8453170.1463 | 62.4242 | 62.2271 | 1.0015 | 0.99813 | 684844.8961 | 891776.7114 | 459.3401 | 0.47459 | 0 | 0 | 31.3089 | 25.0051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017951 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 618.5346 | 1367.8637 | 54.9915 | 44.1676 | 30.3457 | 1787.7084 | 69.5705 | 26.5285 | 459.6533 | 0.0059898 | 59.9924 | 0.50072 | 3.1329 | 78.7793 | 2.3346 | 1.0247 | 0.74427 | 4.146 | 4.2193 | 0.36105 | 0 | 100 | 584.8 | 320 | 102 | 103.63 | 101.7 | 314.2 | 3 | 88.66 | 41.65 | 4 | 36.86 | 43.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.85 | 0 | 37.69 | 64 | 64 | 96.15 | 85.41 | 76.9 | 0 | 101.7 | 2.19 | 87.48 | 42.48 | 101.98 | 14.97 | 103.63 | 110 | 0 | 15816 | 78.39 | 113.28 | 214.54 | 208.54 | 214.34 | 0 | 27.81 | 49.44 | 12632 | 88.66 | 41.65 | 36.86 | 2.03 | 41.65 | 0 | 604 | 440.8 | 457.4 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.1 | 321 | 0 | 314.7 | 101.76 | 15816 | 15816 | 318
03/26/22 10:20:56.210 | 620.3416 | 1365.1976 | 55.7491 | 44.8704 | 10.8787 | 31.0711 | 50.7946 | 0 | 1785.6232 | 85.3867 | 75.9175 | 9.4692 | 25.1672 | 69.0166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9961 | 460.1501 | 457.1601 | 460.7101 | 422.0701 | 450.6501 | 429.8201 | 321.2001 | 0.51778 | 1.2894 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7471355.7559 | 8457571.8422 | 8457571.8422 | 62.4242 | 62.2267 | 1.0015 | 0.99813 | 683274.7597 | 891782.3818 | 459.3401 | 0.47459 | 0 | 0 | 31.0711 | 25.1672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016245 | 0.017963 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 618.7853 | 1367.8545 | 55.0052 | 44.1768 | 30.3492 | 1787.7311 | 69.6478 | 26.5174 | 459.6472 | 0.0059768 | 59.9924 | 0.50129 | 3.1193 | 78.8629 | 2.3419 | 1.0183 | 0.74272 | 4.1232 | 4.2073 | 0.35715 | 0 | 100 | 584.3 | 317 | 102 | 103.63 | 101.62 | 311.2 | 3 | 88.66 | 41.65 | 4 | 36.86 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.93 | 0 | 37.71 | 64 | 64 | 96.2 | 85.44 | 76.88 | 0 | 101.62 | 2.19 | 87.52 | 42.5 | 102 | 14.97 | 103.63 | 110 | 0 | 15812 | 78.41 | 113.32 | 214.65 | 208.64 | 214.34 | 0 | 27.82 | 49.42 | 12637 | 88.66 | 41.65 | 36.86 | 1.97 | 41.65 | 0 | 604 | 437.3 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.4 | 318 | 0 | 311.7 | 101.63 | 15813 | 15812 | 318
03/26/22 10:21:01.209 | 621.3888 | 1366.1317 | 55.7416 | 44.8521 | 10.8896 | 31.2 | 50.8002 | 0 | 1779.9564 | 85.4497 | 75.9718 | 9.4779 | 24.8882 | 69.0492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.01 | 460.23 | 457.27 | 460.77 | 421.97 | 450.34 | 429.87 | 321.16 | 0.51684 | 1.6691 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7484054.2896 | 8438010.7624 | 8438010.7624 | 62.4243 | 62.2262 | 1.0015 | 0.99813 | 683742.6431 | 888945.5225 | 459.4233 | 0.4687 | 0 | 0 | 31.2 | 24.8882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016241 | 0.017964 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 619.0369 | 1367.8333 | 55.0188 | 44.1859 | 30.355 | 1787.7047 | 69.7248 | 26.5012 | 459.6412 | 0.0059638 | 59.9925 | 0.50187 | 3.1081 | 78.9463 | 2.3464 | 1.0115 | 0.74093 | 4.157 | 4.1953 | 0.35311 | 0 | 100 | 585 | 320 | 102.08 | 103.63 | 101.67 | 312.8 | 3 | 88.7 | 41.67 | 4 | 36.89 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 99.98 | 0 | 37.75 | 64 | 64 | 96.27 | 85.48 | 76.96 | 0 | 101.67 | 2.19 | 87.55 | 42.54 | 102.13 | 14.9 | 103.63 | 110 | 0 | 15810 | 78.43 | 113.37 | 214.76 | 208.74 | 214.45 | 0 | 27.66 | 49.29 | 12642 | 88.72 | 41.69 | 36.9 | 2.03 | 41.69 | 0 | 604 | 438.3 | 457.4 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.4 | 320.6 | 0 | 314.2 | 101.81 | 15809 | 15810 | 319
03/26/22 10:21:06.209 | 623.7972 | 1370.6682 | 55.7404 | 44.8448 | 10.8956 | 30.5147 | 50.8031 | 0 | 1780.8286 | 85.4805 | 75.998 | 9.4825 | 25.632 | 69.0265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 460.2701 | 457.3301 | 460.8001 | 421.8801 | 450.1801 | 429.8501 | 321.1101 | 0.51477 | 1.8908 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7512442.878 | 8447041.0987 | 8447041.0987 | 62.4243 | 62.2259 | 1.0015 | 0.99812 | 686013.2152 | 889377.8814 | 459.4667 | 0.46503 | 0 | 0 | 30.5147 | 25.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017967 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 619.2903 | 1367.8193 | 55.0326 | 44.1949 | 30.3598 | 1787.6773 | 69.8016 | 26.4872 | 459.6361 | 0.0059526 | 59.9927 | 0.50241 | 3.0966 | 79.0295 | 2.3391 | 1.0044 | 0.73897 | 4.1887 | 4.1825 | 0.34945 | 0 | 100 | 585.5 | 321 | 102.2 | 103.63 | 101.81 | 313.1 | 3 | 88.77 | 41.71 | 4 | 36.93 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.05 | 0 | 37.8 | 64 | 64 | 96.33 | 85.51 | 77 | 0 | 101.81 | 2.19 | 87.59 | 42.58 | 102.23 | 14.85 | 103.63 | 110 | 0 | 15807 | 78.49 | 113.42 | 214.87 | 208.84 | 214.56 | 0 | 27.58 | 49.35 | 12647 | 88.78 | 41.72 | 36.94 | 2.05 | 41.72 | 0 | 604 | 441.2 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.8 | 320.2 | 0 | 313.8 | 101.88 | 15806 | 15807 | 320
03/26/22 10:21:11.210 | 624.8278 | 1371.8965 | 55.7404 | 44.8366 | 10.9038 | 30.004 | 50.8235 | 0 | 1787.5895 | 85.5207 | 76.0326 | 9.4881 | 26.6862 | 69.0302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.016 | 460.27 | 457.33 | 460.8 | 421.88 | 450.18 | 429.85 | 321.11 | 0.51392 | 1.5755 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7524383.7477 | 8485312.7439 | 8485312.7439 | 62.4243 | 62.2255 | 1.0015 | 0.99812 | 686627.9781 | 892750.0946 | 459.4667 | 0.46503 | 0 | 0 | 30.004 | 26.6862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017955 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 619.5719 | 1367.8439 | 55.0465 | 44.2041 | 30.3581 | 1787.6724 | 69.8775 | 26.4858 | 459.6314 | 0.0059425 | 59.993 | 0.50293 | 3.0854 | 79.1117 | 2.3586 | 0.99664 | 0.7366 | 4.1883 | 4.171 | 0.34604 | 0 | 100 | 585.1 | 319 | 102.23 | 103.63 | 101.76 | 310.7 | 3 | 88.77 | 41.74 | 4 | 36.95 | 43.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.08 | 0 | 37.81 | 64 | 64 | 96.38 | 85.54 | 77.04 | 0 | 101.76 | 2.19 | 87.6 | 42.6 | 102.23 | 14.85 | 103.65 | 110 | 0 | 15803 | 78.54 | 113.49 | 214.98 | 208.94 | 214.67 | 0 | 27.51 | 49.39 | 12652 | 88.78 | 41.75 | 36.96 | 1.97 | 41.75 | 0 | 604 | 437 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.6 | 319.6 | 0 | 313.3 | 101.67 | 15803 | 15803 | 320
03/26/22 10:21:16.210 | 625.0753 | 1371.0553 | 55.7434 | 44.8286 | 10.9148 | 30.9599 | 50.8054 | 0 | 1789.8913 | 85.5748 | 76.08 | 9.4948 | 24.9543 | 69.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0231 | 460.3901 | 457.4201 | 460.8701 | 421.7501 | 449.8601 | 429.6701 | 321.0001 | 0.51354 | 1.4427 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7528179.4231 | 8500123.0529 | 8500123.0529 | 62.4243 | 62.2251 | 1.0015 | 0.99812 | 686206.8092 | 893893.7587 | 459.5601 | 0.46566 | 0 | 0 | 30.9599 | 24.9543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017951 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 619.8601 | 1367.8694 | 55.0607 | 44.2135 | 30.3663 | 1787.6771 | 69.9525 | 26.4692 | 459.6272 | 0.0059335 | 59.9933 | 0.50343 | 3.074 | 79.1934 | 2.3712 | 0.98813 | 0.7338 | 4.1902 | 4.1602 | 0.34289 | 0 | 100 | 585.3 | 319 | 102.23 | 103.65 | 101.7 | 314 | 3 | 88.78 | 41.79 | 4 | 37 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.05 | 0 | 37.82 | 64 | 64 | 96.38 | 85.54 | 77.06 | 0 | 101.7 | 2.18 | 87.59 | 42.61 | 102.23 | 14.87 | 103.65 | 110 | 0 | 15800 | 78.56 | 113.56 | 214.98 | 209.03 | 214.78 | 0 | 27.41 | 49.37 | 12657 | 88.78 | 41.79 | 37 | 1.93 | 41.79 | 0 | 604 | 441.1 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.3 | 320.3 | 0 | 314 | 101.79 | 15801 | 15800 | 319
03/26/22 10:21:21.210 | 625.0753 | 1370.2296 | 55.7442 | 44.8276 | 10.9167 | 30.8998 | 50.8066 | 0 | 1790.1906 | 85.5845 | 76.0886 | 9.4959 | 25.0472 | 69.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.023 | 460.39 | 457.42 | 460.87 | 421.75 | 449.86 | 429.67 | 321 | 0.51354 | 1.4407 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7528179.4231 | 8500123.0529 | 8500123.0529 | 62.4243 | 62.2251 | 1.0015 | 0.99812 | 686206.8092 | 893893.7587 | 459.56 | 0.46566 | 0 | 0 | 30.8998 | 25.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016242 | 0.017949 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 620.1555 | 1367.9011 | 55.0752 | 44.223 | 30.3733 | 1787.6598 | 70.027 | 26.4547 | 459.6233 | 0.005925 | 59.9936 | 0.50392 | 3.0645 | 79.2744 | 2.3644 | 0.97895 | 0.7306 | 4.1733 | 4.1494 | 0.33959 | 0 | 100 | 585.1 | 320 | 102.25 | 103.65 | 101.79 | 315 | 3 | 88.79 | 41.81 | 4 | 37.02 | 43.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.1 | 0 | 37.85 | 64 | 64 | 96.43 | 85.57 | 77.13 | 0 | 101.79 | 2.18 | 87.62 | 42.64 | 102.3 | 14.84 | 103.65 | 110 | 0 | 15797 | 78.58 | 113.61 | 215.08 | 209.13 | 214.89 | 0 | 27.38 | 49.51 | 12661 | 88.82 | 41.81 | 37.02 | 1.9 | 41.81 | 0 | 604 | 441.1 | 457.4 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585 | 321.4 | 0 | 315 | 101.74 | 15797 | 15797 | 319
03/26/22 10:21:26.209 | 622.5087 | 1363.9125 | 55.7517 | 44.8247 | 10.9269 | 30.5596 | 50.7895 | 0 | 1789.9894 | 85.6411 | 76.1396 | 9.5015 | 26.0511 | 69.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.025 | 460.44 | 457.46 | 460.9 | 421.67 | 449.65 | 429.54 | 320.92 | 0.51553 | 0.9847 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7496887.8458 | 8507721.5623 | 8507721.5623 | 62.4243 | 62.2245 | 1.0015 | 0.99812 | 682631.4424 | 893935.2836 | 459.6 | 0.46562 | 0 | 0 | 30.5596 | 26.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016245 | 0.017952 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 620.4356 | 1367.8906 | 55.0898 | 44.2326 | 30.3761 | 1787.6355 | 70.101 | 26.4494 | 459.6197 | 0.0059173 | 59.9939 | 0.50442 | 3.0523 | 79.3551 | 2.3779 | 0.96909 | 0.72701 | 4.1467 | 4.1387 | 0.33637 | 0 | 100 | 585 | 318 | 102.3 | 103.65 | 101.83 | 313 | 3 | 88.82 | 41.84 | 4 | 37.05 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.13 | 0 | 37.88 | 64 | 64 | 96.45 | 85.57 | 77.17 | 0 | 101.83 | 2.18 | 87.63 | 42.66 | 102.3 | 14.83 | 103.65 | 110 | 0 | 15794 | 78.62 | 113.68 | 215.19 | 209.23 | 215 | 0 | 27.44 | 49.77 | 12666 | 88.82 | 41.84 | 37.05 | 1.91 | 41.84 | 0 | 604 | 438.3 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585 | 319.1 | 0 | 312.8 | 101.74 | 15794 | 15794 | 317
03/26/22 10:21:31.209 | 622.2861 | 1362.7874 | 55.7571 | 44.825 | 10.932 | 31.2092 | 50.8142 | 0 | 1787.7495 | 85.6698 | 76.1653 | 9.5045 | 25.1634 | 69.1079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.025 | 460.44 | 457.46 | 460.9 | 421.67 | 449.65 | 429.54 | 320.92 | 0.51571 | 1.0655 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7494763.1181 | 8498751.6442 | 8498751.6442 | 62.4243 | 62.2242 | 1.0015 | 0.99812 | 682068.0725 | 892813.4686 | 459.6 | 0.46562 | 0 | 0 | 31.2092 | 25.1634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016243 | 0.017948 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 620.7133 | 1367.8686 | 55.1048 | 44.2425 | 30.3809 | 1787.6352 | 70.1743 | 26.4397 | 459.6161 | 0.0059095 | 59.9942 | 0.50493 | 3.0386 | 79.435 | 2.4067 | 0.95827 | 0.72281 | 4.1467 | 4.1287 | 0.33307 | 0 | 100 | 585.2 | 319 | 102.25 | 103.65 | 101.77 | 311.5 | 3 | 88.79 | 41.88 | 4 | 37.09 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.13 | 0 | 37.91 | 64 | 64 | 96.45 | 85.6 | 77.17 | 0 | 101.77 | 2.18 | 87.63 | 42.7 | 102.25 | 14.86 | 103.65 | 110 | 0 | 15791 | 78.64 | 113.75 | 215.3 | 209.23 | 215 | 0 | 27.49 | 49.86 | 12671 | 88.79 | 41.88 | 37.09 | 1.88 | 41.88 | 0 | 604 | 439.8 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.4 | 321.9 | 0 | 315.5 | 101.81 | 15789 | 15791 | 319
03/26/22 10:21:36.210 | 623.694 | 1365.8117 | 55.7634 | 44.8264 | 10.937 | 31.4393 | 50.8186 | 0 | 1788.2656 | 85.6977 | 76.1892 | 9.5085 | 24.432 | 69.1103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0261 | 460.4701 | 457.4701 | 460.8901 | 421.6401 | 449.4301 | 429.4501 | 320.8501 | 0.51444 | 1.1926 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7511931.8632 | 8504684.7262 | 8504684.7262 | 62.4243 | 62.224 | 1.0015 | 0.99812 | 683356.7627 | 893231.151 | 459.6101 | 0.46561 | 0 | 0 | 31.4393 | 24.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.01795 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 620.9894 | 1367.8473 | 55.1201 | 44.2527 | 30.3887 | 1787.6499 | 70.2467 | 26.4237 | 459.6126 | 0.005902 | 59.9945 | 0.50544 | 3.0241 | 79.514 | 2.4079 | 0.94656 | 0.71792 | 4.1442 | 4.1191 | 0.3298 | 0 | 100 | 585.4 | 320 | 102.33 | 103.65 | 101.9 | 314.3 | 3 | 88.83 | 41.93 | 4 | 37.14 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.2 | 0 | 37.98 | 64 | 64 | 96.55 | 85.63 | 77.23 | 0 | 101.9 | 2.18 | 87.67 | 42.76 | 102.38 | 14.79 | 103.65 | 110 | 0 | 15787 | 78.68 | 113.8 | 215.41 | 209.33 | 215.11 | 0 | 27.51 | 49.94 | 12676 | 88.86 | 41.93 | 37.14 | 1.84 | 41.93 | 0 | 604 | 440.6 | 457.4 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.4 | 320.7 | 0 | 314.3 | 101.81 | 15787 | 15787 | 320
03/26/22 10:21:41.209 | 625.5002 | 1368.0309 | 55.7783 | 44.8319 | 10.9464 | 30.8522 | 50.8109 | 0 | 1785.7625 | 85.7515 | 76.2351 | 9.5164 | 25.2403 | 69.0492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.02 | 460.48 | 457.42 | 460.88 | 421.59 | 449.37 | 429.17 | 320.75 | 0.51279 | 1.4934 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7533123.7748 | 8499881.9086 | 8499881.9086 | 62.4242 | 62.2235 | 1.0015 | 0.99811 | 684691.4054 | 891812.4451 | 459.5934 | 0.47288 | 0 | 0 | 30.8522 | 25.2403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016241 | 0.017954 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 621.274 | 1367.8446 | 55.1355 | 44.2631 | 30.3911 | 1787.649 | 70.3189 | 26.4135 | 459.609 | 0.0058941 | 59.9948 | 0.50595 | 3.012 | 79.5929 | 2.4075 | 0.93429 | 0.71262 | 4.1446 | 4.1092 | 0.32614 | 0 | 100 | 585.2 | 318 | 102.38 | 103.63 | 101.77 | 312 | 3 | 88.87 | 41.94 | 4 | 37.15 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.28 | 0 | 37.99 | 64 | 64 | 96.6 | 85.67 | 77.23 | 0 | 101.77 | 2.18 | 87.71 | 42.78 | 102.38 | 14.77 | 103.63 | 110 | 0 | 15784 | 78.71 | 113.85 | 215.52 | 209.42 | 215.21 | 0 | 27.41 | 49.79 | 12681 | 88.86 | 41.94 | 37.15 | 1.8 | 41.94 | 0 | 604 | 439.1 | 457.4 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.4 | 321 | 0 | 314.7 | 101.81 | 15783 | 15784 | 319
03/26/22 10:21:46.209 | 625.5276 | 1367.5768 | 55.7863 | 44.8357 | 10.9506 | 30.4106 | 50.8022 | 0 | 1786.2167 | 85.7758 | 76.256 | 9.5198 | 26.2071 | 69.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 460.4801 | 457.4201 | 460.8801 | 421.5901 | 449.3701 | 429.1701 | 320.7501 | 0.51277 | 1.4169 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7533054.9467 | 8506114.1497 | 8506114.1497 | 62.4242 | 62.2233 | 1.0015 | 0.99811 | 684463.7021 | 892036.6473 | 459.5934 | 0.47288 | 0 | 0 | 30.4106 | 26.2071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016244 | 0.017938 | 0.01348 | 0.00479 | 0.011584 | 0.0119 | 621.5504 | 1367.8431 | 55.1512 | 44.2739 | 30.3878 | 1787.6568 | 70.3905 | 26.4129 | 459.6052 | 0.0058859 | 59.995 | 0.50646 | 3.0001 | 79.6708 | 2.4076 | 0.92132 | 0.70651 | 4.1405 | 4.0997 | 0.32224 | 0 | 100 | 585.8 | 320 | 102.4 | 103.63 | 101.88 | 314.5 | 3 | 88.87 | 41.96 | 4 | 37.18 | 43.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.28 | 0 | 38.01 | 64 | 64 | 96.6 | 85.67 | 77.26 | 0 | 101.88 | 2.18 | 87.71 | 42.8 | 102.4 | 14.75 | 103.63 | 110 | 0 | 15781 | 78.75 | 113.9 | 215.52 | 209.53 | 215.32 | 0 | 27.3 | 49.73 | 12686 | 88.87 | 41.96 | 37.18 | 1.72 | 41.96 | 0 | 604 | 441.2 | 457.3 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.8 | 320.8 | 0 | 314.4 | 101.88 | 15782 | 15781 | 318
03/26/22 10:21:51.209 | 625.0208 | 1365.8479 | 55.7968 | 44.8413 | 10.9556 | 30.8208 | 50.7979 | 0 | 1791.5531 | 85.8045 | 76.2805 | 9.524 | 25.8851 | 69.0608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 460.5001 | 457.4001 | 460.8901 | 421.5701 | 449.3301 | 428.9601 | 320.6801 | 0.51307 | 1.0126 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7527299.7072 | 8534882.6114 | 8534882.6114 | 62.4242 | 62.223 | 1.0015 | 0.99811 | 683597.8791 | 894698.6214 | 459.5967 | 0.47796 | 0 | 0 | 30.8208 | 25.8851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016244 | 0.017943 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 621.8157 | 1367.829 | 55.1669 | 44.2848 | 30.3878 | 1787.6871 | 70.4617 | 26.4089 | 459.6013 | 0.0058774 | 59.9952 | 0.50699 | 2.9868 | 79.7483 | 2.4118 | 0.90785 | 0.69985 | 4.149 | 4.0901 | 0.31796 | 0 | 100 | 585.8 | 320 | 102.45 | 103.63 | 101.88 | 310.4 | 3 | 88.9 | 41.99 | 4 | 37.2 | 43.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.23 | 0 | 38.05 | 64 | 64 | 96.6 | 85.67 | 77.32 | 0 | 101.88 | 2.18 | 87.69 | 42.84 | 102.43 | 14.74 | 103.63 | 110 | 0 | 15777 | 78.77 | 113.92 | 215.63 | 209.63 | 215.43 | 0 | 27.3 | 49.96 | 12692 | 88.89 | 42 | 37.21 | 1.68 | 42 | 0 | 604 | 440.4 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.8 | 316.7 | 0 | 310.4 | 101.88 | 15779 | 15777 | 320
03/26/22 10:21:56.209 | 626.3654 | 1367.8813 | 55.814 | 44.8512 | 10.9629 | 30.9476 | 50.8062 | 0 | 1789.5971 | 85.845 | 76.3139 | 9.5311 | 25.1622 | 69.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.021 | 460.53 | 457.39 | 460.9 | 421.59 | 449.34 | 428.79 | 320.66 | 0.51194 | 1.2431 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7543587.1802 | 8531008.0502 | 8531008.0502 | 62.4241 | 62.2226 | 1.0015 | 0.99811 | 684614.751 | 893717.6061 | 459.6067 | 0.4823 | 0 | 0 | 30.9476 | 25.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01624 | 0.017944 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 622.0827 | 1367.8392 | 55.1827 | 44.296 | 30.3952 | 1787.7134 | 70.5324 | 26.3934 | 459.5974 | 0.0058689 | 59.9955 | 0.50751 | 2.9759 | 79.8252 | 2.4081 | 0.89405 | 0.69271 | 4.146 | 4.0805 | 0.31349 | 0 | 100 | 585.8 | 319 | 102.48 | 103.63 | 101.88 | 312.8 | 3 | 88.91 | 42.03 | 4 | 37.24 | 43.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.33 | 0 | 38.07 | 64 | 64 | 96.7 | 85.72 | 77.32 | 0 | 101.88 | 2.18 | 87.74 | 42.86 | 102.48 | 14.71 | 103.63 | 110 | 0 | 15774 | 78.81 | 113.99 | 215.74 | 209.73 | 215.54 | 0 | 27.48 | 50.21 | 12696 | 88.91 | 42.03 | 37.24 | 1.81 | 42.03 | 0 | 604 | 439.4 | 457.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585 | 318 | 0 | 311.7 | 101.74 | 15773 | 15774 | 317
03/26/22 10:22:01.209 | 627.8191 | 1370.5444 | 55.8257 | 44.8588 | 10.967 | 31.0031 | 50.8025 | 0 | 1788.0695 | 85.8698 | 76.3342 | 9.5355 | 25.3623 | 69.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0211 | 460.5301 | 457.3901 | 460.9001 | 421.5901 | 449.3401 | 428.7901 | 320.6601 | 0.51075 | 1.4832 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7561133.1353 | 8527842.6785 | 8527842.6785 | 62.4241 | 62.2224 | 1.0015 | 0.99811 | 685947.0237 | 892952.1508 | 459.6068 | 0.4823 | 0 | 0 | 31.0031 | 25.3623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017949 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 622.3527 | 1367.8615 | 55.1986 | 44.3072 | 30.4043 | 1787.7212 | 70.6031 | 26.3765 | 459.5935 | 0.0058605 | 59.9957 | 0.50804 | 2.967 | 79.902 | 2.4145 | 0.87989 | 0.68526 | 4.1454 | 4.0702 | 0.30891 | 0 | 100 | 585.1 | 321 | 102.5 | 103.63 | 101.76 | 314.5 | 3 | 88.93 | 42.05 | 4 | 37.26 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.38 | 0 | 38.1 | 64 | 64 | 96.67 | 85.71 | 77.34 | 0 | 101.76 | 2.18 | 87.77 | 42.88 | 102.5 | 14.7 | 103.63 | 110 | 0 | 15771 | 78.83 | 114.02 | 215.85 | 209.84 | 215.65 | 0 | 27.41 | 50.05 | 12701 | 88.93 | 42.05 | 37.26 | 1.97 | 42.05 | 0 | 604 | 441.9 | 457.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.1 | 318.8 | 0 | 312.5 | 101.76 | 15770 | 15771 | 317
03/26/22 10:22:06.209 | 628.2331 | 1371.7366 | 55.837 | 44.8723 | 10.9647 | 30.5467 | 50.8157 | 0 | 1786.7328 | 85.9064 | 76.3706 | 9.5358 | 25.6639 | 69.0851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.02 | 460.59 | 457.39 | 460.93 | 420.84 | 448.53 | 427.64 | 319.99 | 0.50935 | 1.5938 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7565722.5489 | 8522020.415 | 8522020.415 | 62.4241 | 62.2221 | 1.0015 | 0.99811 | 686543.1639 | 892280.054 | 459.6367 | 0.48879 | 0 | 0 | 30.5467 | 25.6639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017942 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 622.6107 | 1367.8655 | 55.2143 | 44.3185 | 30.408 | 1787.6882 | 70.6734 | 26.3638 | 459.5896 | 0.0058521 | 59.9959 | 0.50856 | 2.959 | 79.9783 | 2.421 | 0.86547 | 0.67753 | 4.1366 | 4.0594 | 0.30392 | 0 | 100 | 581 | 317 | 102.73 | 103.65 | 101.04 | 310.6 | 3 | 89.05 | 41.94 | 4 | 37.14 | 44.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.68 | 0 | 37.96 | 64 | 64 | 96.95 | 85.87 | 77.38 | 0 | 101.04 | 2.19 | 87.93 | 42.75 | 102.78 | 14.59 | 103.65 | 110 | 0 | 15768 | 78.86 | 114.07 | 215.96 | 209.93 | 215.65 | 0 | 27.58 | 50.48 | 12706 | 89.06 | 41.91 | 37.13 | 2.2 | 41.91 | 0 | 604 | 436.2 | 457.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581 | 316.9 | 0 | 310.6 | 101.04 | 15770 | 15768 | 317
03/26/22 10:22:11.209 | 627.4463 | 1371.143 | 55.8355 | 44.8798 | 10.9557 | 30.7741 | 50.8128 | 0 | 1791.2744 | 85.9247 | 76.3953 | 9.5294 | 25.7526 | 69.0839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 460.5901 | 457.3901 | 460.9301 | 420.8401 | 448.5301 | 427.6401 | 319.9901 | 0.50999 | 1.2835 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7556469.1726 | 8538024.2587 | 8538024.2587 | 62.4241 | 62.2219 | 1.0015 | 0.99811 | 686246.1726 | 894545.0214 | 459.6367 | 0.48879 | 0 | 0 | 30.7741 | 25.7526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017935 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 622.8652 | 1367.8902 | 55.23 | 44.3299 | 30.4082 | 1787.6971 | 70.7436 | 26.3597 | 459.5858 | 0.0058439 | 59.9961 | 0.50907 | 2.9501 | 80.0543 | 2.4317 | 0.85096 | 0.6697 | 4.1426 | 4.0485 | 0.29892 | 0 | 100 | 579.9 | 318 | 102.98 | 103.72 | 100.85 | 310.2 | 3 | 89.19 | 41.76 | 4 | 36.99 | 44.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 100.92 | 0 | 37.8 | 64 | 64 | 97.15 | 85.98 | 77.45 | 0 | 100.85 | 2.2 | 88.07 | 42.59 | 102.98 | 14.54 | 103.72 | 110 | 0 | 15768 | 78.9 | 114.09 | 215.96 | 210.03 | 215.76 | 0 | 27.92 | 50.49 | 12711 | 89.19 | 41.76 | 36.98 | 2.32 | 41.76 | 0 | 604 | 435.4 | 457.6 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.9 | 317.3 | 0 | 311 | 100.85 | 15768 | 15768 | 319
03/26/22 10:22:16.208 | 624.4608 | 1367.4271 | 55.823 | 44.8898 | 10.9332 | 31.8043 | 50.8029 | 0 | 1790.5003 | 85.9488 | 76.4367 | 9.5122 | 24.6696 | 69.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0191 | 460.6201 | 457.3901 | 460.9601 | 420.3001 | 447.9801 | 426.9001 | 319.5401 | 0.51171 | 1.1171 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7521475.6687 | 8517640.5997 | 8517640.5997 | 62.4241 | 62.2216 | 1.0015 | 0.99811 | 684387.0036 | 894153.2226 | 459.6568 | 0.49312 | 0 | 0 | 31.8043 | 24.6696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017948 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.0976 | 1367.8905 | 55.2454 | 44.3412 | 30.4133 | 1787.73 | 70.8137 | 26.3513 | 459.5821 | 0.0058358 | 59.9963 | 0.50957 | 2.9385 | 80.13 | 2.4316 | 0.83625 | 0.66181 | 4.1412 | 4.0372 | 0.29377 | 0 | 100 | 579.6 | 317 | 103.08 | 103.77 | 100.8 | 307.9 | 3 | 89.24 | 41.71 | 4 | 36.93 | 44.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.1 | 0 | 37.74 | 64 | 64 | 97.38 | 86.1 | 77.6 | 0 | 100.8 | 2.21 | 88.17 | 42.53 | 103.1 | 14.52 | 103.77 | 110 | 0 | 15768 | 78.92 | 114.09 | 216.07 | 210.13 | 215.76 | 0 | 27.83 | 50.09 | 12716 | 89.25 | 41.71 | 36.93 | 2.37 | 41.71 | 0 | 604 | 435.5 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 317.1 | 0 | 310.8 | 100.82 | 15765 | 15768 | 318
03/26/22 10:22:21.209 | 623.1474 | 1371.174 | 55.7761 | 44.9033 | 10.8728 | 31.2446 | 50.8117 | 0 | 1785.2464 | 85.9981 | 76.533 | 9.4652 | 24.9717 | 69.0942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.022 | 460.7 | 457.48 | 461.04 | 419.24 | 446.85 | 425.74 | 318.74 | 0.5115 | 1.5821 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7505421.3908 | 8459505.3115 | 8459505.3115 | 62.4241 | 62.221 | 1.0015 | 0.99811 | 686044.5603 | 891599.5376 | 459.74 | 0.49158 | 0 | 0 | 31.2446 | 24.9717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017946 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.3231 | 1367.9179 | 55.2604 | 44.3524 | 30.4159 | 1787.7445 | 70.8839 | 26.344 | 459.5786 | 0.0058283 | 59.9964 | 0.51008 | 2.9296 | 80.2056 | 2.4357 | 0.82127 | 0.65391 | 4.1284 | 4.0258 | 0.28856 | 0 | 100 | 580.1 | 319 | 103.38 | 103.8 | 100.97 | 308.5 | 3 | 89.39 | 41.72 | 4 | 36.94 | 44.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.38 | 0 | 37.75 | 64 | 64 | 97.65 | 86.26 | 77.78 | 0 | 100.97 | 2.21 | 88.32 | 42.54 | 103.38 | 14.4 | 103.8 | 110 | 0 | 15768 | 78.96 | 114.07 | 216.18 | 210.13 | 215.87 | 0 | 27.69 | 49.9 | 12722 | 89.4 | 41.71 | 36.93 | 2.31 | 41.71 | 0 | 604 | 434.7 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 314.8 | 0 | 308.5 | 100.89 | 15767 | 15768 | 319
03/26/22 10:22:26.208 | 620.1366 | 1370.5186 | 55.7368 | 44.9039 | 10.8329 | 31.0966 | 50.8239 | 0 | 1784.56 | 86.0315 | 76.5983 | 9.4332 | 25.043 | 69.0835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.022 | 460.7 | 457.48 | 461.04 | 419.24 | 446.85 | 425.74 | 318.74 | 0.51398 | 1.6166 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7469024.3858 | 8419391.0266 | 8419391.0266 | 62.4242 | 62.2204 | 1.0015 | 0.9981 | 685938.4887 | 891166.4292 | 459.74 | 0.49158 | 0 | 0 | 31.0966 | 25.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017952 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.5366 | 1367.9617 | 55.275 | 44.3636 | 30.4207 | 1787.7667 | 70.9543 | 26.3333 | 459.5752 | 0.0058209 | 59.9966 | 0.51058 | 2.9215 | 80.2811 | 2.4109 | 0.8061 | 0.64603 | 4.1002 | 4.0143 | 0.28292 | 0 | 100 | 579.6 | 320 | 103.45 | 103.82 | 100.82 | 310.6 | 3 | 89.44 | 41.7 | 4 | 36.91 | 43.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.5 | 0 | 37.71 | 64 | 64 | 97.83 | 86.36 | 77.91 | 0 | 100.82 | 2.22 | 88.38 | 42.5 | 103.45 | 14.39 | 103.85 | 110 | 0 | 15768 | 78.98 | 114.07 | 216.18 | 210.23 | 215.98 | 0 | 27.72 | 49.9 | 12727 | 89.45 | 41.7 | 36.91 | 2.08 | 41.7 | 0 | 604 | 434.5 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.9 | 316.7 | 0 | 310.4 | 100.85 | 15768 | 15768 | 318
03/26/22 10:22:31.209 | 618.1584 | 1369.8838 | 55.7039 | 44.9006 | 10.8033 | 31.3008 | 50.8237 | 0 | 1782.2633 | 86.0582 | 76.6486 | 9.4096 | 24.8489 | 69.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.022 | 460.7 | 457.48 | 461.04 | 419.24 | 446.85 | 425.74 | 318.74 | 0.51563 | 1.7227 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7445453.7596 | 8387299.6817 | 8387299.6817 | 62.4242 | 62.22 | 1.0015 | 0.9981 | 685622.3747 | 890013.2212 | 459.74 | 0.49158 | 0 | 0 | 31.3008 | 24.8489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017954 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.7358 | 1368 | 55.2893 | 44.3746 | 30.4269 | 1787.7732 | 71.0248 | 26.3219 | 459.5718 | 0.0058135 | 59.9968 | 0.5111 | 2.9142 | 80.3564 | 2.3861 | 0.79056 | 0.63802 | 4.0905 | 4.0021 | 0.27713 | 0 | 100 | 579.7 | 318 | 103.6 | 103.87 | 100.82 | 308.4 | 3 | 89.51 | 41.69 | 4 | 36.9 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.65 | 0 | 37.71 | 64 | 64 | 97.98 | 86.43 | 78.06 | 0 | 100.82 | 2.22 | 88.47 | 42.5 | 103.63 | 14.33 | 103.87 | 110 | 0 | 15768 | 79.01 | 114.07 | 216.3 | 210.23 | 215.98 | 0 | 27.74 | 49.94 | 12732 | 89.54 | 41.69 | 36.9 | 1.98 | 41.69 | 0 | 604 | 436.6 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 315.5 | 0 | 309.2 | 100.87 | 15767 | 15768 | 315
03/26/22 10:22:36.208 | 613.9147 | 1368.9135 | 55.6188 | 44.8823 | 10.7365 | 30.3811 | 50.8113 | 0 | 1786.2218 | 86.1264 | 76.7697 | 9.3567 | 26.3846 | 69.1054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.023 | 460.71 | 457.54 | 461.09 | 417.75 | 445.45 | 424.34 | 317.67 | 0.51745 | 1.4048 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7393700.6931 | 8360385.2047 | 8360385.2047 | 62.4244 | 62.2191 | 1.0015 | 0.9981 | 685140.9063 | 891974.7103 | 459.78 | 0.48719 | 0 | 0 | 30.3811 | 26.3846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017941 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.8963 | 1368.0087 | 55.3028 | 44.3854 | 30.4272 | 1787.7897 | 71.0955 | 26.3188 | 459.5686 | 0.0058068 | 59.997 | 0.5116 | 2.9038 | 80.4317 | 2.3866 | 0.775 | 0.63008 | 4.0781 | 3.9904 | 0.27153 | 0 | 100 | 580.4 | 318 | 103.63 | 103.89 | 101.01 | 308.7 | 3 | 89.54 | 41.7 | 4 | 36.91 | 43.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.7 | 0 | 37.74 | 64 | 64 | 97.98 | 86.44 | 78.21 | 0 | 101.01 | 2.22 | 88.49 | 42.53 | 103.63 | 14.36 | 103.89 | 110 | 0 | 15768 | 79.03 | 114.07 | 216.3 | 210.33 | 215.98 | 0 | 27.78 | 49.95 | 12736 | 89.54 | 41.71 | 36.93 | 1.86 | 41.71 | 0 | 604 | 437.9 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.8 | 315 | 0 | 308.7 | 101.01 | 15767 | 15768 | 320
03/26/22 10:22:41.209 | 611.1382 | 1369.3367 | 55.5413 | 44.8569 | 10.6845 | 30.1013 | 50.8239 | 0 | 1791.8525 | 86.1881 | 76.8723 | 9.3158 | 26.9501 | 69.0847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0251 | 460.7101 | 457.5501 | 461.1201 | 417.5301 | 445.3401 | 424.1701 | 317.5401 | 0.51959 | 1.1062 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7360145.3958 | 8350748.1875 | 8350748.1875 | 62.4246 | 62.2183 | 1.0015 | 0.9981 | 685356.4747 | 894773.4329 | 459.7934 | 0.4879 | 0 | 0 | 30.1013 | 26.9501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017935 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.0336 | 1368.0067 | 55.3157 | 44.3959 | 30.427 | 1787.8283 | 71.1667 | 26.3167 | 459.5657 | 0.0058003 | 59.9972 | 0.5121 | 2.891 | 80.507 | 2.3853 | 0.75918 | 0.62199 | 4.0836 | 3.9785 | 0.26606 | 0 | 100 | 581 | 319 | 103.68 | 103.89 | 101.04 | 310.7 | 3 | 89.55 | 41.72 | 4 | 36.94 | 43.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.67 | 0 | 37.75 | 64 | 64 | 97.98 | 86.44 | 78.32 | 0 | 101.04 | 2.22 | 88.48 | 42.54 | 103.68 | 14.33 | 103.89 | 110 | 0 | 15768 | 79.07 | 114.07 | 216.41 | 210.43 | 216.11 | 0 | 27.67 | 49.7 | 12741 | 89.56 | 41.74 | 36.95 | 1.69 | 41.74 | 0 | 604 | 435.1 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.9 | 314.8 | 0 | 308.5 | 101.03 | 15767 | 15768 | 316
03/26/22 10:22:46.208 | 608.1017 | 1368.5367 | 55.448 | 44.82 | 10.6279 | 29.8843 | 50.8159 | 0 | 1794.0459 | 86.2631 | 76.991 | 9.2722 | 26.9616 | 69.1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.026 | 460.73 | 457.58 | 461.14 | 417.61 | 445.54 | 424.31 | 317.66 | 0.52238 | 0.94535 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7323489.8282 | 8327879.6081 | 8327879.6081 | 62.4247 | 62.2175 | 1.0015 | 0.99809 | 684918.422 | 895761.0784 | 459.8167 | 0.48643 | 0 | 0 | 29.8843 | 26.9616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.01793 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.1485 | 1368.0029 | 55.328 | 44.406 | 30.4314 | 1787.8558 | 71.2379 | 26.3057 | 459.5629 | 0.0057943 | 59.9974 | 0.51259 | 2.8787 | 80.5822 | 2.384 | 0.74348 | 0.61393 | 4.1075 | 3.9669 | 0.26099 | 0 | 100 | 581.8 | 320 | 103.65 | 103.87 | 101.18 | 310.7 | 3 | 89.55 | 41.74 | 4 | 36.95 | 43.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.7 | 0 | 37.76 | 64 | 64 | 97.95 | 86.43 | 78.45 | 0 | 101.18 | 2.22 | 88.49 | 42.55 | 103.65 | 14.33 | 103.87 | 110 | 0 | 15768 | 79.09 | 114.11 | 216.52 | 210.54 | 216.23 | 0 | 27.57 | 49.67 | 12746 | 89.54 | 41.75 | 36.96 | 1.64 | 41.75 | 0 | 604 | 434 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.8 | 318.6 | 0 | 312.3 | 101.18 | 15767 | 15768 | 318
03/26/22 10:22:51.208 | 605.9629 | 1368.4232 | 55.398 | 44.7973 | 10.6007 | 30.1304 | 50.8138 | 0 | 1795.7542 | 86.304 | 77.0524 | 9.2516 | 26.3824 | 69.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0261 | 460.7301 | 457.5801 | 461.1401 | 417.6101 | 445.5401 | 424.3101 | 317.6601 | 0.52422 | 0.85605 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7298049.5477 | 8310501.7134 | 8310501.7134 | 62.4249 | 62.2169 | 1.0015 | 0.99809 | 684906.184 | 896698.8079 | 459.8167 | 0.48643 | 0 | 0 | 30.1304 | 26.3824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017925 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.2492 | 1368.0047 | 55.3396 | 44.4159 | 30.4327 | 1787.885 | 71.3093 | 26.296 | 459.5602 | 0.0057886 | 59.9977 | 0.51308 | 2.867 | 80.6572 | 2.3842 | 0.72786 | 0.60581 | 4.1448 | 3.9552 | 0.25585 | 0 | 100 | 582.2 | 320 | 103.7 | 103.87 | 101.25 | 309.8 | 3 | 89.56 | 41.76 | 4 | 36.98 | 43.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.7 | 0 | 37.78 | 64 | 64 | 98 | 86.47 | 78.49 | 0 | 101.25 | 2.22 | 88.49 | 42.56 | 103.68 | 14.28 | 103.85 | 110 | 0 | 15767 | 79.11 | 114.16 | 216.52 | 210.54 | 216.34 | 0 | 27.6 | 49.81 | 12751 | 89.56 | 41.76 | 36.98 | 1.55 | 41.76 | 0 | 604 | 438 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.1 | 317.2 | 0 | 310.9 | 101.23 | 15767 | 15767 | 319
03/26/22 10:22:56.208 | 604.1939 | 1371.6591 | 55.274 | 44.7326 | 10.5414 | 31.5832 | 50.8132 | 0 | 1794.0924 | 86.4101 | 77.2025 | 9.2076 | 24.2766 | 69.1326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.03 | 460.74 | 457.59 | 461.16 | 417.74 | 445.79 | 424.56 | 317.83 | 0.52604 | 1.1524 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7278088.7347 | 8266747.176 | 8266747.176 | 62.4252 | 62.2157 | 1.0015 | 0.99809 | 686505.4954 | 896237.7322 | 459.83 | 0.48714 | 0 | 0 | 31.5832 | 24.2766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017925 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.3352 | 1368.0274 | 55.3503 | 44.4253 | 30.4412 | 1787.903 | 71.3811 | 26.2774 | 459.5577 | 0.005783 | 59.9979 | 0.51357 | 2.857 | 80.7323 | 2.3995 | 0.7124 | 0.5975 | 4.1648 | 3.9441 | 0.25076 | 0 | 100 | 582.3 | 319 | 103.77 | 103.82 | 101.27 | 311.8 | 3 | 89.6 | 41.77 | 4 | 36.99 | 43.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.77 | 0 | 37.79 | 64 | 64 | 98.02 | 86.47 | 78.58 | 0 | 101.27 | 2.22 | 88.53 | 42.58 | 103.85 | 14.18 | 103.82 | 110 | 0 | 15766 | 79.15 | 114.21 | 216.52 | 210.54 | 216.34 | 0 | 27.77 | 50.16 | 12756 | 89.63 | 41.77 | 36.99 | 1.54 | 41.77 | 0 | 604 | 437.3 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.2 | 317.4 | 0 | 311.1 | 101.25 | 15766 | 15766 | 318
03/26/22 10:23:01.208 | 601.417 | 1369.5741 | 55.1812 | 44.6694 | 10.5118 | 32.2553 | 50.8276 | 0 | 1785.6902 | 86.5016 | 77.3128 | 9.1888 | 23.8178 | 69.1665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0301 | 460.7401 | 457.5901 | 461.1601 | 417.7401 | 445.7901 | 424.5601 | 317.8301 | 0.52847 | 1.5135 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7245391.4031 | 8204745.1031 | 8204745.1031 | 62.4254 | 62.2146 | 1.0016 | 0.99808 | 685492.5726 | 891640.2721 | 459.8301 | 0.48714 | 0 | 0 | 32.2553 | 23.8178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017949 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.3994 | 1368.0307 | 55.3603 | 44.4342 | 30.451 | 1787.8782 | 71.4532 | 26.2601 | 459.5551 | 0.0057775 | 59.9982 | 0.51408 | 2.8486 | 80.8075 | 2.4012 | 0.69702 | 0.58897 | 4.1647 | 3.9331 | 0.24555 | 0 | 100 | 582.9 | 316 | 103.95 | 103.82 | 101.37 | 310.4 | 3 | 89.71 | 41.8 | 4 | 37.01 | 43.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.88 | 0 | 37.8 | 64 | 64 | 98.18 | 86.54 | 78.66 | 0 | 101.37 | 2.22 | 88.59 | 42.59 | 103.98 | 14.11 | 103.82 | 110 | 0 | 15765 | 79.18 | 114.26 | 216.63 | 210.64 | 216.34 | 0 | 28.14 | 50.75 | 12761 | 89.72 | 41.8 | 37.01 | 1.57 | 41.8 | 0 | 604 | 437 | 457.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.9 | 316.6 | 0 | 310.4 | 101.37 | 15766 | 15765 | 316
03/26/22 10:23:06.208 | 601.8926 | 1372.4178 | 55.091 | 44.5929 | 10.4981 | 30.5222 | 50.8223 | 0 | 1779.9254 | 86.6022 | 77.419 | 9.1832 | 25.9786 | 69.1971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.034 | 460.68 | 457.48 | 461.13 | 418.37 | 446.7 | 425.17 | 318.33 | 0.52888 | 1.9321 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7249629.2784 | 8175628.8777 | 8175628.8777 | 62.4257 | 62.2136 | 1.0016 | 0.99808 | 686920.1934 | 888748.222 | 459.7633 | 0.49663 | 0 | 0 | 30.5222 | 25.9786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017943 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.4593 | 1368.0449 | 55.3698 | 44.4427 | 30.4506 | 1787.8219 | 71.5257 | 26.2549 | 459.5526 | 0.0057722 | 59.9985 | 0.51455 | 2.8422 | 80.8831 | 2.4187 | 0.68156 | 0.58014 | 4.2004 | 3.9218 | 0.24085 | 0 | 100 | 582.8 | 320 | 104.03 | 103.82 | 101.36 | 312.4 | 3 | 89.75 | 41.81 | 4 | 37.02 | 43.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.98 | 0 | 37.82 | 64 | 64 | 98.28 | 86.61 | 78.73 | 0 | 101.36 | 2.22 | 88.64 | 42.61 | 104.03 | 14.07 | 103.82 | 110 | 0 | 15764 | 79.22 | 114.33 | 216.74 | 210.74 | 216.45 | 0 | 28.53 | 51.08 | 12766 | 89.75 | 41.82 | 37.04 | 1.68 | 41.82 | 0 | 604 | 435.1 | 457.6 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.8 | 317.9 | 0 | 311.6 | 101.36 | 15763 | 15764 | 317
03/26/22 10:23:11.208 | 601.2171 | 1370.085 | 55.0372 | 44.5401 | 10.4971 | 30.1207 | 50.8243 | 0 | 1787.1508 | 86.6677 | 77.4816 | 9.1861 | 26.3383 | 69.1685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0341 | 460.6801 | 457.4801 | 461.1301 | 418.3701 | 446.7001 | 425.1701 | 318.3301 | 0.52948 | 1.505 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7241146.2625 | 8202941.2698 | 8202941.2698 | 62.4258 | 62.2131 | 1.0016 | 0.99808 | 686216.9136 | 891496.9297 | 459.7634 | 0.49663 | 0 | 0 | 30.1207 | 26.3383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.01793 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.5062 | 1368.0524 | 55.3786 | 44.4507 | 30.4491 | 1787.8053 | 71.5981 | 26.2489 | 459.5502 | 0.0057669 | 59.9988 | 0.51501 | 2.8326 | 80.9583 | 2.423 | 0.66677 | 0.57128 | 4.1972 | 3.9108 | 0.2364 | 0 | 100 | 583.2 | 317 | 103.95 | 103.82 | 101.43 | 312.3 | 3 | 89.71 | 41.84 | 4 | 37.05 | 43.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.95 | 0 | 37.85 | 64 | 64 | 98.2 | 86.56 | 78.77 | 0 | 101.43 | 2.22 | 88.63 | 42.64 | 103.95 | 14.11 | 103.82 | 110 | 0 | 15762 | 79.24 | 114.33 | 216.74 | 210.74 | 216.45 | 0 | 28.56 | 50.74 | 12771 | 89.71 | 41.84 | 37.05 | 1.71 | 41.84 | 0 | 604 | 435.4 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.2 | 317.5 | 0 | 311.2 | 101.43 | 15763 | 15762 | 318
03/26/22 10:23:16.208 | 601.6397 | 1370.9882 | 54.9555 | 44.4513 | 10.5042 | 30.8205 | 50.8233 | 0 | 1794.1646 | 86.7778 | 77.5777 | 9.2001 | 25.3035 | 69.1607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0361 | 460.6501 | 457.4301 | 461.1401 | 418.6501 | 447.2401 | 425.4501 | 318.6101 | 0.52957 | 0.94512 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7246828.9677 | 8255135.8384 | 8255135.8384 | 62.4261 | 62.212 | 1.0016 | 0.99807 | 686211.0494 | 895837.6606 | 459.7401 | 0.50246 | 0 | 0 | 30.8205 | 25.3035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01621 | 0.017923 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.5332 | 1368.0418 | 55.387 | 44.4585 | 30.4552 | 1787.7981 | 71.6702 | 26.233 | 459.5478 | 0.0057616 | 59.9991 | 0.51548 | 2.8204 | 81.0331 | 2.4171 | 0.65238 | 0.56235 | 4.1913 | 3.8996 | 0.23198 | 0 | 100 | 583.5 | 319 | 103.98 | 103.8 | 101.48 | 309.5 | 3 | 89.72 | 41.86 | 4 | 37.08 | 43.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 101.98 | 0 | 37.86 | 64 | 64 | 98.2 | 86.56 | 78.81 | 0 | 101.48 | 2.22 | 88.63 | 42.65 | 103.95 | 14.09 | 103.8 | 110 | 0 | 15761 | 79.28 | 114.33 | 216.85 | 210.84 | 216.56 | 0 | 28.41 | 50.3 | 12776 | 89.71 | 41.86 | 37.08 | 1.64 | 41.86 | 0 | 604 | 432.4 | 457.6 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.4 | 317.8 | 0 | 311.5 | 101.46 | 15761 | 15761 | 319
03/26/22 10:23:21.208 | 602.9391 | 1372.903 | 54.9163 | 44.4042 | 10.5121 | 30.7404 | 50.8347 | 0 | 1791.5222 | 86.8361 | 77.6246 | 9.2115 | 25.4266 | 69.1545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.034 | 460.64 | 457.39 | 461.15 | 418.74 | 447.47 | 425.44 | 318.69 | 0.52856 | 1.1605 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7262388.7575 | 8253197.366 | 8253197.366 | 62.4262 | 62.2115 | 1.0016 | 0.99807 | 687171.2719 | 894512.2272 | 459.7267 | 0.50827 | 0 | 0 | 30.7404 | 25.4266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016211 | 0.017926 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.5695 | 1368.0579 | 55.3948 | 44.4658 | 30.4614 | 1787.7843 | 71.7425 | 26.2178 | 459.5453 | 0.0057563 | 59.9994 | 0.51592 | 2.8093 | 81.1081 | 2.4397 | 0.63831 | 0.55328 | 4.1683 | 3.8882 | 0.22751 | 0 | 100 | 583.2 | 317 | 104.08 | 103.8 | 101.43 | 310 | 3 | 89.78 | 41.88 | 4 | 37.09 | 43.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.03 | 0 | 37.89 | 64 | 64 | 98.28 | 86.61 | 78.9 | 0 | 101.43 | 2.22 | 88.67 | 42.68 | 104.05 | 14.03 | 103.8 | 110 | 0 | 15758 | 79.33 | 114.33 | 216.85 | 210.95 | 216.68 | 0 | 28.19 | 49.92 | 12781 | 89.76 | 41.88 | 37.09 | 1.63 | 41.88 | 0 | 604 | 436.2 | 457.6 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.5 | 317.5 | 0 | 311.2 | 101.48 | 15758 | 15758 | 317
03/26/22 10:23:26.207 | 602.3669 | 1370.6012 | 54.8876 | 44.368 | 10.5197 | 31.079 | 50.8448 | 0 | 1790.4693 | 86.8804 | 77.6588 | 9.2216 | 24.9281 | 69.1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.034 | 460.64 | 457.39 | 461.15 | 418.74 | 447.47 | 425.44 | 318.69 | 0.52906 | 1.0413 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7255774.6678 | 8256765.6148 | 8256765.6148 | 62.4263 | 62.2111 | 1.0016 | 0.99807 | 686020.4993 | 893982.1386 | 459.7267 | 0.50827 | 0 | 0 | 31.079 | 24.9281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017932 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6012 | 1368.0654 | 55.4022 | 44.4727 | 30.4676 | 1787.7593 | 71.8149 | 26.2027 | 459.5428 | 0.005751 | 59.9997 | 0.51635 | 2.7982 | 81.1832 | 2.4455 | 0.62431 | 0.54408 | 4.1384 | 3.8762 | 0.22311 | 0 | 100 | 583.4 | 317 | 104.05 | 103.8 | 101.46 | 310.1 | 3 | 89.75 | 41.9 | 4 | 37.11 | 43.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102 | 0 | 37.9 | 64 | 64 | 98.33 | 86.62 | 78.98 | 0 | 101.46 | 2.22 | 88.66 | 42.69 | 104.03 | 14.05 | 103.8 | 110 | 0 | 15757 | 79.37 | 114.33 | 216.97 | 210.95 | 216.68 | 0 | 28.14 | 50.01 | 12786 | 89.75 | 41.9 | 37.11 | 1.57 | 41.9 | 0 | 604 | 435.8 | 457.6 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.4 | 319 | 0 | 312.7 | 101.46 | 15757 | 15757 | 315
03/26/22 10:23:31.207 | 600.5623 | 1364.0364 | 54.8337 | 44.296 | 10.5376 | 31.1829 | 50.846 | 0 | 1784.3278 | 86.9674 | 77.7231 | 9.2443 | 24.2861 | 69.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.034 | 460.6 | 457.3 | 461.15 | 418.97 | 447.89 | 425.42 | 318.82 | 0.53087 | 0.9091 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7234036.3161 | 8246143.1713 | 8246143.1713 | 62.4265 | 62.2104 | 1.0016 | 0.99807 | 682920.3236 | 890944.2631 | 459.6834 | 0.51847 | 0 | 0 | 31.1829 | 24.2861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017933 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6165 | 1368.0536 | 55.4091 | 44.4792 | 30.4726 | 1787.7079 | 71.887 | 26.1874 | 459.5402 | 0.0057452 | 60 | 0.5168 | 2.7868 | 81.2581 | 2.4581 | 0.61112 | 0.53499 | 4.1223 | 3.8645 | 0.21842 | 0 | 100 | 583.4 | 317 | 104.03 | 103.77 | 101.46 | 309.8 | 3 | 89.75 | 41.9 | 4 | 37.11 | 43.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102 | 0 | 37.91 | 64 | 64 | 98.28 | 86.61 | 78.98 | 0 | 101.46 | 2.22 | 88.66 | 42.7 | 104.03 | 14.02 | 103.77 | 110 | 0 | 15755 | 79.41 | 114.33 | 216.97 | 210.95 | 216.79 | 0 | 28.39 | 50.48 | 12791 | 89.75 | 41.9 | 37.11 | 1.53 | 41.9 | 0 | 604 | 437.7 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.6 | 318.4 | 0 | 312.1 | 101.5 | 15753 | 15755 | 319
03/26/22 10:23:36.208 | 602.3812 | 1366.1214 | 54.7964 | 44.2423 | 10.5541 | 31.1982 | 50.8306 | 0 | 1786.0825 | 87.0327 | 77.7695 | 9.2632 | 24.3186 | 69.1987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.032 | 460.59 | 457.27 | 461.15 | 419.06 | 448.04 | 425.43 | 318.88 | 0.52937 | 0.85628 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7255961.775 | 8272678.1616 | 8272678.1616 | 62.4267 | 62.2098 | 1.0016 | 0.99807 | 683782.5086 | 891777.5191 | 459.67 | 0.52211 | 0 | 0 | 31.1982 | 24.3186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017932 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6259 | 1368.0414 | 55.4155 | 44.4854 | 30.4797 | 1787.6814 | 71.959 | 26.1709 | 459.5377 | 0.0057399 | 60.0002 | 0.51721 | 2.7735 | 81.3326 | 2.467 | 0.59835 | 0.52591 | 4.1136 | 3.8523 | 0.21428 | 0 | 100 | 584.3 | 318 | 104.13 | 103.77 | 101.62 | 313.5 | 3 | 89.8 | 41.95 | 4 | 37.16 | 43.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.08 | 0 | 37.96 | 64 | 64 | 98.33 | 86.63 | 79.05 | 0 | 101.62 | 2.22 | 88.7 | 42.75 | 104.1 | 13.98 | 103.77 | 110 | 0 | 15753 | 79.43 | 114.35 | 217.08 | 211.05 | 216.79 | 0 | 28.68 | 50.84 | 12796 | 89.79 | 41.95 | 37.16 | 1.42 | 41.95 | 0 | 604 | 437.3 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.6 | 317.6 | 0 | 311.2 | 101.67 | 15753 | 15753 | 317
03/26/22 10:23:41.209 | 603.4755 | 1366.6839 | 54.7686 | 44.1998 | 10.5688 | 31.3011 | 50.8396 | 0 | 1781.9434 | 87.0854 | 77.806 | 9.2793 | 24.3714 | 69.1842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.033 | 460.58 | 457.27 | 461.15 | 419.12 | 448.11 | 425.47 | 318.93 | 0.52849 | 1.0778 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7269195.2711 | 8267832.5289 | 8267832.5289 | 62.4268 | 62.2094 | 1.0017 | 0.99806 | 684065.3703 | 889706.1787 | 459.6667 | 0.52139 | 0 | 0 | 31.3011 | 24.3714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017938 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6445 | 1368.0393 | 55.4217 | 44.4912 | 30.4846 | 1787.6438 | 72.0312 | 26.1581 | 459.5352 | 0.0057345 | 60.0005 | 0.5176 | 2.7607 | 81.4075 | 2.468 | 0.58573 | 0.51685 | 4.1345 | 3.8394 | 0.21003 | 0 | 100 | 584.4 | 319 | 104.03 | 103.75 | 101.57 | 310.9 | 3 | 89.76 | 41.98 | 4 | 37.19 | 43.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.05 | 0 | 37.99 | 64 | 64 | 98.33 | 86.63 | 79.11 | 0 | 101.57 | 2.22 | 88.68 | 42.78 | 104.03 | 13.98 | 103.75 | 110 | 0 | 15750 | 79.45 | 114.4 | 217.08 | 211.15 | 216.79 | 0 | 28.86 | 50.89 | 12801 | 89.76 | 41.98 | 37.19 | 1.32 | 41.98 | 0 | 604 | 438.4 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.4 | 316.1 | 0 | 309.8 | 101.63 | 15752 | 15750 | 316
03/26/22 10:23:46.208 | 603.8055 | 1365.9614 | 54.7491 | 44.1674 | 10.5817 | 31.0273 | 50.8487 | 0 | 1782.3149 | 87.1274 | 77.8348 | 9.2926 | 25.062 | 69.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0341 | 460.5801 | 457.2801 | 461.1501 | 419.1501 | 448.1401 | 425.4901 | 318.9601 | 0.52825 | 0.97223 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7273050.0302 | 8280386.1718 | 8280386.1718 | 62.4268 | 62.2091 | 1.0017 | 0.99806 | 683792.272 | 890009.9249 | 459.6701 | 0.51994 | 0 | 0 | 31.0273 | 25.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017941 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6445 | 1368.0173 | 55.4274 | 44.4967 | 30.4892 | 1787.6294 | 72.1028 | 26.1458 | 459.5328 | 0.0057293 | 60.0008 | 0.518 | 2.7449 | 81.4816 | 2.4672 | 0.57402 | 0.50802 | 4.1478 | 3.8265 | 0.20593 | 0 | 100 | 584.2 | 318 | 104.08 | 103.7 | 101.6 | 313.2 | 3 | 89.78 | 41.99 | 4 | 37.2 | 43.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.08 | 0 | 38.01 | 64 | 64 | 98.35 | 86.65 | 79.11 | 0 | 101.6 | 2.22 | 88.7 | 42.8 | 104.1 | 13.92 | 103.7 | 110 | 0 | 15748 | 79.48 | 114.4 | 217.19 | 211.15 | 216.9 | 0 | 28.87 | 50.66 | 12806 | 89.78 | 41.99 | 37.2 | 1.24 | 41.99 | 0 | 604 | 434.7 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.2 | 319.5 | 0 | 313.2 | 101.6 | 15747 | 15748 | 318
03/26/22 10:23:51.207 | 604.2283 | 1365.8633 | 54.7406 | 44.1523 | 10.5882 | 30.2007 | 50.8491 | 0 | 1786.707 | 87.1476 | 77.8486 | 9.2991 | 26.1181 | 69.1686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.034 | 460.58 | 457.28 | 461.15 | 419.15 | 448.14 | 425.49 | 318.96 | 0.52788 | 0.67333 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7277247.1438 | 8309444.8937 | 8309444.8937 | 62.4269 | 62.2088 | 1.0017 | 0.99806 | 683655.9375 | 892079.1004 | 459.67 | 0.51994 | 0 | 0 | 30.2007 | 26.1181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017923 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6351 | 1367.9757 | 55.4329 | 44.5021 | 30.4924 | 1787.6551 | 72.1744 | 26.1341 | 459.5305 | 0.0057243 | 60.001 | 0.51838 | 2.7252 | 81.5557 | 2.4397 | 0.56242 | 0.49917 | 4.1274 | 3.8127 | 0.20197 | 0 | 100 | 584.7 | 317 | 104.05 | 103.7 | 101.69 | 310.5 | 3 | 89.78 | 42.03 | 4 | 37.24 | 43.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.08 | 0 | 38.04 | 64 | 64 | 98.33 | 86.63 | 79.15 | 0 | 101.69 | 2.21 | 88.7 | 42.83 | 104.03 | 13.91 | 103.68 | 110 | 0 | 15745 | 79.5 | 114.4 | 217.31 | 211.25 | 216.9 | 0 | 28.85 | 50.54 | 12811 | 89.76 | 42.03 | 37.24 | 1.17 | 42.03 | 0 | 604 | 438.4 | 457.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.8 | 317 | 0 | 310.7 | 101.7 | 15747 | 15745 | 317
03/26/22 10:23:56.207 | 606.3731 | 1368.7741 | 54.7203 | 44.1115 | 10.6089 | 30.728 | 50.8487 | 0 | 1792.0847 | 87.2053 | 77.8871 | 9.3181 | 25.3809 | 69.2392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0341 | 460.5901 | 457.2901 | 461.1501 | 419.2101 | 448.1501 | 425.4901 | 318.9901 | 0.52606 | 0.48363 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7303378.4315 | 8351330.0357 | 8351330.0357 | 62.4269 | 62.2084 | 1.0017 | 0.99806 | 684896.7458 | 895022.4987 | 459.6768 | 0.51921 | 0 | 0 | 30.728 | 25.3809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017925 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6282 | 1367.951 | 55.4381 | 44.5071 | 30.4977 | 1787.66 | 72.2457 | 26.1229 | 459.5285 | 0.0057198 | 60.0013 | 0.51874 | 2.7074 | 81.6295 | 2.4086 | 0.55156 | 0.49061 | 4.1323 | 3.7987 | 0.19859 | 0 | 100 | 584.5 | 316 | 103.95 | 103.65 | 101.65 | 308.3 | 3 | 89.71 | 42.05 | 4 | 37.26 | 43.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.03 | 0 | 38.06 | 64 | 64 | 98.33 | 86.63 | 79.22 | 0 | 101.65 | 2.21 | 88.67 | 42.85 | 103.98 | 13.93 | 103.65 | 110 | 0 | 15742 | 79.5 | 114.4 | 217.31 | 211.25 | 217.01 | 0 | 28.82 | 50.38 | 12816 | 89.72 | 42.05 | 37.26 | 1.12 | 42.05 | 0 | 604 | 437 | 457.6 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.8 | 318.9 | 0 | 312.6 | 101.7 | 15742 | 15742 | 317
03/26/22 10:24:01.207 | 607.0347 | 1367.2259 | 54.7088 | 44.0821 | 10.6267 | 30.6667 | 50.8433 | 0 | 1791.3415 | 87.2491 | 77.9156 | 9.3335 | 25.1698 | 69.1888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0321 | 460.6001 | 457.3201 | 461.1501 | 419.2901 | 448.1901 | 425.5501 | 319.0201 | 0.52554 | 0.46841 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7311359.7287 | 8360544.6914 | 8360544.6914 | 62.427 | 62.208 | 1.0017 | 0.99806 | 684339.39 | 894384.3974 | 459.6901 | 0.51556 | 0 | 0 | 30.6667 | 25.1698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017918 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6241 | 1367.9383 | 55.4429 | 44.5119 | 30.5013 | 1787.676 | 72.3168 | 26.1141 | 459.5264 | 0.0057154 | 60.0016 | 0.5191 | 2.6901 | 81.703 | 2.398 | 0.54122 | 0.48221 | 4.1367 | 3.7841 | 0.19513 | 0 | 100 | 584.4 | 318 | 104.05 | 103.6 | 101.63 | 309.5 | 3 | 89.76 | 42.06 | 4 | 37.28 | 43.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.1 | 0 | 38.07 | 64 | 64 | 98.4 | 86.68 | 79.22 | 0 | 101.63 | 2.21 | 88.71 | 42.86 | 104.05 | 13.84 | 103.6 | 110 | 0 | 15740 | 79.52 | 114.4 | 217.42 | 211.35 | 217.01 | 0 | 28.74 | 50.28 | 12821 | 89.76 | 42.06 | 37.28 | 1.11 | 42.06 | 0 | 604 | 438.1 | 457.6 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.4 | 317.6 | 0 | 311.3 | 101.63 | 15739 | 15740 | 317
03/26/22 10:24:06.209 | 606.4935 | 1364.2222 | 54.7016 | 44.0611 | 10.6405 | 30.4406 | 50.8361 | 0 | 1790.65 | 87.2812 | 77.937 | 9.3442 | 25.6703 | 69.1748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.032 | 460.6 | 457.32 | 461.15 | 419.29 | 448.19 | 425.55 | 319.02 | 0.52601 | 0.30754 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7304606.9655 | 8367375.7155 | 8367375.7155 | 62.4271 | 62.2077 | 1.0017 | 0.99806 | 682836.2803 | 894036.3427 | 459.69 | 0.51556 | 0 | 0 | 30.4406 | 25.6703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.01792 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6134 | 1367.9053 | 55.4475 | 44.5164 | 30.5042 | 1787.6984 | 72.3878 | 26.1053 | 459.5249 | 0.0057122 | 60.0018 | 0.51942 | 2.6715 | 81.7764 | 2.4081 | 0.53115 | 0.47398 | 4.1418 | 3.7688 | 0.19275 | 0 | 100 | 584.6 | 317 | 104.05 | 103.58 | 101.63 | 312.1 | 3 | 89.76 | 42.08 | 4 | 37.29 | 43.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.13 | 0 | 38.1 | 64 | 64 | 98.4 | 86.68 | 79.26 | 0 | 101.63 | 2.21 | 88.72 | 42.89 | 104.08 | 13.8 | 103.58 | 110 | 0 | 15738 | 79.52 | 114.4 | 217.42 | 211.35 | 217.13 | 0 | 28.73 | 50.32 | 12826 | 89.78 | 42.08 | 37.29 | 1.13 | 42.08 | 0 | 604 | 437 | 457.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.4 | 317.9 | 0 | 311.5 | 101.63 | 15738 | 15738 | 317
03/26/22 10:24:11.208 | 607.7426 | 1364.9395 | 54.6954 | 44.0385 | 10.6568 | 30.6347 | 50.8299 | 0 | 1791.3054 | 87.3181 | 77.9616 | 9.3565 | 25.4763 | 69.2086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.028 | 460.61 | 457.37 | 461.16 | 419.27 | 448.07 | 425.59 | 319 | 0.52489 | 0.32216 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7319780.6612 | 8381209.377 | 8381209.377 | 62.4271 | 62.2074 | 1.0017 | 0.99806 | 683195.6236 | 894360.3806 | 459.7134 | 0.50974 | 0 | 0 | 30.6347 | 25.4763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017914 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6049 | 1367.8933 | 55.4517 | 44.5206 | 30.5081 | 1787.7019 | 72.4584 | 26.0948 | 459.5237 | 0.0057096 | 60.0021 | 0.51973 | 2.6545 | 81.8492 | 2.42 | 0.52211 | 0.46621 | 4.1441 | 3.7534 | 0.19102 | 0 | 100 | 584.4 | 317 | 104.08 | 103.55 | 101.63 | 312.2 | 3 | 89.78 | 42.09 | 4 | 37.3 | 43.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.05 | 0 | 38.11 | 64 | 64 | 98.38 | 86.66 | 79.3 | 0 | 101.63 | 2.21 | 88.68 | 42.9 | 104.08 | 13.76 | 103.55 | 110 | 0 | 15735 | 79.54 | 114.4 | 217.53 | 211.46 | 217.13 | 0 | 28.9 | 50.63 | 12831 | 89.79 | 42.09 | 37.3 | 1.12 | 42.09 | 0 | 604 | 438.7 | 457.6 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.6 | 317.7 | 0 | 311.4 | 101.67 | 15734 | 15735 | 316
03/26/22 10:24:16.207 | 609.422 | 1367.3549 | 54.6926 | 44.0253 | 10.6674 | 30.8196 | 50.8227 | 0 | 1791.0577 | 87.343 | 77.9778 | 9.3651 | 24.9954 | 69.1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.028 | 460.63 | 457.41 | 461.17 | 419.18 | 447.97 | 425.56 | 318.95 | 0.52336 | 0.49092 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7340143.3434 | 8387170.4685 | 8387170.4685 | 62.4271 | 62.2072 | 1.0017 | 0.99806 | 684404.7125 | 894234.6 | 459.7367 | 0.50609 | 0 | 0 | 30.8196 | 24.9954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017913 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6043 | 1367.899 | 55.4558 | 44.5247 | 30.5143 | 1787.7098 | 72.5289 | 26.0798 | 459.5229 | 0.0057078 | 60.0024 | 0.52 | 2.638 | 81.9219 | 2.4162 | 0.51327 | 0.45852 | 4.1499 | 3.7371 | 0.18986 | 0 | 100 | 584.6 | 318 | 104.1 | 103.51 | 101.69 | 313.2 | 3 | 89.79 | 42.11 | 4 | 37.33 | 43.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.1 | 0 | 38.13 | 64 | 64 | 98.38 | 86.66 | 79.35 | 0 | 101.69 | 2.21 | 88.71 | 42.91 | 104.1 | 13.71 | 103.51 | 110 | 0 | 15733 | 79.54 | 114.4 | 217.53 | 211.56 | 217.24 | 0 | 29.2 | 51 | 12836 | 89.79 | 42.11 | 37.33 | 1.06 | 42.11 | 0 | 604 | 438.9 | 457.6 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.6 | 316.6 | 0 | 310.3 | 101.67 | 15733 | 15733 | 316
03/26/22 10:24:21.207 | 609.9382 | 1367.0762 | 54.691 | 44.0154 | 10.6756 | 31.0769 | 50.8357 | 0 | 1790.041 | 87.3632 | 77.9917 | 9.3715 | 24.7477 | 69.2065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0281 | 460.6301 | 457.4101 | 461.1701 | 419.1801 | 447.9701 | 425.5601 | 318.9501 | 0.52292 | 0.5426 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7346557.7949 | 8389216.4429 | 8389216.4429 | 62.4271 | 62.2071 | 1.0017 | 0.99806 | 684552.0257 | 893978.0388 | 459.7368 | 0.50609 | 0 | 0 | 31.0769 | 24.7477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017915 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.6061 | 1367.9199 | 55.4595 | 44.5286 | 30.5194 | 1787.7214 | 72.599 | 26.0675 | 459.5224 | 0.0057068 | 60.0026 | 0.52026 | 2.6222 | 81.9942 | 2.3924 | 0.5052 | 0.45122 | 4.1535 | 3.7204 | 0.18923 | 0 | 100 | 584.4 | 318 | 104.15 | 103.51 | 101.63 | 312.1 | 3 | 89.82 | 42.13 | 4 | 37.35 | 43.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.17 | 0 | 38.14 | 64 | 64 | 98.4 | 86.68 | 79.37 | 0 | 101.63 | 2.21 | 88.75 | 42.92 | 104.15 | 13.69 | 103.51 | 110 | 0 | 15730 | 79.56 | 114.43 | 217.65 | 211.56 | 217.24 | 0 | 29.41 | 51.08 | 12841 | 89.82 | 42.14 | 37.35 | 1.03 | 42.14 | 0 | 604 | 437.5 | 457.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.4 | 318.5 | 0 | 312.1 | 101.63 | 15730 | 15730 | 318
03/26/22 10:24:26.207 | 608.5328 | 1363.0197 | 54.689 | 44.0033 | 10.6857 | 31.0391 | 50.8648 | 0 | 1789.0242 | 87.391 | 78.0116 | 9.3794 | 24.6422 | 69.2111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.029 | 460.63 | 457.43 | 461.19 | 419.11 | 447.97 | 425.51 | 318.91 | 0.52406 | 0.33153 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7329580.0436 | 8389884.2722 | 8389884.2722 | 62.4272 | 62.2068 | 1.0017 | 0.99806 | 682234.9669 | 893214.9634 | 459.75 | 0.50462 | 0 | 0 | 31.0391 | 24.6422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016243 | 0.017918 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.5882 | 1367.9055 | 55.4629 | 44.5322 | 30.5252 | 1787.7312 | 72.6689 | 26.0543 | 459.5222 | 0.0057063 | 60.0028 | 0.5205 | 2.6037 | 82.0662 | 2.4141 | 0.49765 | 0.44419 | 4.1545 | 3.7031 | 0.18896 | 0 | 100 | 584.6 | 318 | 104.23 | 103.48 | 101.67 | 311.3 | 3 | 89.84 | 42.13 | 4 | 37.34 | 43.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.17 | 0 | 38.14 | 64 | 64 | 98.4 | 86.68 | 79.41 | 0 | 101.67 | 2.21 | 88.75 | 42.92 | 104.2 | 13.64 | 103.48 | 110 | 0 | 15727 | 79.56 | 114.43 | 217.65 | 211.66 | 217.35 | 0 | 29.53 | 51.04 | 12846 | 89.84 | 42.13 | 37.34 | 1.05 | 42.13 | 0 | 604 | 439.4 | 457.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.4 | 318.6 | 0 | 312.2 | 101.63 | 15728 | 15727 | 319
03/26/22 10:24:31.207 | 608.282 | 1362.0339 | 54.6882 | 43.9975 | 10.6907 | 31.1915 | 50.8623 | 0 | 1785.938 | 87.4072 | 78.0239 | 9.3833 | 24.6251 | 69.2198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0291 | 460.6301 | 457.4301 | 461.1901 | 419.1101 | 447.9701 | 425.5101 | 318.9101 | 0.52428 | 0.39647 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7326652.4935 | 8381521.6173 | 8381521.6173 | 62.4272 | 62.2067 | 1.0017 | 0.99806 | 681692.521 | 892018.0769 | 459.7501 | 0.50462 | 0 | 0 | 31.1915 | 24.6251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016244 | 0.017924 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.546 | 1367.8555 | 55.466 | 44.5357 | 30.5327 | 1787.6972 | 72.7384 | 26.0367 | 459.522 | 0.0057059 | 60.003 | 0.52076 | 2.5855 | 82.1376 | 2.4421 | 0.491 | 0.43758 | 4.1439 | 3.6855 | 0.18869 | 0 | 100 | 584.4 | 318 | 104.27 | 103.46 | 101.63 | 311.1 | 3 | 89.88 | 42.14 | 4 | 37.36 | 43.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.25 | 0 | 38.16 | 64 | 64 | 98.5 | 86.73 | 79.41 | 0 | 101.63 | 2.21 | 88.79 | 42.95 | 104.25 | 13.59 | 103.46 | 110 | 0 | 15725 | 79.58 | 114.4 | 217.76 | 211.76 | 217.47 | 0 | 29.64 | 51.02 | 12851 | 89.87 | 42.15 | 37.36 | 1.02 | 42.15 | 0 | 604 | 435.6 | 457.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.7 | 319.2 | 0 | 312.9 | 101.69 | 15722 | 15725 | 317
03/26/22 10:24:36.207 | 609.1769 | 1363.0764 | 54.6882 | 43.9914 | 10.6968 | 30.5938 | 50.8423 | 0 | 1781.5718 | 87.4279 | 78.0404 | 9.3874 | 25.671 | 69.2449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.028 | 460.66 | 457.46 | 461.21 | 419.01 | 447.84 | 425.46 | 318.82 | 0.52336 | 0.75974 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7337175.3992 | 8361267.8525 | 8361267.8525 | 62.4272 | 62.2065 | 1.0017 | 0.99806 | 682302.16 | 889382.4947 | 459.7767 | 0.50387 | 0 | 0 | 30.5938 | 25.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016244 | 0.017926 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.5112 | 1367.8307 | 55.4689 | 44.5389 | 30.5348 | 1787.6487 | 72.8075 | 26.0288 | 459.5221 | 0.0057061 | 60.0031 | 0.52097 | 2.5689 | 82.2086 | 2.4678 | 0.48491 | 0.43126 | 4.1642 | 3.6673 | 0.18879 | 0 | 100 | 585.1 | 316 | 104.27 | 103.46 | 101.76 | 312.1 | 3 | 89.88 | 42.19 | 4 | 37.4 | 43.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.28 | 0 | 38.19 | 64 | 64 | 98.55 | 86.76 | 79.45 | 0 | 101.76 | 2.21 | 88.81 | 42.97 | 104.27 | 13.57 | 103.46 | 110 | 0 | 15722 | 79.58 | 114.4 | 217.76 | 211.76 | 217.47 | 0 | 29.59 | 50.69 | 12856 | 89.88 | 42.19 | 37.4 | 1.04 | 42.19 | 0 | 604 | 435.6 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.9 | 319.1 | 0 | 312.7 | 101.72 | 15722 | 15722 | 318
03/26/22 10:24:41.207 | 610.9299 | 1366.0853 | 54.6892 | 43.9855 | 10.7037 | 30.3369 | 50.8537 | 0 | 1784.7509 | 87.455 | 78.0629 | 9.3922 | 26.239 | 69.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.028 | 460.66 | 457.5 | 461.21 | 418.93 | 447.71 | 425.5 | 318.79 | 0.52181 | 0.7439 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7357789.2921 | 8382952.1337 | 8382952.1337 | 62.4272 | 62.2063 | 1.0017 | 0.99805 | 683769.4013 | 891074.7654 | 459.79 | 0.49805 | 0 | 0 | 30.3369 | 26.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016241 | 0.017923 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.4917 | 1367.8463 | 55.4715 | 44.542 | 30.5354 | 1787.6316 | 72.8765 | 26.0234 | 459.5223 | 0.0057066 | 60.0032 | 0.52115 | 2.5525 | 82.2795 | 2.4478 | 0.47928 | 0.42517 | 4.1698 | 3.6486 | 0.18911 | 0 | 100 | 584.8 | 317 | 104.3 | 103.43 | 101.74 | 311 | 3 | 89.9 | 42.2 | 4 | 37.41 | 43.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.25 | 0 | 38.21 | 64 | 64 | 98.53 | 86.75 | 79.5 | 0 | 101.74 | 2.21 | 88.79 | 43 | 104.25 | 13.56 | 103.43 | 110 | 0 | 15718 | 79.6 | 114.38 | 217.88 | 211.86 | 217.58 | 0 | 29.4 | 50.32 | 12861 | 89.87 | 42.2 | 37.41 | 1.06 | 42.2 | 0 | 604 | 439.7 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.3 | 317.3 | 0 | 311 | 101.79 | 15719 | 15718 | 314
03/26/22 10:24:46.206 | 612.4659 | 1369.0529 | 54.69 | 43.9827 | 10.7073 | 30.8241 | 50.8516 | 0 | 1787.925 | 87.4731 | 78.0781 | 9.3951 | 25.2691 | 69.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0281 | 460.6601 | 457.5301 | 461.2201 | 418.8001 | 447.5701 | 425.5501 | 318.7401 | 0.52042 | 0.77238 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7376708.4102 | 8399338.3991 | 8399338.3991 | 62.4272 | 62.2061 | 1.0017 | 0.99805 | 685254.7304 | 892657.4849 | 459.8034 | 0.49441 | 0 | 0 | 30.8241 | 25.2691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.01792 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.4734 | 1367.8787 | 55.4739 | 44.5449 | 30.5361 | 1787.6455 | 72.9451 | 26.0153 | 459.5227 | 0.0057074 | 60.0033 | 0.52129 | 2.5349 | 82.3498 | 2.4247 | 0.47434 | 0.41945 | 4.1666 | 3.6295 | 0.18961 | 0 | 100 | 584.7 | 317 | 104.3 | 103.41 | 101.69 | 311.9 | 3 | 89.88 | 42.21 | 4 | 37.41 | 43.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.23 | 0 | 38.23 | 64 | 64 | 98.5 | 86.73 | 79.56 | 0 | 101.69 | 2.21 | 88.78 | 43.01 | 104.33 | 13.51 | 103.41 | 110 | 0 | 15715 | 79.6 | 114.35 | 217.99 | 211.97 | 217.58 | 0 | 29.17 | 50.03 | 12866 | 89.88 | 42.21 | 37.43 | 1.05 | 42.21 | 0 | 604 | 435 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.8 | 315.9 | 0 | 309.6 | 101.7 | 15717 | 15715 | 317
03/26/22 10:24:51.207 | 615.5449 | 1375.3751 | 54.6924 | 43.9807 | 10.7117 | 31.1969 | 50.8541 | 0 | 1786.4489 | 87.4995 | 78.0995 | 9.4 | 24.7034 | 69.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.03 | 460.66 | 457.58 | 461.23 | 418.66 | 447.41 | 425.63 | 318.7 | 0.51775 | 1.2482 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7414110.6893 | 8396098.1521 | 8396098.1521 | 62.4272 | 62.2059 | 1.0017 | 0.99805 | 688419.0971 | 891917.7501 | 459.8234 | 0.48787 | 0 | 0 | 31.1969 | 24.7034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017923 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.4642 | 1367.9358 | 55.4761 | 44.5477 | 30.5426 | 1787.6641 | 73.0135 | 26.0003 | 459.5231 | 0.0057083 | 60.0034 | 0.52141 | 2.5182 | 82.4199 | 2.4677 | 0.46983 | 0.41392 | 4.1561 | 3.6097 | 0.19017 | 0 | 100 | 585.4 | 318 | 104.33 | 103.38 | 101.81 | 311.8 | 3 | 89.91 | 42.25 | 4 | 37.46 | 43.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.28 | 0 | 38.26 | 64 | 64 | 98.53 | 86.75 | 79.58 | 0 | 101.81 | 2.21 | 88.81 | 43.05 | 104.35 | 13.46 | 103.38 | 110 | 0 | 15713 | 79.62 | 114.33 | 217.99 | 211.97 | 217.69 | 0 | 29.19 | 50.19 | 12871 | 89.92 | 42.25 | 37.46 | 1.03 | 42.25 | 0 | 604 | 439.3 | 457.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.5 | 316.5 | 0 | 310.2 | 101.83 | 15712 | 15713 | 317
03/26/22 10:24:56.207 | 615.0178 | 1373.9094 | 54.6943 | 43.9804 | 10.7139 | 30.5675 | 50.8646 | 0 | 1785.5767 | 87.5157 | 78.1122 | 9.4034 | 25.6769 | 69.2916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.03 | 460.66 | 457.58 | 461.23 | 418.66 | 447.41 | 425.63 | 318.7 | 0.5182 | 1.1663 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7407200.3587 | 8396151.1529 | 8396151.1529 | 62.4272 | 62.2057 | 1.0017 | 0.99805 | 687685.3595 | 891480.6415 | 459.8233 | 0.48787 | 0 | 0 | 30.5675 | 25.6769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017923 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.4438 | 1367.9837 | 55.478 | 44.5504 | 30.5447 | 1787.6781 | 73.0816 | 25.9913 | 459.5236 | 0.0057093 | 60.0035 | 0.52151 | 2.5003 | 82.4896 | 2.4995 | 0.46594 | 0.40871 | 4.1446 | 3.5896 | 0.19082 | 0 | 100 | 585.1 | 316 | 104.38 | 103.36 | 101.76 | 310.2 | 3 | 89.94 | 42.28 | 4 | 37.49 | 43.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.33 | 0 | 38.27 | 64 | 64 | 98.58 | 86.77 | 79.6 | 0 | 101.76 | 2.21 | 88.83 | 43.06 | 104.38 | 13.42 | 103.36 | 110 | 0 | 15709 | 79.62 | 114.31 | 217.99 | 212.07 | 217.69 | 0 | 29.07 | 49.99 | 12876 | 89.94 | 42.28 | 37.49 | 1.01 | 42.28 | 0 | 604 | 432.8 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.1 | 317.5 | 0 | 311.1 | 101.76 | 15711 | 15709 | 317
03/26/22 10:25:01.206 | 613.7211 | 1369.9767 | 54.6966 | 43.981 | 10.7156 | 30.1903 | 50.8687 | 0 | 1788.2398 | 87.5344 | 78.1272 | 9.4071 | 26.1986 | 69.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.032 | 460.68 | 457.63 | 461.25 | 418.38 | 447.12 | 425.58 | 318.55 | 0.51905 | 0.85037 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7391010.666 | 8406666.9568 | 8406666.9568 | 62.4272 | 62.2056 | 1.0017 | 0.99805 | 686161.1763 | 892283.3477 | 459.8534 | 0.48349 | 0 | 0 | 30.1903 | 26.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017918 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.4026 | 1368.0059 | 55.4795 | 44.5528 | 30.5428 | 1787.6913 | 73.1492 | 25.9886 | 459.5241 | 0.0057104 | 60.0036 | 0.52163 | 2.4808 | 82.5587 | 2.5072 | 0.4628 | 0.40389 | 4.1393 | 3.5692 | 0.19147 | 0 | 100 | 584.1 | 315 | 104.33 | 103.34 | 101.58 | 308.8 | 3 | 89.91 | 42.25 | 4 | 37.46 | 43.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.28 | 0 | 38.26 | 64 | 64 | 98.53 | 86.75 | 79.62 | 0 | 101.6 | 2.21 | 88.81 | 43.05 | 104.33 | 13.42 | 103.34 | 110 | 0 | 15707 | 79.62 | 114.31 | 218.11 | 212.07 | 217.81 | 0 | 29.01 | 50.19 | 12881 | 89.91 | 42.25 | 37.46 | 1.02 | 42.25 | 0 | 605 | 437 | 458.1 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.9 | 315.3 | 0 | 309 | 101.55 | 15706 | 15707 | 315
03/26/22 10:25:06.207 | 613.417 | 1370.018 | 54.7002 | 43.9838 | 10.7164 | 30.3509 | 50.8718 | 0 | 1788.7146 | 87.5603 | 78.1486 | 9.4117 | 26.0121 | 69.3383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.031 | 460.67 | 457.64 | 461.26 | 418.23 | 447.04 | 425.59 | 318.49 | 0.51921 | 0.66139 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7387724.1187 | 8418591.9812 | 8418591.9812 | 62.4272 | 62.2053 | 1.0017 | 0.99805 | 685737.3236 | 893042.5587 | 459.8567 | 0.48203 | 0 | 0 | 30.3509 | 26.0121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017921 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.3534 | 1368.0237 | 55.4809 | 44.5552 | 30.545 | 1787.7007 | 73.2165 | 25.9819 | 459.525 | 0.0057124 | 60.0038 | 0.52171 | 2.4611 | 82.6275 | 2.5086 | 0.4602 | 0.39936 | 4.1413 | 3.5483 | 0.19268 | 0 | 100 | 584.4 | 317 | 104.33 | 103.31 | 101.65 | 310.7 | 3 | 89.91 | 42.26 | 4 | 37.48 | 43.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.3 | 0 | 38.27 | 64 | 64 | 98.55 | 86.76 | 79.65 | 0 | 101.65 | 2.21 | 88.82 | 43.06 | 104.3 | 13.4 | 103.31 | 110 | 0 | 15704 | 79.62 | 114.31 | 218.22 | 212.17 | 217.81 | 0 | 29.2 | 50.39 | 12886 | 89.91 | 42.26 | 37.48 | 1 | 42.26 | 0 | 605 | 437.7 | 458.1 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.6 | 316.2 | 0 | 309.8 | 101.67 | 15703 | 15704 | 317
03/26/22 10:25:11.207 | 614.1988 | 1371.5921 | 54.7028 | 43.986 | 10.7168 | 29.7375 | 50.8785 | 0 | 1788.0643 | 87.5737 | 78.1595 | 9.4142 | 26.8005 | 69.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.028 | 460.67 | 457.65 | 461.26 | 418.02 | 446.91 | 425.48 | 318.38 | 0.51837 | 0.78404 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7396645.8865 | 8417124.7677 | 8417124.7677 | 62.4272 | 62.2052 | 1.0017 | 0.99805 | 686592.2967 | 892618.855 | 459.86 | 0.48058 | 0 | 0 | 29.7375 | 26.8005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017917 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.3002 | 1368.0508 | 55.4818 | 44.5573 | 30.5423 | 1787.7219 | 73.2834 | 25.9831 | 459.5262 | 0.005715 | 60.004 | 0.52177 | 2.4397 | 82.6957 | 2.5222 | 0.45833 | 0.39527 | 4.1323 | 3.5272 | 0.19407 | 0 | 100 | 584.6 | 316 | 104.3 | 103.29 | 101.67 | 311.4 | 3 | 89.9 | 42.3 | 4 | 37.51 | 43.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.3 | 0 | 38.3 | 64 | 64 | 98.55 | 86.77 | 79.69 | 0 | 101.67 | 2.21 | 88.82 | 43.09 | 104.33 | 13.38 | 103.29 | 110 | 0 | 15702 | 79.65 | 114.33 | 218.22 | 212.17 | 217.92 | 0 | 29.05 | 50.21 | 12891 | 89.91 | 42.3 | 37.51 | 0.97 | 42.3 | 0 | 605 | 434.4 | 458 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.5 | 317.1 | 0 | 310.7 | 101.65 | 15701 | 15702 | 317
03/26/22 10:25:16.206 | 613.522 | 1370.5031 | 54.7072 | 43.9897 | 10.7175 | 30.2901 | 50.8661 | 0 | 1793.0756 | 87.5925 | 78.1748 | 9.4177 | 26.1319 | 69.3085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0261 | 460.6401 | 457.6301 | 461.2501 | 417.8701 | 446.8001 | 425.3601 | 318.2601 | 0.51874 | 0.43067 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7388852.1307 | 8438787.6315 | 8438787.6315 | 62.4272 | 62.2051 | 1.0017 | 0.99805 | 685793.8808 | 894644.8156 | 459.8401 | 0.4806 | 0 | 0 | 30.2901 | 26.1319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017905 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.2348 | 1368.0563 | 55.4826 | 44.5593 | 30.5406 | 1787.7806 | 73.35 | 25.9822 | 459.5275 | 0.0057178 | 60.0043 | 0.52183 | 2.4148 | 82.7636 | 2.5257 | 0.45687 | 0.39142 | 4.1164 | 3.5055 | 0.19538 | 0 | 100 | 583.7 | 317 | 104.25 | 103.29 | 101.51 | 312.1 | 3 | 89.86 | 42.31 | 4 | 37.53 | 43.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.23 | 0 | 38.31 | 64 | 64 | 98.48 | 86.72 | 79.73 | 0 | 101.51 | 2.21 | 88.78 | 43.1 | 104.25 | 13.42 | 103.29 | 110 | 0 | 15699 | 79.65 | 114.35 | 218.34 | 212.28 | 217.92 | 0 | 29.39 | 51.04 | 12896 | 89.87 | 42.3 | 37.51 | 0.97 | 42.3 | 0 | 604 | 438 | 457.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584 | 317.9 | 0 | 311.6 | 101.57 | 15698 | 15699 | 317
03/26/22 10:25:21.208 | 613.2109 | 1369.4038 | 54.7127 | 43.9951 | 10.7176 | 30.4267 | 50.8568 | 0 | 1793.1221 | 87.6137 | 78.192 | 9.4217 | 25.5312 | 69.3461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0251 | 460.6601 | 457.6401 | 461.2801 | 417.6901 | 446.6701 | 425.1701 | 318.1501 | 0.51883 | 0.27861 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7385305.3311 | 8447684.1333 | 8447684.1333 | 62.4271 | 62.2048 | 1.0017 | 0.99805 | 685429.328 | 895237.3905 | 459.8601 | 0.48276 | 0 | 0 | 30.4267 | 25.5312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017907 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.1591 | 1368.0575 | 55.4831 | 44.5611 | 30.5425 | 1787.8669 | 73.4161 | 25.9757 | 459.5289 | 0.0057208 | 60.0045 | 0.52188 | 2.3878 | 82.8309 | 2.5263 | 0.4561 | 0.38808 | 4.0766 | 3.4836 | 0.19671 | 0 | 100 | 583.7 | 316 | 104.3 | 103.24 | 101.51 | 309.7 | 3 | 89.9 | 42.31 | 4 | 37.53 | 43.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.23 | 0 | 38.31 | 64 | 64 | 98.58 | 86.77 | 79.71 | 0 | 101.51 | 2.21 | 88.78 | 43.1 | 104.3 | 13.34 | 103.24 | 110 | 0 | 15697 | 79.65 | 114.4 | 218.34 | 212.38 | 218.04 | 0 | 29.63 | 50.94 | 12900 | 89.9 | 42.31 | 37.53 | 0.95 | 42.31 | 0 | 604 | 438 | 457.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.9 | 314.4 | 0 | 308.1 | 101.55 | 15696 | 15697 | 315
03/26/22 10:25:26.207 | 612.3074 | 1367.4323 | 54.7178 | 44.0005 | 10.7173 | 30.2189 | 50.8803 | 0 | 1789.3029 | 87.6295 | 78.2044 | 9.4251 | 25.5768 | 69.3857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.025 | 460.66 | 457.64 | 461.28 | 417.69 | 446.67 | 425.17 | 318.15 | 0.51959 | 0.32055 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7374241.8502 | 8432740.0708 | 8432740.0708 | 62.4271 | 62.2047 | 1.0017 | 0.99805 | 684442.3059 | 893329.0313 | 459.86 | 0.48276 | 0 | 0 | 30.2189 | 25.5768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017907 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 624.0778 | 1368.0608 | 55.4832 | 44.5627 | 30.5437 | 1787.9107 | 73.482 | 25.9695 | 459.5305 | 0.0057243 | 60.0047 | 0.52192 | 2.3631 | 82.8979 | 2.5251 | 0.4558 | 0.3851 | 4.0493 | 3.4612 | 0.19823 | 0 | 100 | 583.8 | 317 | 104.23 | 103.22 | 101.53 | 310.6 | 3 | 89.86 | 42.34 | 4 | 37.55 | 43.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.25 | 0 | 38.34 | 64 | 64 | 98.55 | 86.76 | 79.73 | 0 | 101.53 | 2.21 | 88.79 | 43.12 | 104.25 | 13.34 | 103.22 | 110 | 0 | 15694 | 79.65 | 114.4 | 218.34 | 212.38 | 218.04 | 0 | 29.51 | 50.75 | 12905 | 89.87 | 42.34 | 37.55 | 0.93 | 42.34 | 0 | 605 | 434.3 | 458.1 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.9 | 317.3 | 0 | 311 | 101.55 | 15693 | 15694 | 317
03/26/22 10:25:31.206 | 611.7829 | 1366.302 | 54.7229 | 44.0059 | 10.717 | 29.7066 | 50.876 | 0 | 1790.2423 | 87.6415 | 78.2127 | 9.4288 | 26.7314 | 69.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.026 | 460.7 | 457.71 | 461.35 | 417.16 | 446.29 | 424.77 | 317.88 | 0.5196 | 0.13301 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7367475.8543 | 8441812.3639 | 8441812.3639 | 62.4271 | 62.2046 | 1.0017 | 0.99805 | 683876.3356 | 893796.9115 | 459.92 | 0.48052 | 0 | 0 | 29.7066 | 26.7314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017896 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.9899 | 1368.0604 | 55.4831 | 44.5641 | 30.5428 | 1787.9432 | 73.5476 | 25.9663 | 459.5321 | 0.0057277 | 60.005 | 0.52197 | 2.3384 | 82.9645 | 2.5254 | 0.45595 | 0.3825 | 4.0444 | 3.4382 | 0.19972 | 0 | 100 | 583.9 | 316 | 104.2 | 103.19 | 101.55 | 310.3 | 3 | 89.84 | 42.35 | 4 | 37.56 | 43.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.2 | 0 | 38.35 | 64 | 64 | 98.48 | 86.72 | 79.75 | 0 | 101.55 | 2.2 | 88.77 | 43.14 | 104.17 | 13.36 | 103.19 | 110 | 0 | 15692 | 79.67 | 114.4 | 218.45 | 212.48 | 218.04 | 0 | 29.5 | 50.56 | 12911 | 89.83 | 42.35 | 37.56 | 0.93 | 42.35 | 0 | 605 | 436.4 | 458.1 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.9 | 316.6 | 0 | 310.3 | 101.55 | 15691 | 15692 | 316
03/26/22 10:25:36.206 | 612.1609 | 1367.1897 | 54.7291 | 44.0124 | 10.7167 | 30.505 | 50.8753 | 0 | 1793.2614 | 87.6523 | 78.2195 | 9.4328 | 25.6045 | 69.3717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.022 | 460.7 | 457.73 | 461.36 | 416.99 | 446.08 | 424.64 | 317.78 | 0.51911 | -0.010225 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7372730.7539 | 8458246.8153 | 8458246.8153 | 62.4271 | 62.2045 | 1.0017 | 0.99805 | 684320.3711 | 895303.3732 | 459.93 | 0.47833 | 0 | 0 | 30.505 | 25.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017896 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.8905 | 1368.0457 | 55.4828 | 44.5654 | 30.5496 | 1787.979 | 73.6127 | 25.9518 | 459.5342 | 0.0057323 | 60.0052 | 0.52201 | 2.3123 | 83.0307 | 2.5227 | 0.45655 | 0.38031 | 4.0628 | 3.4147 | 0.2018 | 0 | 100 | 583.7 | 317 | 104.23 | 103.17 | 101.57 | 310.5 | 3 | 89.86 | 42.36 | 4 | 37.56 | 43.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.17 | 0 | 38.36 | 64 | 64 | 98.45 | 86.7 | 79.77 | 0 | 101.57 | 2.2 | 88.75 | 43.15 | 104.23 | 13.31 | 103.17 | 110 | 0 | 15690 | 79.67 | 114.4 | 218.45 | 212.48 | 218.15 | 0 | 29.34 | 50.49 | 12916 | 89.86 | 42.36 | 37.58 | 0.92 | 42.36 | 0 | 605 | 436.9 | 458.1 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.4 | 314.4 | 0 | 308.1 | 101.46 | 15688 | 15690 | 315
03/26/22 10:25:41.206 | 612.4131 | 1367.9793 | 54.7358 | 44.0197 | 10.7162 | 31.0347 | 50.8737 | 0 | 1791.6254 | 87.662 | 78.2259 | 9.4361 | 24.5826 | 69.3803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0181 | 460.7201 | 457.7601 | 461.3701 | 416.8601 | 445.9001 | 424.5101 | 317.7001 | 0.51877 | 0.061417 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7376257.0324 | 8455372.5868 | 8455372.5868 | 62.4271 | 62.2044 | 1.0017 | 0.99805 | 684630.0665 | 894841.3932 | 459.9501 | 0.47614 | 0 | 0 | 31.0347 | 24.5826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017899 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.7838 | 1368.0231 | 55.482 | 44.5664 | 30.5605 | 1787.981 | 73.6775 | 25.9296 | 459.5364 | 0.005737 | 60.0053 | 0.52205 | 2.2876 | 83.0963 | 2.5062 | 0.45762 | 0.37864 | 4.0649 | 3.3909 | 0.20395 | 0 | 100 | 583.6 | 317 | 104.27 | 103.17 | 101.5 | 308 | 3 | 89.88 | 42.38 | 4 | 37.59 | 43.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.25 | 0 | 38.38 | 64 | 64 | 98.55 | 86.76 | 79.75 | 0 | 101.5 | 2.2 | 88.79 | 43.16 | 104.3 | 13.27 | 103.17 | 110 | 0 | 15688 | 79.67 | 114.4 | 218.57 | 212.59 | 218.15 | 0 | 29.73 | 51.16 | 12921 | 89.9 | 42.38 | 37.59 | 0.91 | 42.38 | 0 | 605 | 437.8 | 458 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.6 | 317.1 | 0 | 310.8 | 101.5 | 15685 | 15688 | 317
03/26/22 10:25:46.206 | 612.6323 | 1368.3354 | 54.7391 | 44.0231 | 10.716 | 30.7453 | 50.8735 | 0 | 1790.1906 | 87.6656 | 78.2285 | 9.4371 | 24.8348 | 69.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.018 | 460.72 | 457.76 | 461.37 | 416.86 | 445.9 | 424.51 | 317.7 | 0.51858 | 0.18848 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7378621.2257 | 8446722.5527 | 8446722.5527 | 62.4271 | 62.2044 | 1.0017 | 0.99805 | 684893.3661 | 893769.0608 | 459.95 | 0.47614 | 0 | 0 | 30.7453 | 24.8348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017894 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.6756 | 1368.0048 | 55.4812 | 44.5672 | 30.5704 | 1787.959 | 73.742 | 25.9077 | 459.5387 | 0.005742 | 60.0055 | 0.52209 | 2.2646 | 83.1618 | 2.4918 | 0.4589 | 0.37721 | 4.0419 | 3.3661 | 0.20627 | 0 | 100 | 583.7 | 317 | 104.33 | 103.14 | 101.51 | 310.6 | 3 | 89.9 | 42.39 | 4 | 37.6 | 43.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.3 | 0 | 38.39 | 64 | 64 | 98.58 | 86.76 | 79.8 | 0 | 101.5 | 2.2 | 88.82 | 43.17 | 104.33 | 13.23 | 103.14 | 110 | 0 | 15686 | 79.67 | 114.4 | 218.57 | 212.59 | 218.27 | 0 | 29.73 | 50.73 | 12926 | 89.91 | 42.39 | 37.6 | 0.92 | 42.39 | 0 | 605 | 433.7 | 458.1 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.7 | 315.5 | 0 | 309.3 | 101.51 | 15687 | 15686 | 317
03/26/22 10:25:51.206 | 614.3367 | 1372.3507 | 54.749 | 44.0329 | 10.7162 | 30.7305 | 50.8638 | 0 | 1788.7713 | 87.6741 | 78.2346 | 9.4395 | 25.4269 | 69.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 460.7701 | 457.8201 | 461.3901 | 416.6801 | 445.5701 | 424.2901 | 317.5501 | 0.5169 | 0.43264 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7399119.6607 | 8446024.7194 | 8446024.7194 | 62.427 | 62.2043 | 1.0017 | 0.99805 | 686794.2324 | 893428.217 | 459.9934 | 0.47247 | 0 | 0 | 30.7305 | 25.4269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017899 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.5764 | 1368.019 | 55.4797 | 44.5677 | 30.5786 | 1787.9059 | 73.8059 | 25.8933 | 459.5411 | 0.0057473 | 60.0057 | 0.52212 | 2.245 | 83.2264 | 2.5092 | 0.46078 | 0.37658 | 3.9669 | 3.3415 | 0.20903 | 0 | 100 | 583 | 317 | 104.2 | 103.14 | 101.39 | 309.1 | 3 | 89.84 | 42.39 | 4 | 37.6 | 43.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.25 | 0 | 38.4 | 64 | 64 | 98.5 | 86.73 | 79.82 | 0 | 101.39 | 2.2 | 88.79 | 43.17 | 104.2 | 13.3 | 103.14 | 110 | 0 | 15684 | 79.67 | 114.4 | 218.69 | 212.69 | 218.27 | 0 | 29.62 | 50.78 | 12931 | 89.84 | 42.39 | 37.6 | 0.94 | 42.39 | 0 | 605 | 434.4 | 458.3 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 313.2 | 0 | 306.9 | 101.39 | 15683 | 15684 | 317
03/26/22 10:25:56.205 | 613.1389 | 1369.3367 | 54.7571 | 44.0401 | 10.717 | 31.0425 | 50.8673 | 0 | 1782.2479 | 87.6791 | 78.2377 | 9.4413 | 24.8831 | 69.4056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0191 | 460.8201 | 457.8901 | 461.4401 | 416.5101 | 445.3101 | 424.1001 | 317.4401 | 0.51773 | 0.65251 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7384981.265 | 8413055.6767 | 8413055.6767 | 62.427 | 62.2043 | 1.0017 | 0.99805 | 685393.6929 | 889802.3731 | 460.0501 | 0.46951 | 0 | 0 | 31.0425 | 24.8831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017908 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.4753 | 1368.0303 | 55.4781 | 44.5679 | 30.5836 | 1787.8231 | 73.8694 | 25.8802 | 459.5438 | 0.005753 | 60.0058 | 0.52215 | 2.2276 | 83.2908 | 2.5105 | 0.46282 | 0.37624 | 3.9283 | 3.3161 | 0.21243 | 0 | 100 | 583.5 | 316 | 104.33 | 103.14 | 101.48 | 308.6 | 3 | 89.91 | 42.41 | 4 | 37.63 | 43.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.33 | 0 | 38.41 | 64 | 64 | 98.63 | 86.79 | 79.77 | 0 | 101.48 | 2.2 | 88.83 | 43.2 | 104.35 | 13.22 | 103.14 | 110 | 0 | 15682 | 79.67 | 114.4 | 218.69 | 212.69 | 218.39 | 0 | 29.94 | 51.18 | 12935 | 89.92 | 42.41 | 37.63 | 0.97 | 42.41 | 0 | 605 | 436.5 | 458.3 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.8 | 316 | 0 | 309.7 | 101.53 | 15683 | 15682 | 316
03/26/22 10:26:01.206 | 613.8334 | 1370.8747 | 54.7668 | 44.0496 | 10.7172 | 31.1543 | 50.8679 | 0 | 1782.1808 | 87.6847 | 78.2422 | 9.4426 | 25.1011 | 69.3878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0241 | 460.9701 | 458.0501 | 461.5701 | 416.0301 | 444.9101 | 423.7601 | 317.2301 | 0.5168 | 0.74027 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7393444.4819 | 8414076.3614 | 8414076.3614 | 62.427 | 62.2042 | 1.0017 | 0.99805 | 686163.0604 | 889768.3013 | 460.1968 | 0.46647 | 0 | 0 | 31.1543 | 25.1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016212 | 0.01791 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.364 | 1368.025 | 55.476 | 44.5677 | 30.5889 | 1787.7663 | 73.9325 | 25.8684 | 459.5464 | 0.0057587 | 60.006 | 0.52219 | 2.2073 | 83.3545 | 2.5076 | 0.4652 | 0.37648 | 3.9347 | 3.2906 | 0.21574 | 0 | 100 | 583.1 | 315 | 104.4 | 103.17 | 101.41 | 309.2 | 3 | 89.95 | 42.41 | 4 | 37.63 | 43.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.4 | 0 | 38.41 | 64 | 64 | 98.65 | 86.82 | 79.84 | 0 | 101.41 | 2.2 | 88.87 | 43.2 | 104.4 | 13.22 | 103.17 | 110 | 0 | 15680 | 79.67 | 114.38 | 218.69 | 212.69 | 218.39 | 0 | 30 | 50.83 | 12941 | 89.95 | 42.41 | 37.63 | 0.99 | 42.41 | 0 | 606 | 434.3 | 458.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.1 | 315.5 | 0 | 309.2 | 101.41 | 15682 | 15680 | 315
03/26/22 10:26:06.206 | 613.9769 | 1370.8799 | 54.7721 | 44.0559 | 10.7163 | 30.8263 | 50.8605 | 0 | 1784.1833 | 87.6883 | 78.2457 | 9.4425 | 25.3793 | 69.4031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0181 | 461.0101 | 458.1101 | 461.6001 | 415.8201 | 444.7001 | 423.6301 | 317.1201 | 0.5165 | 0.64319 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7394987.5815 | 8423069.7691 | 8423069.7691 | 62.427 | 62.2042 | 1.0017 | 0.99805 | 686366.9478 | 890700.7184 | 460.2401 | 0.4628 | 0 | 0 | 30.8263 | 25.3793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017909 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.2591 | 1368.0398 | 55.4738 | 44.5674 | 30.593 | 1787.7237 | 73.9953 | 25.8582 | 459.5496 | 0.0057656 | 60.0061 | 0.52222 | 2.1874 | 83.4181 | 2.5206 | 0.46761 | 0.37687 | 3.9412 | 3.264 | 0.22106 | 0 | 100 | 582.4 | 317 | 104.4 | 103.17 | 101.29 | 310 | 3 | 89.95 | 42.41 | 4 | 37.63 | 43.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.38 | 0 | 38.41 | 64 | 64 | 98.63 | 86.79 | 79.88 | 0 | 101.29 | 2.2 | 88.87 | 43.2 | 104.4 | 13.23 | 103.17 | 110 | 0 | 15679 | 79.67 | 114.33 | 218.8 | 212.79 | 218.39 | 0 | 29.59 | 50.23 | 12946 | 89.94 | 42.41 | 37.61 | 0.99 | 42.41 | 0 | 606 | 430.6 | 458.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.7 | 316.5 | 0 | 310.2 | 101.17 | 15677 | 15679 | 317
03/26/22 10:26:11.206 | 612.624 | 1368.4232 | 54.7775 | 44.0622 | 10.7153 | 30.8514 | 50.8733 | 0 | 1783.4917 | 87.6925 | 78.25 | 9.4424 | 24.997 | 69.4084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 461.0601 | 458.1701 | 461.6401 | 415.6601 | 444.5901 | 423.5301 | 317.0401 | 0.51751 | 0.48163 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7378616.6905 | 8420023.1722 | 8420023.1722 | 62.4269 | 62.2041 | 1.0017 | 0.99805 | 684935.514 | 890421.7548 | 460.2901 | 0.46058 | 0 | 0 | 30.8514 | 24.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017916 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.1448 | 1368.0343 | 55.4711 | 44.5667 | 30.5995 | 1787.695 | 74.0576 | 25.8394 | 459.5531 | 0.0057732 | 60.0061 | 0.52225 | 2.1657 | 83.4811 | 2.5171 | 0.47024 | 0.37774 | 3.9503 | 3.2373 | 0.22694 | 0 | 100 | 583.2 | 317 | 104.43 | 103.17 | 101.41 | 310.2 | 3 | 89.96 | 42.43 | 4 | 37.64 | 43.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.4 | 0 | 38.44 | 64 | 64 | 98.65 | 86.83 | 79.86 | 0 | 101.41 | 2.2 | 88.87 | 43.22 | 104.43 | 13.23 | 103.19 | 110 | 0 | 15678 | 79.67 | 114.31 | 218.8 | 212.79 | 218.39 | 0 | 29.57 | 50.54 | 12951 | 89.96 | 42.43 | 37.64 | 1.04 | 42.43 | 0 | 606 | 435.4 | 458.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.2 | 316.5 | 0 | 310.2 | 101.43 | 15678 | 15678 | 317
03/26/22 10:26:16.205 | 612.3197 | 1368.3045 | 54.7832 | 44.0692 | 10.714 | 30.712 | 50.884 | 0 | 1781.324 | 87.6984 | 78.2565 | 9.4419 | 24.993 | 69.4093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 461.0601 | 458.1701 | 461.6401 | 415.6601 | 444.5901 | 423.5301 | 317.0401 | 0.51777 | 0.55443 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7374770.3463 | 8409798.8983 | 8409798.8983 | 62.4269 | 62.2041 | 1.0017 | 0.99805 | 684664.031 | 889359.478 | 460.2901 | 0.46058 | 0 | 0 | 30.712 | 24.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017919 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 623.0316 | 1368.0358 | 55.468 | 44.5656 | 30.6061 | 1787.6431 | 74.1196 | 25.8249 | 459.5569 | 0.0057813 | 60.0061 | 0.52228 | 2.1456 | 83.5437 | 2.5171 | 0.47292 | 0.37888 | 3.9723 | 3.2101 | 0.23345 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 104.45 | 13.21 | 103.19 | 110 | 0 | 15676 | 79.69 | 114.31 | 218.8 | 212.9 | 218.5 | 0 | 29.73 | 50.54 | 12955 | 89.98 | 42.44 | 37.65 | 1.02 | 42.44 | 0 | 606 | 432.8 | 458.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.7 | 315.5 | 0 | 309.3 | 101.34 | 15678 | 15676 | 315
03/26/22 10:26:21.205 | 612.6364 | 1368.9083 | 54.7914 | 44.0797 | 10.7117 | 31.019 | 50.8702 | 0 | 1780.0338 | 87.7096 | 78.2702 | 9.4394 | 24.7787 | 69.4588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.004 | 461.13 | 458.22 | 461.71 | 415.41 | 444.5 | 423.19 | 316.87 | 0.51722 | 0.70518 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7378922.0676 | 8400677.4909 | 8400677.4909 | 62.4269 | 62.204 | 1.0017 | 0.99805 | 685177.6874 | 888692.7638 | 460.3533 | 0.46341 | 0 | 0 | 31.019 | 24.7787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017925 | 0.01269 | 0.00479 | 0.011584 | 0.0119 | 622.9167 | 1368.0334 | 55.4647 | 44.5642 | 30.6134 | 1787.6195 | 74.1812 | 25.8093 | 459.5609 | 0.0057901 | 60.006 | 0.5223 | 2.1243 | 83.606 | 2.5171 | 0.47561 | 0.38021 | 3.9971 | 3.1822 | 0.24055 | 0 | 100 | 582.7 | 317 | 104.48 | 103.17 | 101.34 | 310.8 | 3 | 89.99 | 42.44 | 4 | 37.65 | 43.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.48 | 0 | 38.44 | 64 | 64 | 98.7 | 86.84 | 79.94 | 0 | 101.34 | 2.21 | 88.91 | 43.22 | 104.48 | 13.17 | 103.17 | 110 | 0 | 15674 | 79.69 | 114.28 | 218.92 | 212.9 | 218.5 | 0 | 29.57 | 50.48 | 12960 | 89.99 | 42.44 | 37.65 | 1.01 | 42.44 | 0 | 605 | 434.1 | 458.5 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.6 | 316.1 | 0 | 309.8 | 101.32 | 15673 | 15674 | 317
03/26/22 10:26:26.205 | 612.5947 | 1368.9187 | 54.796 | 44.0851 | 10.7109 | 31.0259 | 50.8883 | 0 | 1780.1422 | 87.7164 | 78.2787 | 9.4377 | 25.1689 | 69.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.004 | 461.13 | 458.22 | 461.71 | 415.41 | 444.5 | 423.19 | 316.87 | 0.51726 | 0.7051 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7378428.9633 | 8400194.7656 | 8400194.7656 | 62.4269 | 62.2039 | 1.0017 | 0.99805 | 685182.6416 | 888745.7654 | 460.3533 | 0.46341 | 0 | 0 | 31.0259 | 25.1689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017925 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 622.8077 | 1368.0448 | 55.4611 | 44.5626 | 30.6216 | 1787.5899 | 74.2426 | 25.7936 | 459.565 | 0.0057989 | 60.0059 | 0.52232 | 2.1041 | 83.668 | 2.5182 | 0.47824 | 0.38164 | 4.0336 | 3.1536 | 0.24766 | 0 | 100 | 582.9 | 316 | 104.53 | 103.17 | 101.37 | 310.3 | 3 | 90.02 | 42.46 | 4 | 37.68 | 43.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.5 | 0 | 38.46 | 64 | 64 | 98.75 | 86.87 | 79.96 | 0 | 101.37 | 2.2 | 88.93 | 43.25 | 104.55 | 13.13 | 103.17 | 110 | 0 | 15673 | 79.69 | 114.28 | 218.92 | 212.9 | 218.5 | 0 | 29.71 | 50.59 | 12965 | 90.03 | 42.48 | 37.69 | 0.97 | 42.48 | 0 | 605 | 435.5 | 458.3 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.2 | 317.7 | 0 | 311.4 | 101.43 | 15673 | 15673 | 316
03/26/22 10:26:31.206 | 610.7124 | 1364.7434 | 54.8008 | 44.0901 | 10.7107 | 30.5599 | 50.8881 | 0 | 1784.529 | 87.7237 | 78.287 | 9.4367 | 26.0353 | 69.4386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 461.1301 | 458.2201 | 461.7101 | 415.4101 | 444.5001 | 423.1901 | 316.8701 | 0.51885 | 0.1855 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7355348.8615 | 8420918.6594 | 8420918.6594 | 62.4269 | 62.2038 | 1.0017 | 0.99805 | 683092.5884 | 890934.8386 | 460.3534 | 0.46341 | 0 | 0 | 30.5599 | 26.0353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017915 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 622.6851 | 1368.0235 | 55.4572 | 44.5608 | 30.6247 | 1787.5643 | 74.3038 | 25.7876 | 459.5691 | 0.0058077 | 60.0058 | 0.52235 | 2.0816 | 83.7297 | 2.5298 | 0.48075 | 0.38313 | 4.0383 | 3.1244 | 0.25451 | 0 | 100 | 582.8 | 317 | 104.53 | 103.17 | 101.36 | 307.8 | 3 | 90.01 | 42.49 | 4 | 37.7 | 43.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.48 | 0 | 38.48 | 64 | 64 | 98.7 | 86.83 | 79.94 | 0 | 101.36 | 2.2 | 88.91 | 43.26 | 104.48 | 13.16 | 103.17 | 110 | 0 | 15671 | 79.69 | 114.28 | 218.92 | 213 | 218.62 | 0 | 29.48 | 50.27 | 12970 | 90.01 | 42.49 | 37.7 | 0.96 | 42.49 | 0 | 605 | 433.8 | 458.3 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.8 | 315.5 | 0 | 309.2 | 101.36 | 15672 | 15671 | 317
03/26/22 10:26:36.206 | 610.6682 | 1365.146 | 54.8121 | 44.0996 | 10.7125 | 30.7321 | 50.8855 | 0 | 1789.3391 | 87.7408 | 78.3044 | 9.4364 | 25.2454 | 69.4617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0021 | 461.1201 | 458.1901 | 461.6601 | 415.4401 | 444.4401 | 422.9201 | 316.7901 | 0.51876 | -0.072419 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7354796.7149 | 8441942.6 | 8441942.6 | 62.4268 | 62.2037 | 1.0017 | 0.99805 | 682957.8069 | 893246.6657 | 460.3234 | 0.46344 | 0 | 0 | 30.7321 | 25.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017916 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 622.5565 | 1367.9925 | 55.4529 | 44.5585 | 30.6252 | 1787.5973 | 74.3646 | 25.7848 | 459.5732 | 0.0058166 | 60.0056 | 0.52238 | 2.0555 | 83.791 | 2.539 | 0.48305 | 0.38466 | 4.0268 | 3.0949 | 0.26123 | 0 | 100 | 583.6 | 316 | 104.38 | 103.14 | 101.5 | 309 | 3 | 89.94 | 42.5 | 4 | 37.71 | 43.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.43 | 0 | 38.5 | 64 | 64 | 98.68 | 86.83 | 80.03 | 0 | 101.5 | 2.2 | 88.89 | 43.28 | 104.35 | 13.22 | 103.14 | 110 | 0 | 15670 | 79.69 | 114.28 | 219.04 | 213 | 218.62 | 0 | 29.68 | 50.98 | 12975 | 89.92 | 42.51 | 37.73 | 0.95 | 42.51 | 0 | 605 | 433.3 | 458.3 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.6 | 316 | 0 | 309.7 | 101.5 | 15670 | 15670 | 316
03/26/22 10:26:41.205 | 611.4417 | 1365.5176 | 54.8187 | 44.1047 | 10.7141 | 30.9718 | 50.8863 | 0 | 1787.7959 | 87.751 | 78.3149 | 9.4361 | 24.8214 | 69.4654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.002 | 461.12 | 458.19 | 461.66 | 415.44 | 444.44 | 422.92 | 316.79 | 0.5181 | 0.10959 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7364405.4486 | 8436087.3976 | 8436087.3976 | 62.4268 | 62.2036 | 1.0017 | 0.99805 | 683727.3489 | 892696.7947 | 460.3233 | 0.46344 | 0 | 0 | 30.9718 | 24.8214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017913 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 622.4422 | 1367.9904 | 55.4482 | 44.5558 | 30.6315 | 1787.6352 | 74.425 | 25.7726 | 459.5771 | 0.0058252 | 60.0055 | 0.52239 | 2.0314 | 83.8519 | 2.5408 | 0.4851 | 0.38614 | 3.9961 | 3.065 | 0.26713 | 0 | 100 | 583.2 | 314 | 104.53 | 103.14 | 101.43 | 308.4 | 3 | 90.02 | 42.54 | 4 | 37.75 | 43.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.6 | 0 | 38.51 | 64 | 64 | 98.88 | 86.93 | 79.99 | 0 | 101.43 | 2.2 | 88.98 | 43.31 | 104.58 | 13.1 | 103.14 | 110 | 0 | 15668 | 79.69 | 114.33 | 219.04 | 213 | 218.62 | 0 | 30.25 | 51.59 | 12980 | 90.05 | 42.53 | 37.73 | 0.98 | 42.53 | 0 | 605 | 434.9 | 458.3 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.2 | 315.8 | 0 | 309.5 | 101.43 | 15671 | 15668 | 318
03/26/22 10:26:46.206 | 610.0289 | 1363.8041 | 54.8203 | 44.1142 | 10.7061 | 30.1914 | 50.8879 | 0 | 1788.1572 | 87.769 | 78.3448 | 9.4242 | 26.1197 | 69.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0051 | 461.1201 | 458.1601 | 461.6201 | 414.6901 | 443.5001 | 421.8801 | 316.0901 | 0.51816 | -0.019171 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7346805.004 | 8426963.8075 | 8426963.8075 | 62.4268 | 62.2033 | 1.0017 | 0.99805 | 682621.5486 | 892738.6878 | 460.3001 | 0.46491 | 0 | 0 | 30.1914 | 26.1197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017914 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 622.3196 | 1367.9787 | 55.4433 | 44.553 | 30.6391 | 1787.6666 | 74.4854 | 25.7602 | 459.581 | 0.0058336 | 60.0054 | 0.52241 | 2.0074 | 83.9127 | 2.5553 | 0.48698 | 0.38751 | 3.9778 | 3.0342 | 0.27251 | 0 | 100 | 577.8 | 317 | 104.95 | 103.19 | 100.49 | 306.7 | 3 | 90.25 | 42.31 | 4 | 37.54 | 43.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.98 | 0 | 38.31 | 64 | 64 | 99.23 | 87.12 | 80.06 | 0 | 100.49 | 2.22 | 89.19 | 43.11 | 104.95 | 12.94 | 103.19 | 110 | 0 | 15667 | 79.69 | 114.33 | 219.04 | 213.11 | 218.73 | 0 | 30.36 | 51.18 | 12986 | 90.25 | 42.3 | 37.51 | 1.22 | 42.3 | 0 | 605 | 428.2 | 458.4 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 312.9 | 0 | 306.7 | 100.49 | 15669 | 15667 | 317
03/26/22 10:26:51.206 | 610.3515 | 1365.9305 | 54.8132 | 44.1181 | 10.6951 | 30.8134 | 50.8948 | 0 | 1788.6888 | 87.7761 | 78.3635 | 9.4126 | 25.2404 | 69.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.005 | 461.12 | 458.16 | 461.62 | 414.69 | 443.5 | 421.88 | 316.09 | 0.51788 | 0.13957 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7351264.4725 | 8418050.4642 | 8418050.4642 | 62.4268 | 62.2032 | 1.0017 | 0.99805 | 683686.1673 | 893001.6281 | 460.3 | 0.46491 | 0 | 0 | 30.8134 | 25.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017912 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 622.1839 | 1367.9495 | 55.438 | 44.5498 | 30.6478 | 1787.6582 | 74.5454 | 25.7458 | 459.5848 | 0.0058418 | 60.0053 | 0.52242 | 1.9848 | 83.9731 | 2.5485 | 0.4886 | 0.38872 | 3.974 | 3.0031 | 0.27772 | 0 | 100 | 576 | 317 | 105.13 | 103.26 | 100.17 | 307.8 | 3 | 90.34 | 42.14 | 4 | 37.35 | 43.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 103.18 | 0 | 38.14 | 64 | 64 | 99.4 | 87.22 | 80.15 | 0 | 100.17 | 2.23 | 89.29 | 42.94 | 105.15 | 12.91 | 103.26 | 110 | 0 | 15667 | 79.69 | 114.31 | 219.16 | 213.11 | 218.73 | 0 | 30.21 | 50.51 | 12990 | 90.34 | 42.14 | 37.35 | 1.29 | 42.14 | 0 | 605 | 427.7 | 458.6 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 311.6 | 0 | 305.4 | 100.17 | 15668 | 15667 | 315
03/26/22 10:26:56.205 | 606.9932 | 1365.4195 | 54.7684 | 44.1282 | 10.6402 | 31.4501 | 50.8954 | 0 | 1786.0825 | 87.8041 | 78.4438 | 9.3602 | 23.9929 | 69.4456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0061 | 461.1301 | 458.1501 | 461.6201 | 414.0901 | 442.8201 | 421.1201 | 315.5801 | 0.51991 | 0.36621 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7311512.9007 | 8357653.0831 | 8357653.0831 | 62.4269 | 62.2026 | 1.0017 | 0.99804 | 683432.4985 | 891689.9487 | 460.3001 | 0.46709 | 0 | 0 | 31.4501 | 23.9929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017921 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 622.0402 | 1367.9213 | 55.4323 | 44.5464 | 30.6554 | 1787.6558 | 74.6054 | 25.7299 | 459.5887 | 0.0058501 | 60.0053 | 0.52244 | 1.9624 | 84.0332 | 2.5435 | 0.4901 | 0.38976 | 3.9731 | 2.9713 | 0.28278 | 0 | 100 | 575.6 | 317 | 105.35 | 103.31 | 100.1 | 304.1 | 3 | 90.45 | 42.08 | 4 | 37.29 | 43.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 103.45 | 0 | 38.07 | 64 | 64 | 99.63 | 87.36 | 80.32 | 0 | 100.1 | 2.24 | 89.44 | 42.86 | 105.38 | 12.86 | 103.34 | 110 | 0 | 15667 | 79.69 | 114.26 | 219.16 | 213.11 | 218.73 | 0 | 29.87 | 49.94 | 12995 | 90.47 | 42.08 | 37.29 | 1.25 | 42.08 | 0 | 606 | 427.2 | 458.9 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.2 | 311 | 0 | 304.7 | 100.03 | 15666 | 15667 | 314
03/26/22 10:27:01.205 | 606.1921 | 1367.2723 | 54.7406 | 44.129 | 10.6115 | 31.4985 | 50.8921 | 0 | 1783.7188 | 87.8193 | 78.4861 | 9.3332 | 23.9867 | 69.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0061 | 461.1301 | 458.1501 | 461.6201 | 414.0901 | 442.8201 | 421.1201 | 315.5801 | 0.52059 | 0.56765 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7301979.6098 | 8331355.3915 | 8331355.3915 | 62.4269 | 62.2024 | 1.0017 | 0.99804 | 684076.8064 | 891036.0205 | 460.3001 | 0.46709 | 0 | 0 | 31.4985 | 23.9867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017929 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 621.88 | 1367.9019 | 55.4259 | 44.5427 | 30.6605 | 1787.642 | 74.6654 | 25.716 | 459.5925 | 0.0058584 | 60.0052 | 0.52248 | 1.9408 | 84.093 | 2.5349 | 0.49156 | 0.39051 | 3.9825 | 2.9396 | 0.28771 | 0 | 100 | 574.3 | 317 | 105.6 | 103.38 | 99.88 | 304.1 | 3 | 90.59 | 42.01 | 4 | 37.23 | 43.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 103.75 | 0 | 38 | 64 | 64 | 99.9 | 87.51 | 80.43 | 0 | 99.88 | 2.25 | 89.59 | 42.79 | 105.6 | 12.82 | 103.41 | 110 | 0 | 15668 | 79.69 | 114.23 | 219.16 | 213.11 | 218.73 | 0 | 29.75 | 49.76 | 13000 | 90.59 | 42.01 | 37.23 | 1.3 | 42.01 | 0 | 606 | 424.1 | 459.1 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574.2 | 312.1 | 0 | 305.8 | 99.86 | 15669 | 15668 | 317
03/26/22 10:27:06.205 | 603.1711 | 1369.2232 | 54.6637 | 44.1201 | 10.5436 | 31.7474 | 50.8807 | 0 | 1777.0508 | 87.8625 | 78.5937 | 9.2688 | 23.8782 | 69.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.019 | 461.22 | 458.3 | 461.71 | 411.9 | 440.58 | 419.04 | 313.96 | 0.52052 | 1.2655 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7265986.9167 | 8234103.05 | 8234103.05 | 62.427 | 62.2016 | 1.0017 | 0.99804 | 685341.1875 | 887161.3909 | 460.41 | 0.45829 | 0 | 0 | 31.7474 | 23.8782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017939 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 621.7198 | 1367.9069 | 55.4188 | 44.5385 | 30.6686 | 1787.5664 | 74.7253 | 25.702 | 459.5969 | 0.005868 | 60.0054 | 0.5225 | 1.9258 | 84.1524 | 2.5341 | 0.49293 | 0.39092 | 4.0039 | 2.9082 | 0.29369 | 0 | 100 | 574.1 | 315 | 105.78 | 103.48 | 99.84 | 302.2 | 3 | 90.68 | 41.95 | 4 | 37.16 | 43.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 103.9 | 0 | 37.93 | 64 | 64 | 100.05 | 87.59 | 80.7 | 0 | 99.84 | 2.25 | 89.68 | 42.71 | 105.78 | 12.8 | 103.48 | 110 | 0 | 15678 | 79.71 | 114.19 | 219.16 | 213.21 | 218.73 | 0 | 29.61 | 49.56 | 13005 | 90.68 | 41.95 | 37.16 | 1.48 | 41.95 | 0 | 606 | 427.9 | 459 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574.2 | 309.7 | 0 | 303.5 | 99.86 | 15675 | 15678 | 316
03/26/22 10:27:11.205 | 600.3684 | 1369.9199 | 54.5939 | 44.1047 | 10.4891 | 31.3486 | 50.8782 | 0 | 1779.2493 | 87.9053 | 78.6868 | 9.2185 | 24.6926 | 69.5117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.02 | 461.25 | 458.34 | 461.76 | 411.24 | 439.94 | 418.48 | 313.51 | 0.5222 | 1.2457 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7232016.7668 | 8200497.8488 | 8200497.8488 | 62.4272 | 62.2009 | 1.0017 | 0.99804 | 685693.1338 | 888246.8049 | 460.45 | 0.45825 | 0 | 0 | 31.3486 | 24.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017936 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 621.5627 | 1367.9171 | 55.4114 | 44.5339 | 30.6703 | 1787.5024 | 74.7848 | 25.6948 | 459.6016 | 0.0058781 | 60.0056 | 0.5225 | 1.9102 | 84.2115 | 2.5363 | 0.4943 | 0.39096 | 4.0806 | 2.8771 | 0.29986 | 0 | 100 | 575.7 | 316 | 105.93 | 103.53 | 100 | 307.1 | 3 | 90.76 | 41.93 | 4 | 37.14 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104 | 0 | 37.9 | 64 | 64 | 100.13 | 87.63 | 80.83 | 0 | 100 | 2.26 | 89.74 | 42.69 | 105.9 | 12.78 | 103.53 | 110 | 0 | 15686 | 79.73 | 114.16 | 219.16 | 213.21 | 218.73 | 0 | 29.46 | 49.4 | 13010 | 90.75 | 41.91 | 37.13 | 1.73 | 41.91 | 0 | 605 | 428.4 | 458.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7 | 313.4 | 0 | 307.1 | 100.12 | 15686 | 15686 | 317
03/26/22 10:27:16.205 | 598.0863 | 1369.4451 | 54.53 | 44.0863 | 10.4437 | 31.2382 | 50.8776 | 0 | 1784.1316 | 87.9472 | 78.7696 | 9.1777 | 24.9269 | 69.5178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.018 | 461.28 | 458.39 | 461.82 | 410.51 | 439.24 | 417.81 | 313.02 | 0.52337 | 1.0322 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7204702.7838 | 8189475.392 | 8189475.392 | 62.4273 | 62.2004 | 1.0017 | 0.99804 | 685488.8371 | 890242.5684 | 460.4967 | 0.45748 | 0 | 0 | 31.2382 | 24.9269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017931 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 621.3891 | 1367.9319 | 55.4033 | 44.5288 | 30.6739 | 1787.4909 | 74.8446 | 25.6884 | 459.6065 | 0.0058888 | 60.0058 | 0.52252 | 1.8923 | 84.2706 | 2.5378 | 0.49653 | 0.39084 | 4.0896 | 2.8467 | 0.30644 | 0 | 100 | 575.4 | 313 | 105.98 | 103.55 | 100.07 | 305.2 | 3 | 90.78 | 41.9 | 4 | 37.11 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.08 | 0 | 37.88 | 64 | 64 | 100.2 | 87.67 | 81.01 | 0 | 100.07 | 2.26 | 89.78 | 42.66 | 105.98 | 12.76 | 103.55 | 110 | 0 | 15686 | 79.75 | 114.14 | 219.16 | 213.21 | 218.73 | 0 | 29.44 | 49.68 | 13015 | 90.79 | 41.9 | 37.1 | 1.73 | 41.9 | 0 | 606 | 426.3 | 458.9 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.4 | 312.1 | 0 | 305.9 | 100.07 | 15685 | 15686 | 317
03/26/22 10:27:21.205 | 593.9086 | 1367.1433 | 54.4425 | 44.057 | 10.3855 | 31.4634 | 50.8758 | 0 | 1790.0668 | 88.007 | 78.8803 | 9.1267 | 24.502 | 69.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0141 | 461.3001 | 458.4301 | 461.8701 | 410.2101 | 439.0201 | 417.6201 | 312.8601 | 0.52678 | 0.63651 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7154503.2115 | 8170399.9799 | 8170399.9799 | 62.4274 | 62.1996 | 1.0017 | 0.99803 | 684487.8999 | 893129.2484 | 460.5334 | 0.45672 | 0 | 0 | 31.4634 | 24.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017928 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 621.2094 | 1367.9456 | 55.3947 | 44.5235 | 30.6774 | 1787.5111 | 74.9045 | 25.6805 | 459.6117 | 0.0058999 | 60.0059 | 0.52253 | 1.8725 | 84.3297 | 2.5287 | 0.49953 | 0.39059 | 4.0884 | 2.817 | 0.31352 | 0 | 100 | 575.1 | 318 | 105.9 | 103.58 | 100.02 | 307 | 3 | 90.75 | 41.88 | 4 | 37.09 | 43.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.08 | 0 | 37.85 | 64 | 64 | 100.2 | 87.67 | 81.2 | 0 | 100.02 | 2.26 | 89.78 | 42.64 | 105.93 | 12.84 | 103.6 | 110 | 0 | 15690 | 79.77 | 114.19 | 219.16 | 213.21 | 218.85 | 0 | 29.74 | 50.19 | 13020 | 90.76 | 41.86 | 37.08 | 1.67 | 41.86 | 0 | 606 | 428.6 | 458.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574.7 | 309.7 | 0 | 303.5 | 99.95 | 15690 | 15690 | 315
03/26/22 10:27:26.204 | 587.7738 | 1364.1602 | 54.3223 | 44.0105 | 10.3118 | 31.4453 | 50.882 | 0 | 1790.0565 | 88.0926 | 79.0282 | 9.0644 | 24.8742 | 69.4943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 461.3 | 458.43 | 461.87 | 410.21 | 439.02 | 417.62 | 312.86 | 0.53228 | 0.43963 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7080850.5234 | 8112628.7417 | 8112628.7417 | 62.4277 | 62.1983 | 1.0017 | 0.99803 | 682822.5923 | 893596.9014 | 460.5334 | 0.45672 | 0 | 0 | 31.4453 | 24.8742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017924 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 621.0445 | 1367.94 | 55.3859 | 44.5177 | 30.6789 | 1787.5434 | 74.9637 | 25.6746 | 459.617 | 0.0059114 | 60.0061 | 0.52252 | 1.8507 | 84.3883 | 2.5345 | 0.50348 | 0.3901 | 4.0878 | 2.7893 | 0.32095 | 0 | 100 | 575.6 | 316 | 105.9 | 103.6 | 100.1 | 306.4 | 3 | 90.75 | 41.86 | 4 | 37.08 | 43.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.13 | 0 | 37.85 | 64 | 64 | 100.18 | 87.66 | 81.33 | 0 | 100.1 | 2.26 | 89.8 | 42.64 | 105.93 | 12.84 | 103.6 | 110 | 0 | 15694 | 79.8 | 114.21 | 219.16 | 213.21 | 218.85 | 0 | 29.92 | 50.31 | 13026 | 90.76 | 41.88 | 37.09 | 1.74 | 41.88 | 0 | 606 | 428.7 | 458.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 313 | 0 | 306.7 | 100.28 | 15694 | 15694 | 316
03/26/22 10:27:31.205 | 585.1529 | 1365.4298 | 54.2232 | 43.9671 | 10.2561 | 30.8169 | 50.89 | 0 | 1790.4074 | 88.1678 | 79.1493 | 9.0185 | 25.8314 | 69.5055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.007 | 461.3 | 458.47 | 461.93 | 410.29 | 439.14 | 417.87 | 312.99 | 0.53489 | 0.52127 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7048874.5932 | 8074198.4809 | 8074198.4809 | 62.4279 | 62.1973 | 1.0017 | 0.99803 | 683462.5639 | 893756.0134 | 460.5667 | 0.45524 | 0 | 0 | 30.8169 | 25.8314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017918 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 620.8627 | 1367.9383 | 55.3765 | 44.5115 | 30.6756 | 1787.5736 | 75.0233 | 25.6788 | 459.6223 | 0.0059229 | 60.0062 | 0.52253 | 1.8289 | 84.4471 | 2.5361 | 0.5093 | 0.38992 | 4.0888 | 2.7632 | 0.32812 | 0 | 100 | 575.7 | 317 | 105.98 | 103.58 | 100.12 | 306.2 | 3 | 90.79 | 41.86 | 4 | 37.08 | 43.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.15 | 0 | 37.85 | 64 | 64 | 100.25 | 87.7 | 81.56 | 0 | 100.12 | 2.26 | 89.82 | 42.65 | 105.98 | 12.79 | 103.58 | 110 | 0 | 15694 | 79.82 | 114.23 | 219.16 | 213.21 | 218.85 | 0 | 29.91 | 50.19 | 13031 | 90.79 | 41.88 | 37.08 | 1.78 | 41.88 | 0 | 606 | 429.5 | 458.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 311.8 | 0 | 305.6 | 100.19 | 15691 | 15694 | 316
03/26/22 10:27:36.205 | 584.5172 | 1367.8091 | 54.1623 | 43.9353 | 10.227 | 31.1635 | 50.8962 | 0 | 1791.8009 | 88.2205 | 79.2249 | 8.9956 | 24.9024 | 69.5013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 461.3001 | 458.4701 | 461.9301 | 410.2901 | 439.1401 | 417.8701 | 312.9901 | 0.53547 | 0.627 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7041598.1297 | 8058876.3081 | 8058876.3081 | 62.428 | 62.1966 | 1.0017 | 0.99803 | 684656.2152 | 894441.5691 | 460.5668 | 0.45524 | 0 | 0 | 31.1635 | 24.9024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017924 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 620.6899 | 1367.9368 | 55.3671 | 44.5051 | 30.6758 | 1787.608 | 75.0824 | 25.6749 | 459.628 | 0.0059352 | 60.0063 | 0.52252 | 1.8068 | 84.5055 | 2.536 | 0.51599 | 0.3899 | 4.0982 | 2.7385 | 0.33552 | 0 | 100 | 576.1 | 317 | 106 | 103.58 | 100.14 | 306.2 | 3 | 90.8 | 41.86 | 4 | 37.08 | 43.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.15 | 0 | 37.85 | 64 | 64 | 100.25 | 87.7 | 81.66 | 0 | 100.14 | 2.26 | 89.82 | 42.64 | 106 | 12.77 | 103.58 | 110 | 0 | 15694 | 79.84 | 114.26 | 219.16 | 213.21 | 218.85 | 0 | 29.86 | 50.01 | 13035 | 90.8 | 41.86 | 37.06 | 1.68 | 41.86 | 0 | 606 | 428.6 | 458.8 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 312.3 | 0 | 306.1 | 100.23 | 15693 | 15694 | 316
03/26/22 10:27:41.204 | 583.7167 | 1369.7909 | 54.0889 | 43.8909 | 10.198 | 31.002 | 50.9005 | 0 | 1787.9765 | 88.2918 | 79.3175 | 8.9743 | 24.9224 | 69.4827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.005 | 461.28 | 458.45 | 461.93 | 410.4 | 439.3 | 418.04 | 313.12 | 0.53642 | 0.95832 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7031889.2711 | 8022602.7789 | 8022602.7789 | 62.4282 | 62.1958 | 1.0018 | 0.99802 | 685651.5028 | 892520.1882 | 460.5534 | 0.4567 | 0 | 0 | 31.002 | 24.9224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017917 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 620.5418 | 1367.9516 | 55.358 | 44.4987 | 30.6755 | 1787.6105 | 75.1404 | 25.6701 | 459.6334 | 0.0059469 | 60.0063 | 0.52247 | 1.7862 | 84.5632 | 2.5391 | 0.52395 | 0.39043 | 4.0983 | 2.7167 | 0.34252 | 0 | 100 | 576 | 315 | 106.1 | 103.55 | 100.17 | 307.8 | 3 | 90.86 | 41.85 | 4 | 37.06 | 43.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.2 | 0 | 37.84 | 64 | 64 | 100.28 | 87.71 | 81.86 | 0 | 100.17 | 2.26 | 89.84 | 42.63 | 106.13 | 12.7 | 103.55 | 110 | 0 | 15694 | 79.84 | 114.26 | 219.16 | 213.21 | 218.85 | 0 | 29.87 | 50.1 | 13040 | 90.86 | 41.85 | 37.06 | 1.52 | 41.85 | 0 | 606 | 427.7 | 458.7 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 314 | 0 | 307.8 | 100.17 | 15693 | 15694 | 315
03/26/22 10:27:46.205 | 582.0115 | 1368.6245 | 53.9857 | 43.8129 | 10.1728 | 31.2263 | 50.8743 | 0 | 1792.8795 | 88.409 | 79.4503 | 8.9588 | 25.1036 | 69.4968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.999 | 461.31 | 458.46 | 461.96 | 410.8 | 439.64 | 418.31 | 313.43 | 0.53853 | 0.62535 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7011626.0065 | 8030410.3591 | 8030410.3591 | 62.4284 | 62.1947 | 1.0018 | 0.99802 | 685208.7387 | 894835.7128 | 460.5767 | 0.45957 | 0 | 0 | 31.2263 | 25.1036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017911 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 620.394 | 1367.9599 | 55.3486 | 44.492 | 30.6759 | 1787.6443 | 75.1984 | 25.6666 | 459.6388 | 0.0059585 | 60.0063 | 0.52243 | 1.763 | 84.6208 | 2.5397 | 0.53313 | 0.3917 | 4.1147 | 2.6963 | 0.34919 | 0 | 100 | 576 | 315 | 106.03 | 103.58 | 100.17 | 303.8 | 3 | 90.8 | 41.85 | 4 | 37.06 | 43.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.17 | 0 | 37.84 | 64 | 64 | 100.23 | 87.7 | 81.94 | 0 | 100.17 | 2.26 | 89.83 | 42.63 | 106.03 | 12.76 | 103.58 | 110 | 0 | 15694 | 79.84 | 114.28 | 219.16 | 213.21 | 218.85 | 0 | 29.98 | 50.28 | 13045 | 90.82 | 41.85 | 37.06 | 1.42 | 41.85 | 0 | 606 | 428.3 | 458.9 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 314.5 | 0 | 308.2 | 100.19 | 15693 | 15694 | 318
03/26/22 10:27:51.204 | 581.7934 | 1369.4038 | 53.9341 | 43.7672 | 10.1669 | 31.1573 | 50.8693 | 0 | 1791.2589 | 88.4761 | 79.5167 | 8.9594 | 25.1299 | 69.5096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.999 | 461.31 | 458.46 | 461.96 | 410.8 | 439.64 | 418.31 | 313.43 | 0.53873 | 0.67631 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7008939.1721 | 8023955.4216 | 8023955.4216 | 62.4286 | 62.1939 | 1.0018 | 0.99802 | 685464.6607 | 894132.0623 | 460.5767 | 0.45957 | 0 | 0 | 31.1573 | 25.1299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.01792 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 620.2646 | 1367.9804 | 55.3395 | 44.4853 | 30.6784 | 1787.6708 | 75.2557 | 25.6605 | 459.6445 | 0.005971 | 60.0062 | 0.52236 | 1.7403 | 84.678 | 2.5364 | 0.54318 | 0.39378 | 4.1225 | 2.6777 | 0.35603 | 0 | 100 | 576.1 | 316 | 106.05 | 103.58 | 100.19 | 304 | 3 | 90.83 | 41.84 | 4 | 37.05 | 43.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.2 | 0 | 37.84 | 64 | 64 | 100.23 | 87.69 | 82.1 | 0 | 100.19 | 2.26 | 89.84 | 42.63 | 106.05 | 12.75 | 103.58 | 110 | 0 | 15694 | 79.84 | 114.28 | 219.16 | 213.21 | 218.73 | 0 | 30.16 | 50.46 | 13050 | 90.83 | 41.84 | 37.05 | 1.37 | 41.84 | 0 | 606 | 428.8 | 458.9 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 313.6 | 0 | 307.3 | 100.19 | 15694 | 15694 | 317
03/26/22 10:27:56.204 | 582.1388 | 1370.4773 | 53.8685 | 43.7037 | 10.1648 | 30.0125 | 50.922 | 0 | 1790.3661 | 88.5706 | 79.6024 | 8.9683 | 26.4529 | 69.5112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9951 | 461.3301 | 458.4801 | 461.9801 | 410.8501 | 439.7401 | 418.3901 | 313.4801 | 0.5385 | 0.6512 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7012097.4901 | 8029278.2487 | 8029278.2487 | 62.4288 | 62.1929 | 1.0018 | 0.99802 | 686004.8903 | 893674.8865 | 460.5968 | 0.45955 | 0 | 0 | 30.0125 | 26.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017907 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 620.1511 | 1368.0009 | 55.3313 | 44.4793 | 30.6813 | 1787.6793 | 75.3112 | 25.655 | 459.6506 | 0.0059841 | 60.0062 | 0.52227 | 1.7177 | 84.7337 | 2.5431 | 0.55364 | 0.39684 | 4.1226 | 2.6627 | 0.36287 | 0 | 100 | 576.1 | 316 | 106.1 | 103.58 | 100.19 | 306.5 | 3 | 90.86 | 41.84 | 4 | 37.05 | 43.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.23 | 0 | 37.82 | 64 | 64 | 100.23 | 87.7 | 82.29 | 0 | 100.19 | 2.26 | 89.86 | 42.61 | 106.08 | 12.74 | 103.58 | 110 | 0 | 15694 | 79.86 | 114.31 | 219.16 | 213.21 | 218.73 | 0 | 30.23 | 50.33 | 13055 | 90.86 | 41.84 | 37.05 | 1.3 | 41.84 | 0 | 606 | 428.8 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 313.7 | 0 | 307.5 | 100.21 | 15693 | 15694 | 316
03/26/22 10:28:01.204 | 581.4749 | 1368.6761 | 53.8381 | 43.6717 | 10.1664 | 29.8882 | 50.9214 | 0 | 1793.2046 | 88.6185 | 79.6425 | 8.976 | 26.4481 | 69.5695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.989 | 461.42 | 458.55 | 462.04 | 410.98 | 439.93 | 418.51 | 313.62 | 0.53935 | 0.30715 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7003985.9836 | 8048864.1712 | 8048864.1712 | 62.4289 | 62.1925 | 1.0018 | 0.99801 | 685104.642 | 895086.3941 | 460.67 | 0.4602 | 0 | 0 | 29.8882 | 26.4481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.0179 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 620.034 | 1368.0118 | 55.3232 | 44.4733 | 30.6796 | 1787.6793 | 75.366 | 25.6534 | 459.6567 | 0.0059972 | 60.0061 | 0.52219 | 1.6944 | 84.7888 | 2.5434 | 0.56462 | 0.40081 | 4.1227 | 2.6493 | 0.36948 | 0 | 100 | 575.7 | 318 | 106 | 103.6 | 100.12 | 308.1 | 3 | 90.8 | 41.84 | 4 | 37.05 | 43.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.13 | 0 | 37.82 | 64 | 64 | 100.1 | 87.62 | 82.39 | 0 | 100.12 | 2.26 | 89.8 | 42.61 | 106 | 12.8 | 103.6 | 110 | 0 | 15694 | 79.86 | 114.31 | 219.16 | 213.21 | 218.73 | 0 | 30.05 | 49.98 | 13060 | 90.8 | 41.84 | 37.05 | 1.28 | 41.84 | 0 | 606 | 429.3 | 459.3 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 313.3 | 0 | 307 | 100.19 | 15691 | 15694 | 317
03/26/22 10:28:06.204 | 581.5739 | 1368.6348 | 53.8078 | 43.6378 | 10.17 | 30.4588 | 50.9045 | 0 | 1795.4497 | 88.6692 | 79.6825 | 8.9867 | 25.571 | 69.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.989 | 461.42 | 458.55 | 462.04 | 410.98 | 439.93 | 418.51 | 313.62 | 0.53926 | 0.15069 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7005666.1319 | 8063621.0253 | 8063621.0253 | 62.4289 | 62.1921 | 1.0018 | 0.99801 | 685033.3667 | 896014.7236 | 460.67 | 0.4602 | 0 | 0 | 30.4588 | 25.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017891 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 619.9146 | 1368.0265 | 55.3154 | 44.4678 | 30.6814 | 1787.7043 | 75.4202 | 25.6481 | 459.6636 | 0.0060123 | 60.0061 | 0.52209 | 1.6699 | 84.8431 | 2.5393 | 0.57576 | 0.40542 | 4.1561 | 2.6373 | 0.37668 | 0 | 100 | 576.3 | 317 | 105.95 | 103.6 | 100.23 | 306.9 | 3 | 90.76 | 41.84 | 4 | 37.05 | 43.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.13 | 0 | 37.82 | 64 | 64 | 100.08 | 87.6 | 82.5 | 0 | 100.23 | 2.26 | 89.8 | 42.61 | 105.95 | 12.82 | 103.6 | 110 | 0 | 15694 | 79.88 | 114.33 | 219.16 | 213.21 | 218.73 | 0 | 30.06 | 50.13 | 13065 | 90.78 | 41.84 | 37.05 | 1.31 | 41.84 | 0 | 606 | 429.1 | 459.4 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.7 | 311.2 | 0 | 305 | 100.3 | 15694 | 15694 | 316
03/26/22 10:28:11.204 | 580.9933 | 1366.0853 | 53.769 | 43.5919 | 10.1771 | 30.4849 | 50.8949 | 0 | 1792.0021 | 88.7371 | 79.7332 | 9.0039 | 25.7365 | 69.5348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 461.45 | 458.59 | 462.08 | 410.98 | 440 | 418.56 | 313.7 | 0.53994 | 0.019162 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6998680.6695 | 8067420.6409 | 8067420.6409 | 62.4291 | 62.1914 | 1.0018 | 0.99801 | 683810.8076 | 894473.9563 | 460.7067 | 0.45944 | 0 | 0 | 30.4849 | 25.7365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017896 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 619.7869 | 1368.0339 | 55.3077 | 44.4624 | 30.685 | 1787.7476 | 75.474 | 25.6404 | 459.6708 | 0.0060277 | 60.006 | 0.522 | 1.6437 | 84.8971 | 2.5366 | 0.58677 | 0.41022 | 4.2029 | 2.6252 | 0.3838 | 0 | 100 | 576.7 | 318 | 106.03 | 103.58 | 100.3 | 308.1 | 3 | 90.82 | 41.84 | 4 | 37.05 | 43.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.15 | 0 | 37.82 | 64 | 64 | 100.1 | 87.62 | 82.63 | 0 | 100.3 | 2.26 | 89.82 | 42.61 | 106.03 | 12.76 | 103.58 | 110 | 0 | 15694 | 79.9 | 114.35 | 219.16 | 213.21 | 218.73 | 0 | 30.31 | 50.45 | 13070 | 90.82 | 41.84 | 37.05 | 1.25 | 41.84 | 0 | 606 | 430.6 | 459 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 313.8 | 0 | 307.5 | 100.35 | 15693 | 15694 | 317
03/26/22 10:28:16.205 | 582.5958 | 1369.409 | 53.7519 | 43.5716 | 10.1803 | 30.7291 | 50.9024 | 0 | 1792.0692 | 88.7666 | 79.7546 | 9.012 | 25.3461 | 69.5587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 461.45 | 458.59 | 462.08 | 410.98 | 440 | 418.56 | 313.7 | 0.53845 | 0.17481 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7018190.9001 | 8074452.0862 | 8074452.0862 | 62.4291 | 62.1912 | 1.0018 | 0.99801 | 685475.2803 | 894504.5651 | 460.7067 | 0.45944 | 0 | 0 | 30.7291 | 25.3461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017893 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 619.6416 | 1368.0524 | 55.3004 | 44.4578 | 30.6882 | 1787.7553 | 75.5266 | 25.6327 | 459.6781 | 0.0060435 | 60.006 | 0.52191 | 1.6203 | 84.9494 | 2.5345 | 0.59786 | 0.41554 | 4.2096 | 2.6156 | 0.3909 | 0 | 100 | 576.6 | 317 | 105.95 | 103.55 | 100.28 | 306.9 | 3 | 90.78 | 41.84 | 4 | 37.05 | 42.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.1 | 0 | 37.82 | 64 | 64 | 100.02 | 87.58 | 82.8 | 0 | 100.28 | 2.26 | 89.79 | 42.61 | 105.95 | 12.78 | 103.55 | 110 | 0 | 15694 | 79.9 | 114.38 | 219.16 | 213.21 | 218.73 | 0 | 30.53 | 50.68 | 13075 | 90.78 | 41.84 | 37.05 | 1.16 | 41.84 | 0 | 606 | 428.9 | 459 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 313.2 | 0 | 306.9 | 100.28 | 15694 | 15694 | 317
03/26/22 10:28:21.204 | 582.0508 | 1366.6065 | 53.737 | 43.5541 | 10.1828 | 30.628 | 50.8968 | 0 | 1791.4705 | 88.7919 | 79.7723 | 9.0196 | 25.6869 | 69.6066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9921 | 461.5001 | 458.6501 | 462.1301 | 410.9601 | 440.0301 | 418.6001 | 313.7401 | 0.53903 | 0.061172 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7011783.2517 | 8077365.4844 | 8077365.4844 | 62.4292 | 62.191 | 1.0018 | 0.99801 | 684711.0567 | 894319.9629 | 460.7601 | 0.45794 | 0 | 0 | 30.628 | 25.6869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.01789 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 619.4878 | 1368.064 | 55.2933 | 44.4535 | 30.6857 | 1787.7524 | 75.5787 | 25.6328 | 459.6859 | 0.0060603 | 60.006 | 0.52184 | 1.5975 | 85.0011 | 2.523 | 0.60879 | 0.42085 | 4.2068 | 2.6062 | 0.3984 | 0 | 100 | 576.8 | 315 | 105.9 | 103.55 | 100.31 | 303.3 | 3 | 90.74 | 41.85 | 4 | 37.06 | 42.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.13 | 0 | 37.82 | 64 | 64 | 100 | 87.56 | 83.01 | 0 | 100.3 | 2.26 | 89.8 | 42.61 | 105.9 | 12.82 | 103.55 | 110 | 0 | 15694 | 79.9 | 114.4 | 219.16 | 213.21 | 218.62 | 0 | 30.8 | 50.96 | 13080 | 90.74 | 41.85 | 37.06 | 1.08 | 41.85 | 0 | 606 | 428.4 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 312.5 | 0 | 306.3 | 100.28 | 15693 | 15694 | 317
03/26/22 10:28:26.204 | 582.263 | 1367.7729 | 53.7163 | 43.5298 | 10.1866 | 31.4721 | 50.9179 | 0 | 1790.8461 | 88.8282 | 79.7958 | 9.0324 | 24.6923 | 69.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.998 | 461.53 | 458.7 | 462.18 | 410.89 | 440.07 | 418.71 | 313.78 | 0.5389 | -0.010192 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7014818.1466 | 8086303.7811 | 8086303.7811 | 62.4292 | 62.1907 | 1.0018 | 0.99801 | 684657.8996 | 893888.5011 | 460.8034 | 0.45645 | 0 | 0 | 31.4721 | 24.6923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017891 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 619.3106 | 1368.0779 | 55.2862 | 44.4498 | 30.6909 | 1787.7845 | 75.63 | 25.6241 | 459.694 | 0.006078 | 60.006 | 0.52178 | 1.5732 | 85.0517 | 2.5168 | 0.6196 | 0.42607 | 4.2137 | 2.5977 | 0.40613 | 0 | 100 | 577.2 | 317 | 105.93 | 103.53 | 100.38 | 308.1 | 3 | 90.76 | 41.85 | 4 | 37.06 | 42.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.1 | 0 | 37.84 | 64 | 64 | 100.02 | 87.58 | 83.19 | 0 | 100.28 | 2.26 | 89.79 | 42.63 | 105.9 | 12.78 | 103.53 | 110 | 0 | 15694 | 79.92 | 114.45 | 219.16 | 213.21 | 218.62 | 0 | 31.25 | 51.74 | 13085 | 90.75 | 41.85 | 37.06 | 1.07 | 41.85 | 0 | 606 | 430.7 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 312.9 | 0 | 306.7 | 100.35 | 15695 | 15694 | 316
03/26/22 10:28:31.204 | 582.2902 | 1367.5458 | 53.7068 | 43.5181 | 10.1887 | 31.3486 | 50.9148 | 0 | 1787.3624 | 88.8452 | 79.8059 | 9.0393 | 24.3282 | 69.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0001 | 461.5301 | 458.7501 | 462.2601 | 410.8001 | 440.2801 | 418.9001 | 313.8801 | 0.53904 | 0.11601 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7015032.0392 | 8076318.2305 | 8076318.2305 | 62.4293 | 62.1905 | 1.0018 | 0.99801 | 684544.6371 | 892148.2862 | 460.8467 | 0.45496 | 0 | 0 | 31.3486 | 24.3282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017894 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 619.1312 | 1368.0854 | 55.2792 | 44.446 | 30.6981 | 1787.7956 | 75.6811 | 25.6094 | 459.7022 | 0.0060956 | 60.006 | 0.52172 | 1.5496 | 85.1021 | 2.5132 | 0.63027 | 0.43125 | 4.2099 | 2.5888 | 0.41355 | 0 | 100 | 577.1 | 315 | 105.95 | 103.53 | 100.38 | 305.8 | 3 | 90.78 | 41.85 | 4 | 37.06 | 42.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.1 | 0 | 37.84 | 64 | 64 | 99.98 | 87.55 | 83.3 | 0 | 100.38 | 2.26 | 89.79 | 42.63 | 105.95 | 12.75 | 103.53 | 110 | 0 | 15694 | 79.92 | 114.54 | 219.04 | 213.21 | 218.62 | 0 | 32.29 | 52.98 | 13090 | 90.78 | 41.85 | 37.06 | 1.01 | 41.85 | 0 | 606 | 430.8 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 312.1 | 0 | 305.8 | 100.37 | 15696 | 15694 | 315
03/26/22 10:28:36.204 | 582.9247 | 1369.1044 | 53.6988 | 43.5083 | 10.1906 | 31.863 | 50.9113 | 0 | 1784.2503 | 88.8595 | 79.8139 | 9.0456 | 23.7442 | 69.5269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 461.53 | 458.75 | 462.26 | 410.8 | 440.28 | 418.9 | 313.88 | 0.53846 | 0.29809 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7022993.4385 | 8069904.4798 | 8069904.4798 | 62.4293 | 62.1904 | 1.0018 | 0.99801 | 685185.6167 | 890983.0068 | 460.8467 | 0.45496 | 0 | 0 | 31.863 | 23.7442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017902 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 618.9224 | 1368.0848 | 55.2723 | 44.4427 | 30.708 | 1787.7294 | 75.7314 | 25.5931 | 459.7102 | 0.006113 | 60.006 | 0.52169 | 1.5306 | 85.1514 | 2.513 | 0.64073 | 0.43614 | 4.171 | 2.5806 | 0.42162 | 0 | 100 | 576.8 | 316 | 105.93 | 103.51 | 100.4 | 303.6 | 3 | 90.76 | 41.85 | 4 | 37.06 | 42.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.13 | 0 | 37.84 | 64 | 64 | 99.98 | 87.55 | 83.45 | 0 | 100.4 | 2.26 | 89.79 | 42.63 | 105.95 | 12.73 | 103.51 | 110 | 0 | 15694 | 79.94 | 114.66 | 219.04 | 213.21 | 218.62 | 0 | 33.23 | 53.62 | 13095 | 90.78 | 41.85 | 37.06 | 0.97 | 41.85 | 0 | 606 | 428 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.8 | 309.8 | 0 | 303.6 | 100.31 | 15693 | 15694 | 316
03/26/22 10:28:41.204 | 583.8857 | 1370.6373 | 53.6884 | 43.4949 | 10.1935 | 31.7408 | 50.9129 | 0 | 1778.9397 | 88.8786 | 79.8243 | 9.0543 | 23.7727 | 69.5406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0031 | 461.5101 | 458.8001 | 462.3201 | 410.6801 | 440.4901 | 419.2301 | 314.0101 | 0.53779 | 0.68077 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7034585.0026 | 8050865.1935 | 8050865.1935 | 62.4293 | 62.1903 | 1.0018 | 0.99801 | 686092.9151 | 887941.676 | 460.8767 | 0.45059 | 0 | 0 | 31.7408 | 23.7727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017913 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 618.7052 | 1368.0855 | 55.2653 | 44.4396 | 30.7187 | 1787.6411 | 75.7813 | 25.5756 | 459.7183 | 0.0061303 | 60.006 | 0.52166 | 1.5136 | 85.2001 | 2.5135 | 0.65098 | 0.44084 | 4.1229 | 2.5722 | 0.42978 | 0 | 100 | 577.2 | 315 | 106 | 103.48 | 100.38 | 305.6 | 3 | 90.8 | 41.85 | 4 | 37.06 | 42.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.17 | 0 | 37.84 | 64 | 64 | 100.05 | 87.58 | 83.61 | 0 | 100.38 | 2.26 | 89.83 | 42.63 | 106 | 12.7 | 103.48 | 110 | 0 | 15694 | 79.94 | 114.74 | 219.04 | 213.11 | 218.62 | 0 | 33.79 | 53.35 | 13100 | 90.8 | 41.85 | 37.06 | 0.95 | 41.85 | 0 | 606 | 428.7 | 459.3 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 312.5 | 0 | 306.3 | 100.4 | 15694 | 15694 | 316
03/26/22 10:28:46.204 | 584.2148 | 1371.2669 | 53.6856 | 43.4911 | 10.1946 | 31.3736 | 50.9177 | 0 | 1778.0726 | 88.8841 | 79.8271 | 9.057 | 24.5932 | 69.5554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0031 | 461.5101 | 458.8001 | 462.3201 | 410.6801 | 440.4901 | 419.2301 | 314.0101 | 0.53749 | 0.73496 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7038223.2586 | 8050284.6426 | 8050284.6426 | 62.4293 | 62.1902 | 1.0018 | 0.99801 | 686408.2246 | 887508.5342 | 460.8767 | 0.45059 | 0 | 0 | 31.3736 | 24.5932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017915 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 618.4787 | 1368.0786 | 55.2583 | 44.4366 | 30.7258 | 1787.5545 | 75.8309 | 25.5637 | 459.7262 | 0.0061475 | 60.0059 | 0.52164 | 1.4964 | 85.2483 | 2.5029 | 0.66113 | 0.44548 | 4.1593 | 2.5636 | 0.43788 | 0 | 100 | 577.3 | 317 | 106.03 | 103.48 | 100.4 | 307.3 | 3 | 90.8 | 41.86 | 4 | 37.08 | 42.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.2 | 0 | 37.85 | 64 | 64 | 100.08 | 87.6 | 83.69 | 0 | 100.4 | 2.26 | 89.84 | 42.63 | 106 | 12.66 | 103.48 | 110 | 0 | 15694 | 79.96 | 114.79 | 219.04 | 213.11 | 218.62 | 0 | 33.77 | 52.36 | 13105 | 90.82 | 41.86 | 37.08 | 0.92 | 41.86 | 0 | 606 | 430.5 | 459.3 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 312.6 | 0 | 306.4 | 100.4 | 15693 | 15694 | 316
03/26/22 10:28:51.204 | 583.5131 | 1369.3419 | 53.6808 | 43.4842 | 10.1966 | 30.6714 | 50.9009 | 0 | 1785.5096 | 88.8947 | 79.8331 | 9.0616 | 25.3969 | 69.5459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0011 | 461.5001 | 458.8601 | 462.4101 | 410.4401 | 440.7301 | 419.5301 | 314.1001 | 0.53829 | 0.14779 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7029146.3237 | 8088936.0475 | 8088936.0475 | 62.4293 | 62.1901 | 1.0019 | 0.99801 | 685444.8059 | 891219.8281 | 460.9234 | 0.44765 | 0 | 0 | 30.6714 | 25.3969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017902 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 618.2359 | 1368.0612 | 55.2513 | 44.4337 | 30.7261 | 1787.5106 | 75.8801 | 25.5624 | 459.7341 | 0.0061646 | 60.0058 | 0.52164 | 1.4762 | 85.2959 | 2.4758 | 0.6711 | 0.44996 | 4.1835 | 2.5549 | 0.44625 | 0 | 100 | 577.2 | 317 | 106.05 | 103.48 | 100.38 | 307.6 | 3 | 90.83 | 41.88 | 4 | 37.09 | 42.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.23 | 0 | 37.85 | 64 | 64 | 100.1 | 87.62 | 83.85 | 0 | 100.38 | 2.26 | 89.86 | 42.64 | 106.05 | 12.65 | 103.48 | 110 | 0 | 15694 | 79.99 | 114.79 | 219.04 | 213.11 | 218.62 | 0 | 33.55 | 51.52 | 13110 | 90.83 | 41.88 | 37.09 | 0.9 | 41.88 | 0 | 606 | 430.5 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 313.7 | 0 | 307.4 | 100.37 | 15694 | 15694 | 316
03/26/22 10:28:56.204 | 583.4723 | 1369.1044 | 53.6798 | 43.4828 | 10.197 | 30.7678 | 50.9005 | 0 | 1787.285 | 88.8969 | 79.8347 | 9.0622 | 25.1727 | 69.5335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0011 | 461.5001 | 458.8601 | 462.4101 | 410.4401 | 440.7301 | 419.5301 | 314.1001 | 0.53833 | 0.090539 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7028697.5825 | 8093120.1945 | 8093120.1945 | 62.4293 | 62.1901 | 1.0019 | 0.99801 | 685385.404 | 891662.8024 | 460.9234 | 0.44765 | 0 | 0 | 30.7678 | 25.1727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017903 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 617.9826 | 1368.0458 | 55.2442 | 44.4309 | 30.724 | 1787.5038 | 75.9287 | 25.5626 | 459.742 | 0.0061816 | 60.0057 | 0.52165 | 1.4548 | 85.3429 | 2.4606 | 0.68092 | 0.4543 | 4.1829 | 2.5463 | 0.45463 | 0 | 100 | 577.1 | 317 | 106.1 | 103.48 | 100.37 | 306.8 | 3 | 90.84 | 41.86 | 4 | 37.08 | 42.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.23 | 0 | 37.85 | 64 | 64 | 100.08 | 87.6 | 83.92 | 0 | 100.37 | 2.26 | 89.86 | 42.64 | 106.1 | 12.64 | 103.48 | 110 | 0 | 15694 | 80.01 | 114.79 | 219.04 | 213.11 | 218.62 | 0 | 33.53 | 51.19 | 13115 | 90.84 | 41.86 | 37.08 | 0.92 | 41.86 | 0 | 606 | 431.2 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 313.9 | 0 | 307.6 | 100.43 | 15693 | 15694 | 315
03/26/22 10:29:01.204 | 583.2543 | 1368.6193 | 53.6752 | 43.4777 | 10.1975 | 31.0859 | 50.8964 | 0 | 1783.6362 | 88.9097 | 79.8456 | 9.0641 | 24.4931 | 69.5715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 461.44 | 458.85 | 462.44 | 410.25 | 440.87 | 419.71 | 314.14 | 0.5386 | 0.2053 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7026391.7281 | 8081672.7151 | 8081672.7151 | 62.4294 | 62.19 | 1.0019 | 0.99801 | 685083.3745 | 890283.0373 | 460.91 | 0.44694 | 0 | 0 | 31.0859 | 24.4931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017913 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 617.7231 | 1368.0335 | 55.237 | 44.4281 | 30.7296 | 1787.5035 | 75.977 | 25.5524 | 459.7498 | 0.0061986 | 60.0055 | 0.52166 | 1.4337 | 85.3893 | 2.446 | 0.6906 | 0.45858 | 4.183 | 2.5375 | 0.46272 | 0 | 100 | 577.1 | 315 | 106.08 | 103.48 | 100.37 | 306.6 | 3 | 90.83 | 41.88 | 4 | 37.09 | 42.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.23 | 0 | 37.85 | 64 | 64 | 100.1 | 87.62 | 84.07 | 0 | 100.37 | 2.26 | 89.86 | 42.64 | 106.08 | 12.64 | 103.48 | 110 | 0 | 15694 | 80.01 | 114.76 | 219.04 | 213.11 | 218.62 | 0 | 33.66 | 51.23 | 13120 | 90.84 | 41.88 | 37.09 | 0.9 | 41.88 | 0 | 606 | 428.2 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 313.6 | 0 | 307.3 | 100.43 | 15694 | 15694 | 317
03/26/22 10:29:06.205 | 583.339 | 1368.8619 | 53.6736 | 43.4765 | 10.1971 | 30.1209 | 50.9111 | 0 | 1785.9586 | 88.918 | 79.8528 | 9.0653 | 25.8779 | 69.586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9871 | 461.4101 | 458.8501 | 462.4501 | 410.1501 | 440.9501 | 419.7801 | 314.1501 | 0.53854 | 0.045933 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7026563.5526 | 8094768.6048 | 8094768.6048 | 62.4294 | 62.1899 | 1.0019 | 0.99801 | 685204.8638 | 891441.2978 | 460.9034 | 0.4455 | 0 | 0 | 30.1209 | 25.8779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017902 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 617.4532 | 1368.018 | 55.2296 | 44.4254 | 30.7346 | 1787.4908 | 76.0249 | 25.5403 | 459.7573 | 0.0062148 | 60.0053 | 0.52168 | 1.4138 | 85.4351 | 2.4316 | 0.70015 | 0.46281 | 4.191 | 2.5288 | 0.47051 | 0 | 100 | 577.4 | 316 | 106.05 | 103.48 | 100.42 | 306.4 | 3 | 90.83 | 41.86 | 4 | 37.08 | 42.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.2 | 0 | 37.85 | 64 | 64 | 100.08 | 87.62 | 84.13 | 0 | 100.42 | 2.26 | 89.84 | 42.64 | 106.05 | 12.65 | 103.48 | 110 | 0 | 15694 | 80.01 | 114.76 | 219.04 | 213.11 | 218.5 | 0 | 33.98 | 51.55 | 13125 | 90.83 | 41.86 | 37.08 | 0.92 | 41.86 | 0 | 606 | 429.6 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 314.7 | 0 | 308.5 | 100.4 | 15693 | 15694 | 315
03/26/22 10:29:11.203 | 583.3765 | 1368.7742 | 53.6728 | 43.4762 | 10.1967 | 30.628 | 50.9131 | 0 | 1790.4074 | 88.9278 | 79.8622 | 9.0655 | 25.1207 | 69.5699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9821 | 461.3701 | 458.8401 | 462.4501 | 410.1101 | 441.0901 | 419.9401 | 314.1901 | 0.53857 | -0.17351 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7027439.2926 | 8113428.8586 | 8113428.8586 | 62.4294 | 62.1898 | 1.0019 | 0.99801 | 685274.6507 | 893562.9155 | 460.8868 | 0.44407 | 0 | 0 | 30.628 | 25.1207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017901 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 617.1744 | 1367.9942 | 55.2221 | 44.4226 | 30.738 | 1787.5006 | 76.0725 | 25.5305 | 459.7648 | 0.0062309 | 60.0051 | 0.52172 | 1.3923 | 85.4806 | 2.4006 | 0.70954 | 0.46703 | 4.1953 | 2.5198 | 0.47797 | 0 | 100 | 577.2 | 316 | 106.08 | 103.48 | 100.38 | 308 | 3 | 90.86 | 41.86 | 4 | 37.08 | 42.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.17 | 0 | 37.85 | 64 | 64 | 100 | 87.56 | 84.15 | 0 | 100.38 | 2.26 | 89.83 | 42.64 | 106.1 | 12.62 | 103.48 | 110 | 0 | 15694 | 80.01 | 114.79 | 219.04 | 213.11 | 218.5 | 0 | 34.38 | 51.69 | 13130 | 90.86 | 41.86 | 37.08 | 0.9 | 41.86 | 0 | 606 | 431.5 | 459.1 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.2 | 310.7 | 0 | 304.5 | 100.38 | 15693 | 15694 | 316
03/26/22 10:29:16.203 | 583.0185 | 1368.191 | 53.6728 | 43.4763 | 10.1965 | 30.6606 | 50.9121 | 0 | 1790.5209 | 88.932 | 79.8665 | 9.0655 | 25.1215 | 69.5724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9821 | 461.3701 | 458.8401 | 462.4501 | 410.1101 | 441.0901 | 419.9401 | 314.1901 | 0.5389 | -0.24091 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7023179.629 | 8114765.7929 | 8114765.7929 | 62.4294 | 62.1898 | 1.0019 | 0.99801 | 684869.0574 | 893716.6771 | 460.8867 | 0.44407 | 0 | 0 | 30.6606 | 25.1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017904 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 616.8942 | 1367.9764 | 55.2145 | 44.4197 | 30.7384 | 1787.4992 | 76.1199 | 25.5249 | 459.772 | 0.0062466 | 60.0048 | 0.52175 | 1.372 | 85.5258 | 2.3871 | 0.71877 | 0.47123 | 4.1943 | 2.5105 | 0.48501 | 0 | 100 | 577.8 | 318 | 106.08 | 103.48 | 100.47 | 308.3 | 3 | 90.84 | 41.86 | 4 | 37.08 | 42.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.17 | 0 | 37.85 | 64 | 64 | 99.98 | 87.55 | 84.28 | 0 | 100.47 | 2.26 | 89.83 | 42.64 | 106.05 | 12.65 | 103.48 | 110 | 0 | 15694 | 80.03 | 114.81 | 219.04 | 213.11 | 218.5 | 0 | 34.6 | 51.51 | 13135 | 90.83 | 41.86 | 37.08 | 0.9 | 41.86 | 0 | 606 | 430.9 | 459.1 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 314.6 | 0 | 308.3 | 100.49 | 15693 | 15694 | 318
03/26/22 10:29:21.203 | 581.5105 | 1364.6144 | 53.6744 | 43.4776 | 10.1968 | 31.7305 | 50.9179 | 0 | 1785.8502 | 88.9453 | 79.8805 | 9.0648 | 24.1336 | 69.5802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9721 | 461.2601 | 458.7901 | 462.4001 | 410.0401 | 441.2201 | 420.0901 | 314.2301 | 0.54037 | -0.17074 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7005950.8026 | 8091849.7717 | 8091849.7717 | 62.4294 | 62.1896 | 1.0019 | 0.99801 | 683078.6722 | 891383.4647 | 460.8167 | 0.4398 | 0 | 0 | 31.7305 | 24.1336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017911 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 616.6094 | 1367.9527 | 55.2067 | 44.4168 | 30.7421 | 1787.4774 | 76.1669 | 25.5169 | 459.7792 | 0.006262 | 60.0045 | 0.5218 | 1.3528 | 85.5705 | 2.3974 | 0.72782 | 0.47544 | 4.1871 | 2.501 | 0.49142 | 0 | 100 | 577.3 | 316 | 106.03 | 103.48 | 100.4 | 305.8 | 3 | 90.82 | 41.88 | 4 | 37.09 | 42.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.17 | 0 | 37.85 | 64 | 64 | 99.95 | 87.53 | 84.35 | 0 | 100.35 | 2.26 | 89.83 | 42.64 | 106.03 | 12.66 | 103.48 | 110 | 0 | 15694 | 80.03 | 114.81 | 219.04 | 213.11 | 218.5 | 0 | 34.56 | 51.11 | 13140 | 90.82 | 41.88 | 37.09 | 0.88 | 41.88 | 0 | 606 | 428.9 | 459.1 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 313.7 | 0 | 307.5 | 100.43 | 15693 | 15694 | 315
03/26/22 10:29:26.204 | 582.0406 | 1365.7188 | 53.6765 | 43.4786 | 10.1979 | 31.6931 | 50.9203 | 0 | 1782.7278 | 88.9521 | 79.8875 | 9.0646 | 23.6515 | 69.5918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.972 | 461.26 | 458.79 | 462.4 | 410.04 | 441.22 | 420.09 | 314.23 | 0.53988 | 0.093767 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7012301.6183 | 8076921.5567 | 8076921.5567 | 62.4294 | 62.1896 | 1.0019 | 0.99801 | 683631.4342 | 889824.0206 | 460.8167 | 0.4398 | 0 | 0 | 31.6931 | 23.6515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017921 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 616.321 | 1367.9369 | 55.1987 | 44.4138 | 30.7493 | 1787.4537 | 76.2137 | 25.5018 | 459.786 | 0.0062768 | 60.0042 | 0.52185 | 1.3352 | 85.6148 | 2.4027 | 0.73667 | 0.47968 | 4.2019 | 2.4914 | 0.49724 | 0 | 100 | 577.4 | 313 | 106.03 | 103.46 | 100.42 | 305.3 | 3 | 90.82 | 41.88 | 4 | 37.09 | 42.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.17 | 0 | 37.86 | 64 | 64 | 100.02 | 87.56 | 84.39 | 0 | 100.47 | 2.26 | 89.83 | 42.65 | 106.05 | 12.63 | 103.46 | 110 | 0 | 15694 | 80.03 | 114.81 | 219.04 | 213.11 | 218.5 | 0 | 34.55 | 50.83 | 13145 | 90.83 | 41.88 | 37.09 | 0.86 | 41.88 | 0 | 606 | 429.9 | 459.1 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.6 | 313.7 | 0 | 307.4 | 100.45 | 15693 | 15694 | 317
03/26/22 10:29:31.203 | 581.3277 | 1363.7319 | 53.6806 | 43.4804 | 10.2002 | 31.7455 | 50.8929 | 0 | 1780.7667 | 88.9616 | 79.8974 | 9.0643 | 23.9414 | 69.5839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9681 | 461.2401 | 458.8001 | 462.4001 | 410.0701 | 441.2401 | 420.1401 | 314.2601 | 0.54059 | 0.097405 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7003753.08 | 8068087.5999 | 8068087.5999 | 62.4294 | 62.1895 | 1.0019 | 0.99801 | 682636.6457 | 888843.8034 | 460.8134 | 0.43691 | 0 | 0 | 31.7455 | 23.9414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017924 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 616.0306 | 1367.9247 | 55.1905 | 44.4105 | 30.7565 | 1787.4144 | 76.26 | 25.4872 | 459.7928 | 0.0062915 | 60.0039 | 0.52191 | 1.3193 | 85.6587 | 2.4182 | 0.74531 | 0.48398 | 4.2283 | 2.4818 | 0.50291 | 0 | 100 | 577.8 | 315 | 106.05 | 103.46 | 100.49 | 305.6 | 3 | 90.83 | 41.89 | 4 | 37.1 | 42.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.2 | 0 | 37.88 | 64 | 64 | 100.02 | 87.58 | 84.41 | 0 | 100.47 | 2.26 | 89.84 | 42.66 | 106.03 | 12.63 | 103.46 | 110 | 0 | 15694 | 80.03 | 114.81 | 219.04 | 213.11 | 218.5 | 0 | 34.54 | 50.59 | 13150 | 90.83 | 41.89 | 37.1 | 0.87 | 41.89 | 0 | 606 | 428.6 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 312.6 | 0 | 306.4 | 100.49 | 15693 | 15694 | 316
03/26/22 10:29:36.203 | 582.4077 | 1366.0956 | 53.683 | 43.4815 | 10.2015 | 32.0901 | 50.8974 | 0 | 1779.0532 | 88.9667 | 79.9024 | 9.0643 | 23.5954 | 69.5843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.967 | 461.23 | 458.81 | 462.39 | 410.11 | 441.28 | 420.22 | 314.31 | 0.53967 | 0.3642 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7017063.0898 | 8059954.5675 | 8059954.5675 | 62.4293 | 62.1894 | 1.0019 | 0.99801 | 683819.7474 | 887987.8894 | 460.81 | 0.43402 | 0 | 0 | 32.0901 | 23.5954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017928 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 615.7452 | 1367.9276 | 55.1822 | 44.4073 | 30.771 | 1787.3505 | 76.3062 | 25.4655 | 459.7997 | 0.0063063 | 60.0035 | 0.52196 | 1.3063 | 85.7023 | 2.4157 | 0.75374 | 0.48828 | 4.2672 | 2.4717 | 0.50837 | 0 | 100 | 577.4 | 316 | 106.08 | 103.46 | 100.42 | 306.7 | 3 | 90.84 | 41.89 | 4 | 37.1 | 42.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.2 | 0 | 37.88 | 64 | 64 | 100.02 | 87.58 | 84.41 | 0 | 100.42 | 2.26 | 89.84 | 42.66 | 106.05 | 12.63 | 103.46 | 110 | 0 | 15694 | 80.05 | 114.81 | 219.04 | 213.11 | 218.5 | 0 | 34.43 | 50.28 | 13155 | 90.83 | 41.89 | 37.1 | 0.87 | 41.89 | 0 | 606 | 429.9 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.9 | 312.8 | 0 | 306.6 | 100.5 | 15693 | 15694 | 315
03/26/22 10:29:41.203 | 583.2216 | 1368.4026 | 53.6859 | 43.4831 | 10.2028 | 32.1884 | 50.9059 | 0 | 1779.8016 | 88.972 | 79.9073 | 9.0647 | 23.598 | 69.6054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.967 | 461.23 | 458.81 | 462.39 | 410.11 | 441.28 | 420.22 | 314.31 | 0.53892 | 0.44326 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7026960.7899 | 8063608.8009 | 8063608.8009 | 62.4293 | 62.1894 | 1.0019 | 0.99801 | 684708.3393 | 888368.63 | 460.81 | 0.43402 | 0 | 0 | 32.1884 | 23.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017934 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 615.4476 | 1367.9136 | 55.1736 | 44.4038 | 30.7853 | 1787.2845 | 76.3521 | 25.4449 | 459.8065 | 0.0063212 | 60.0032 | 0.52203 | 1.2924 | 85.7455 | 2.4055 | 0.76193 | 0.4926 | 4.2917 | 2.4614 | 0.51362 | 0 | 100 | 577.8 | 315 | 106.05 | 103.46 | 100.49 | 305.9 | 3 | 90.83 | 41.89 | 4 | 37.1 | 42.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.25 | 0 | 37.88 | 64 | 64 | 100.08 | 87.6 | 84.43 | 0 | 100.49 | 2.26 | 89.87 | 42.66 | 106.05 | 12.63 | 103.46 | 110 | 0 | 15694 | 80.05 | 114.79 | 219.04 | 213.11 | 218.5 | 0 | 34.4 | 50.22 | 13160 | 90.83 | 41.89 | 37.1 | 0.87 | 41.89 | 0 | 606 | 429.5 | 459.2 | 26 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 314.4 | 0 | 308.1 | 100.52 | 15693 | 15694 | 317
03/26/22 10:29:46.203 | 584.0226 | 1369.347 | 53.6904 | 43.4857 | 10.2047 | 31.3908 | 50.9007 | 0 | 1778.8003 | 88.9786 | 79.9127 | 9.0659 | 24.2851 | 69.5959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9651 | 461.2201 | 458.7901 | 462.3601 | 410.1901 | 441.3301 | 420.3001 | 314.3501 | 0.53825 | 0.58644 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7036053.0846 | 8061246.191 | 8061246.191 | 62.4293 | 62.1893 | 1.0019 | 0.99801 | 685524.5051 | 887945.4132 | 460.7901 | 0.43404 | 0 | 0 | 31.3908 | 24.2851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017938 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 615.1496 | 1367.9031 | 55.1649 | 44.4003 | 30.7947 | 1787.1953 | 76.3978 | 25.4273 | 459.8134 | 0.006336 | 60.0029 | 0.5221 | 1.28 | 85.7885 | 2.395 | 0.76988 | 0.49691 | 4.3004 | 2.4507 | 0.51846 | 0 | 100 | 578 | 318 | 106.15 | 103.46 | 100.52 | 307.9 | 3 | 90.87 | 41.89 | 4 | 37.1 | 42.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.27 | 0 | 37.89 | 64 | 64 | 100.1 | 87.62 | 84.52 | 0 | 100.52 | 2.26 | 89.88 | 42.68 | 106.15 | 12.57 | 103.46 | 110 | 0 | 15694 | 80.05 | 114.79 | 219.04 | 213.11 | 218.5 | 0 | 34.43 | 50.24 | 13165 | 90.88 | 41.9 | 37.11 | 0.86 | 41.9 | 0 | 606 | 431.3 | 459.1 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 315 | 0 | 308.7 | 100.47 | 15693 | 15694 | 317
03/26/22 10:29:51.203 | 583.5822 | 1368.0929 | 53.6959 | 43.4888 | 10.2072 | 31.1694 | 50.9075 | 0 | 1781.9175 | 88.9852 | 79.9184 | 9.0668 | 24.8939 | 69.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9631 | 461.2201 | 458.7801 | 462.3301 | 410.2701 | 441.2901 | 420.3101 | 314.3801 | 0.53871 | 0.32732 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7030388.8369 | 8076617.9273 | 8076617.9273 | 62.4293 | 62.1892 | 1.0018 | 0.99801 | 684818.9565 | 889415.4317 | 460.7767 | 0.43333 | 0 | 0 | 31.1694 | 24.8939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017935 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 614.8545 | 1367.9024 | 55.156 | 44.3965 | 30.8048 | 1787.0954 | 76.4431 | 25.4138 | 459.8201 | 0.0063504 | 60.0026 | 0.52217 | 1.2695 | 85.8311 | 2.3949 | 0.77755 | 0.50125 | 4.2114 | 2.4399 | 0.52311 | 0 | 100 | 577.7 | 317 | 106.15 | 103.46 | 100.47 | 308 | 3 | 90.88 | 41.9 | 4 | 37.11 | 42.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.27 | 0 | 37.89 | 64 | 64 | 100.13 | 87.63 | 84.56 | 0 | 100.4 | 2.26 | 89.88 | 42.68 | 106.13 | 12.59 | 103.46 | 110 | 0 | 15694 | 80.05 | 114.81 | 219.04 | 213.11 | 218.5 | 0 | 34.48 | 50.28 | 13170 | 90.87 | 41.9 | 37.11 | 0.86 | 41.9 | 0 | 606 | 427.6 | 459 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.6 | 312.9 | 0 | 306.7 | 100.45 | 15693 | 15694 | 318
03/26/22 10:29:56.203 | 583.764 | 1368.2271 | 53.7004 | 43.491 | 10.2094 | 31.5733 | 50.9028 | 0 | 1785.1793 | 88.9897 | 79.9229 | 9.0668 | 24.5796 | 69.5971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.963 | 461.22 | 458.77 | 462.31 | 410.35 | 441.24 | 420.26 | 314.4 | 0.53857 | 0.18017 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7032928.3993 | 8091046.117 | 8091046.117 | 62.4293 | 62.1892 | 1.0018 | 0.99801 | 684885.9231 | 891042.8764 | 460.7667 | 0.43334 | 0 | 0 | 31.5733 | 24.5796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017934 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 614.5632 | 1367.9125 | 55.1468 | 44.3925 | 30.8149 | 1787.0284 | 76.4881 | 25.4015 | 459.8265 | 0.0063644 | 60.0023 | 0.52225 | 1.2583 | 85.8733 | 2.3925 | 0.78494 | 0.50557 | 4.1445 | 2.4288 | 0.52758 | 0 | 100 | 578 | 317 | 106.13 | 103.48 | 100.52 | 307.5 | 3 | 90.87 | 41.9 | 4 | 37.11 | 42.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.27 | 0 | 37.89 | 64 | 64 | 100.1 | 87.62 | 84.56 | 0 | 100.52 | 2.26 | 89.88 | 42.68 | 106.1 | 12.62 | 103.48 | 110 | 0 | 15694 | 80.05 | 114.83 | 219.04 | 213.11 | 218.5 | 0 | 34.53 | 50.28 | 13175 | 90.86 | 41.9 | 37.11 | 0.86 | 41.9 | 0 | 606 | 431.4 | 459.1 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 312.1 | 0 | 305.8 | 100.47 | 15693 | 15694 | 315
03/26/22 10:30:01.203 | 583.0578 | 1366.1472 | 53.7071 | 43.4945 | 10.2125 | 30.2323 | 50.9548 | 0 | 1791.3467 | 88.9964 | 79.9303 | 9.0661 | 26.3357 | 69.6174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.967 | 461.27 | 458.77 | 462.3 | 410.5 | 441.24 | 420.2 | 314.44 | 0.53929 | -0.29854 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7023234.2085 | 8120354.1359 | 8120354.1359 | 62.4293 | 62.1891 | 1.0018 | 0.99801 | 683844.5133 | 894120.2236 | 460.78 | 0.43622 | 0 | 0 | 30.2323 | 26.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017921 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 614.2747 | 1367.9281 | 55.1376 | 44.3885 | 30.8144 | 1787.0088 | 76.533 | 25.4027 | 459.833 | 0.0063783 | 60.002 | 0.52232 | 1.2447 | 85.9154 | 2.3708 | 0.79206 | 0.50983 | 4.1203 | 2.4172 | 0.53194 | 0 | 100 | 577.7 | 318 | 106.15 | 103.48 | 100.47 | 308.3 | 3 | 90.88 | 41.9 | 4 | 37.11 | 42.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.27 | 0 | 37.89 | 64 | 64 | 100.13 | 87.63 | 84.54 | 0 | 100.47 | 2.26 | 89.88 | 42.68 | 106.15 | 12.6 | 103.48 | 110 | 0 | 15694 | 80.05 | 114.83 | 219.04 | 213.11 | 218.5 | 0 | 34.5 | 50.09 | 13180 | 90.88 | 41.9 | 37.11 | 0.87 | 41.9 | 0 | 606 | 427.8 | 459.1 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 314.4 | 0 | 308.1 | 100.49 | 15693 | 15694 | 317
03/26/22 10:30:06.203 | 583.4386 | 1366.8697 | 53.7104 | 43.4965 | 10.2138 | 29.9012 | 50.9305 | 0 | 1793.3182 | 88.9999 | 79.9349 | 9.065 | 26.544 | 69.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9671 | 461.2701 | 458.7701 | 462.3001 | 410.5001 | 441.2401 | 420.2001 | 314.4401 | 0.53894 | -0.346 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7027527.5351 | 8128517.5165 | 8128517.5165 | 62.4293 | 62.1891 | 1.0018 | 0.99801 | 684206.0454 | 895103.633 | 460.7801 | 0.43622 | 0 | 0 | 29.9012 | 26.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017917 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 613.9827 | 1367.9333 | 55.1281 | 44.3843 | 30.8087 | 1787.0296 | 76.5777 | 25.4108 | 459.8393 | 0.006392 | 60.0017 | 0.5224 | 1.229 | 85.9572 | 2.3674 | 0.79889 | 0.51406 | 4.1427 | 2.4053 | 0.5364 | 0 | 100 | 578 | 314 | 106.15 | 103.48 | 100.49 | 306.9 | 3 | 90.88 | 41.9 | 4 | 37.11 | 42.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.23 | 0 | 37.89 | 64 | 64 | 100.05 | 87.59 | 84.58 | 0 | 100.49 | 2.26 | 89.86 | 42.68 | 106.1 | 12.62 | 103.48 | 110 | 0 | 15694 | 80.07 | 114.86 | 219.04 | 213.11 | 218.5 | 0 | 34.44 | 50.03 | 13185 | 90.86 | 41.9 | 37.11 | 0.86 | 41.9 | 0 | 606 | 428.9 | 459.2 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 313.4 | 0 | 307.1 | 100.49 | 15695 | 15694 | 315
03/26/22 10:30:11.203 | 582.933 | 1365.0737 | 53.7134 | 43.4985 | 10.2149 | 29.9858 | 50.9164 | 0 | 1794.5259 | 89.0033 | 79.9394 | 9.0639 | 26.1819 | 69.6293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.967 | 461.23 | 458.72 | 462.25 | 410.58 | 441.28 | 420.23 | 314.45 | 0.53943 | -0.43881 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7021408.0026 | 8129952.5322 | 8129952.5322 | 62.4293 | 62.189 | 1.0018 | 0.99801 | 683562.6858 | 895355.6773 | 460.7334 | 0.43698 | 0 | 0 | 29.9858 | 26.1819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017904 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 613.678 | 1367.9166 | 55.1184 | 44.3798 | 30.8106 | 1787.0985 | 76.622 | 25.4079 | 459.8455 | 0.0064054 | 60.0015 | 0.52249 | 1.2097 | 85.9987 | 2.3769 | 0.80541 | 0.51825 | 4.1638 | 2.3932 | 0.54025 | 0 | 100 | 578 | 316 | 106.1 | 103.48 | 100.54 | 307.3 | 3 | 90.86 | 41.91 | 4 | 37.13 | 42.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.17 | 0 | 37.9 | 64 | 64 | 100 | 87.56 | 84.62 | 0 | 100.54 | 2.26 | 89.83 | 42.69 | 106.08 | 12.64 | 103.48 | 110 | 0 | 15694 | 80.07 | 114.86 | 219.04 | 213.11 | 218.5 | 0 | 34.46 | 50.11 | 13190 | 90.84 | 41.91 | 37.13 | 0.86 | 41.91 | 0 | 606 | 430.2 | 458.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.2 | 314.1 | 0 | 307.9 | 100.56 | 15693 | 15694 | 317
03/26/22 10:30:16.202 | 583.4851 | 1366.5394 | 53.7213 | 43.5041 | 10.2171 | 31.1976 | 50.9222 | 0 | 1796.4561 | 89.0126 | 79.9522 | 9.0604 | 24.6902 | 69.5917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9731 | 461.2001 | 458.6401 | 462.2201 | 410.6901 | 441.4301 | 420.1201 | 314.4801 | 0.53897 | -0.42147 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7029217.5867 | 8136488.5857 | 8136488.5857 | 62.4293 | 62.1889 | 1.0018 | 0.99801 | 684040.2397 | 896667.5329 | 460.6867 | 0.44426 | 0 | 0 | 31.1976 | 24.6902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017902 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 613.3722 | 1367.9019 | 55.1085 | 44.3751 | 30.8162 | 1787.1569 | 76.6661 | 25.3999 | 459.8515 | 0.0064182 | 60.0014 | 0.52259 | 1.1914 | 86.0398 | 2.3859 | 0.81158 | 0.52235 | 4.2389 | 2.3808 | 0.54382 | 0 | 100 | 577.7 | 317 | 106.05 | 103.48 | 100.54 | 305.9 | 3 | 90.84 | 41.91 | 4 | 37.13 | 42.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.2 | 0 | 37.89 | 64 | 64 | 100.08 | 87.6 | 84.69 | 0 | 100.52 | 2.26 | 89.84 | 42.68 | 106.05 | 12.65 | 103.48 | 110 | 0 | 15694 | 80.07 | 114.88 | 219.04 | 213.11 | 218.5 | 0 | 34.57 | 50.31 | 13195 | 90.83 | 41.91 | 37.13 | 0.86 | 41.91 | 0 | 606 | 430 | 459 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 312.2 | 0 | 305.9 | 100.47 | 15692 | 15694 | 317
03/26/22 10:30:21.203 | 583.4471 | 1366.6788 | 53.7226 | 43.5051 | 10.2174 | 31.1998 | 50.9195 | 0 | 1795.4807 | 89.014 | 79.9544 | 9.0597 | 24.7051 | 69.5901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9731 | 461.2001 | 458.6401 | 462.2201 | 410.6901 | 441.4301 | 420.1201 | 314.4801 | 0.539 | -0.39435 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7028795.455 | 8133858.3664 | 8133858.3664 | 62.4293 | 62.1889 | 1.0018 | 0.99801 | 683985.9629 | 896425.2382 | 460.6868 | 0.44426 | 0 | 0 | 31.1998 | 24.7051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017903 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 613.0728 | 1367.9048 | 55.0984 | 44.3703 | 30.8223 | 1787.1964 | 76.7101 | 25.3895 | 459.8573 | 0.0064308 | 60.0014 | 0.52268 | 1.1753 | 86.0808 | 2.3841 | 0.81746 | 0.52636 | 4.2832 | 2.368 | 0.54713 | 0 | 100 | 578.2 | 318 | 106.03 | 103.48 | 100.56 | 308.6 | 3 | 90.82 | 41.91 | 4 | 37.13 | 42.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.2 | 0 | 37.9 | 64 | 64 | 100.02 | 87.58 | 84.69 | 0 | 100.56 | 2.26 | 89.84 | 42.69 | 106.03 | 12.66 | 103.48 | 110 | 0 | 15694 | 80.07 | 114.88 | 219.04 | 213.11 | 218.5 | 0 | 34.74 | 50.48 | 13200 | 90.82 | 41.91 | 37.13 | 0.86 | 41.91 | 0 | 606 | 430.8 | 459 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.1 | 313.1 | 0 | 306.8 | 100.54 | 15694 | 15694 | 316
03/26/22 10:30:26.203 | 584.4009 | 1368.3871 | 53.7297 | 43.5103 | 10.2194 | 31.2613 | 50.9166 | 0 | 1790.4848 | 89.02 | 79.963 | 9.057 | 24.5085 | 69.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9741 | 461.1901 | 458.6001 | 462.2201 | 410.7201 | 441.5801 | 420.0801 | 314.5101 | 0.53818 | 0.089002 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7040299.6411 | 8106233.9787 | 8106233.9787 | 62.4292 | 62.1888 | 1.0018 | 0.998 | 684964.7336 | 893685.6216 | 460.6701 | 0.44935 | 0 | 0 | 31.2613 | 24.5085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017906 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 612.7785 | 1367.9191 | 55.0881 | 44.3653 | 30.8261 | 1787.2296 | 76.7539 | 25.3808 | 459.8629 | 0.006443 | 60.0013 | 0.52278 | 1.1608 | 86.1216 | 2.3811 | 0.82304 | 0.53026 | 4.296 | 2.3547 | 0.55025 | 0 | 100 | 578.3 | 316 | 106.05 | 103.48 | 100.57 | 307.3 | 3 | 90.83 | 41.93 | 4 | 37.14 | 42.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.2 | 0 | 37.91 | 64 | 64 | 100.02 | 87.58 | 84.67 | 0 | 100.57 | 2.26 | 89.84 | 42.7 | 106.08 | 12.64 | 103.48 | 110 | 0 | 15694 | 80.07 | 114.9 | 219.04 | 213.11 | 218.5 | 0 | 34.85 | 50.56 | 13205 | 90.84 | 41.93 | 37.14 | 0.85 | 41.93 | 0 | 606 | 432.2 | 459 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 313.6 | 0 | 307.3 | 100.57 | 15693 | 15694 | 316
03/26/22 10:30:31.202 | 584.4147 | 1368.2426 | 53.7336 | 43.5129 | 10.2207 | 31.0407 | 50.9133 | 0 | 1789.4371 | 89.0223 | 79.9661 | 9.0563 | 24.9855 | 69.5975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9741 | 461.1901 | 458.6001 | 462.2201 | 410.7201 | 441.5801 | 420.0801 | 314.5101 | 0.53816 | 0.14893 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7040268.966 | 8101347.2289 | 8101347.2289 | 62.4292 | 62.1888 | 1.0018 | 0.998 | 684892.2296 | 893162.2812 | 460.6701 | 0.44935 | 0 | 0 | 31.0407 | 24.9855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.0179 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 612.4828 | 1367.9329 | 55.0776 | 44.3601 | 30.8276 | 1787.2626 | 76.7974 | 25.3766 | 459.8686 | 0.0064552 | 60.0013 | 0.52287 | 1.1466 | 86.1621 | 2.3756 | 0.82821 | 0.53402 | 4.29 | 2.3411 | 0.5533 | 0 | 100 | 578.3 | 314 | 106.13 | 103.48 | 100.57 | 307.1 | 3 | 90.87 | 41.94 | 4 | 37.15 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.25 | 0 | 37.91 | 64 | 64 | 100.05 | 87.59 | 84.64 | 0 | 100.57 | 2.26 | 89.87 | 42.7 | 106.13 | 12.61 | 103.48 | 110 | 0 | 15694 | 80.09 | 114.9 | 219.04 | 213.11 | 218.5 | 0 | 34.96 | 50.58 | 13210 | 90.87 | 41.94 | 37.15 | 0.85 | 41.94 | 0 | 606 | 430 | 459.1 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 313.4 | 0 | 307.2 | 100.61 | 15695 | 15694 | 318
03/26/22 10:30:36.203 | 585.0365 | 1368.9754 | 53.7396 | 43.5168 | 10.2228 | 30.7068 | 50.9065 | 0 | 1791.4706 | 89.0252 | 79.9698 | 9.0555 | 25.4802 | 69.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.985 | 461.17 | 458.55 | 462.27 | 410.8 | 441.92 | 420.07 | 314.59 | 0.53773 | 0.14866 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7047084.6376 | 8108446.9547 | 8108446.9547 | 62.4292 | 62.1888 | 1.0018 | 0.998 | 685512.0328 | 893862.554 | 460.6634 | 0.45876 | 0 | 0 | 30.7068 | 25.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017894 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 612.191 | 1367.9544 | 55.0669 | 44.3548 | 30.8307 | 1787.3078 | 76.8408 | 25.3719 | 459.8743 | 0.0064677 | 60.0014 | 0.52297 | 1.1328 | 86.2023 | 2.3674 | 0.83302 | 0.53762 | 4.2913 | 2.327 | 0.55615 | 0 | 100 | 578 | 316 | 106.1 | 103.48 | 100.52 | 307.1 | 3 | 90.86 | 41.94 | 4 | 37.14 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.25 | 0 | 37.91 | 64 | 64 | 100.08 | 87.6 | 84.64 | 0 | 100.52 | 2.26 | 89.87 | 42.7 | 106.1 | 12.61 | 103.48 | 110 | 0 | 15694 | 80.09 | 114.93 | 219.04 | 213.11 | 218.5 | 0 | 35.05 | 50.6 | 13214 | 90.87 | 41.93 | 37.14 | 0.87 | 41.93 | 0 | 606 | 432 | 459 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 312.9 | 0 | 306.6 | 100.57 | 15692 | 15694 | 315
03/26/22 10:30:41.202 | 585.2155 | 1369.6515 | 53.7455 | 43.5213 | 10.2242 | 31.9399 | 50.9166 | 0 | 1784.6168 | 89.0272 | 79.9715 | 9.0557 | 24.0574 | 69.6128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 461.14 | 458.51 | 462.27 | 410.82 | 442.1 | 420.09 | 314.61 | 0.5376 | 0.57109 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7050698.572 | 8077927.8954 | 8077927.8954 | 62.4292 | 62.1887 | 1.0018 | 0.998 | 685596.9785 | 890755.5555 | 460.64 | 0.4624 | 0 | 0 | 31.9399 | 24.0574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017913 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 611.8963 | 1367.9758 | 55.056 | 44.3492 | 30.8399 | 1787.2922 | 76.8839 | 25.361 | 459.8801 | 0.0064801 | 60.0015 | 0.52307 | 1.1227 | 86.2423 | 2.3652 | 0.8374 | 0.54105 | 4.2959 | 2.3126 | 0.55869 | 0 | 100 | 578.2 | 317 | 106.13 | 103.48 | 100.56 | 307.8 | 3 | 90.87 | 41.93 | 4 | 37.14 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.25 | 0 | 37.91 | 64 | 64 | 100.1 | 87.62 | 84.67 | 0 | 100.56 | 2.26 | 89.87 | 42.7 | 106.1 | 12.61 | 103.48 | 110 | 0 | 15694 | 80.09 | 114.93 | 219.04 | 213.11 | 218.5 | 0 | 35.09 | 50.52 | 13219 | 90.86 | 41.93 | 37.14 | 0.87 | 41.93 | 0 | 606 | 428.2 | 459 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.2 | 314.1 | 0 | 307.8 | 100.56 | 15695 | 15694 | 317
03/26/22 10:30:46.202 | 584.4429 | 1367.7729 | 53.7502 | 43.5254 | 10.2248 | 31.6673 | 50.9183 | 0 | 1779.4661 | 89.028 | 79.9713 | 9.0567 | 24.2823 | 69.5728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9801 | 461.0901 | 458.4201 | 462.2701 | 410.9201 | 442.4601 | 420.0501 | 314.6701 | 0.53841 | 0.72894 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7041148.2367 | 8055807.3182 | 8055807.3182 | 62.4292 | 62.1887 | 1.0018 | 0.998 | 684656.4112 | 888184.7224 | 460.5934 | 0.47186 | 0 | 0 | 31.6673 | 24.2823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017924 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 611.5898 | 1367.971 | 55.0449 | 44.3435 | 30.8479 | 1787.2784 | 76.9269 | 25.3498 | 459.8857 | 0.0064922 | 60.0015 | 0.52318 | 1.1113 | 86.2821 | 2.3644 | 0.84143 | 0.54431 | 4.3059 | 2.2976 | 0.56087 | 0 | 100 | 578.6 | 315 | 106.23 | 103.48 | 100.63 | 306.4 | 3 | 90.92 | 41.94 | 4 | 37.15 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.35 | 0 | 37.93 | 64 | 64 | 100.15 | 87.64 | 84.67 | 0 | 100.63 | 2.26 | 89.92 | 42.71 | 106.23 | 12.56 | 103.48 | 110 | 0 | 15694 | 80.09 | 114.93 | 219.04 | 213.11 | 218.5 | 0 | 35.1 | 50.42 | 13224 | 90.92 | 41.94 | 37.15 | 0.85 | 41.94 | 0 | 606 | 432.8 | 458.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.6 | 312.2 | 0 | 305.9 | 100.63 | 15692 | 15694 | 316
03/26/22 10:30:51.202 | 584.9322 | 1368.9187 | 53.7532 | 43.5284 | 10.2248 | 30.6487 | 50.9204 | 0 | 1776.963 | 89.0284 | 79.971 | 9.0574 | 25.5731 | 69.5794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.979 | 461.07 | 458.36 | 462.24 | 411.02 | 442.61 | 420.01 | 314.69 | 0.53799 | 0.90731 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7046147.7741 | 8046506.6076 | 8046506.6076 | 62.4292 | 62.1887 | 1.0018 | 0.998 | 685229.8114 | 886935.4077 | 460.5567 | 0.47696 | 0 | 0 | 30.6487 | 25.5731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.01793 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 611.2802 | 1367.968 | 55.0337 | 44.3377 | 30.8542 | 1787.2569 | 76.9697 | 25.3394 | 459.891 | 0.0065037 | 60.0015 | 0.5233 | 1.1 | 86.3218 | 2.3634 | 0.84514 | 0.54741 | 4.3455 | 2.2819 | 0.56302 | 0 | 100 | 578.6 | 317 | 106.3 | 103.51 | 100.63 | 306.7 | 3 | 90.96 | 41.94 | 4 | 37.15 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.4 | 0 | 37.93 | 64 | 64 | 100.23 | 87.69 | 84.67 | 0 | 100.63 | 2.26 | 89.95 | 42.71 | 106.28 | 12.56 | 103.51 | 110 | 0 | 15694 | 80.09 | 114.93 | 219.04 | 213.11 | 218.5 | 0 | 35.06 | 50.26 | 13229 | 90.95 | 41.94 | 37.15 | 0.85 | 41.94 | 0 | 606 | 428.9 | 458.8 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 315 | 0 | 308.7 | 100.57 | 15693 | 15694 | 318
03/26/22 10:30:56.202 | 585.4805 | 1370.3121 | 53.7559 | 43.5319 | 10.2239 | 30.9309 | 50.9063 | 0 | 1784.9832 | 89.0291 | 79.9713 | 9.0578 | 25.1151 | 69.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9791 | 461.0701 | 458.3601 | 462.2401 | 411.0201 | 442.6101 | 420.0101 | 314.6901 | 0.53749 | 0.54455 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7053003.2326 | 8082635.4677 | 8082635.4677 | 62.4292 | 62.1887 | 1.0018 | 0.998 | 685927.2059 | 890938.4901 | 460.5568 | 0.47696 | 0 | 0 | 30.9309 | 25.1151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017911 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 610.98 | 1367.9907 | 55.0221 | 44.3315 | 30.8572 | 1787.2602 | 77.0122 | 25.3346 | 459.896 | 0.0065146 | 60.0015 | 0.52342 | 1.0891 | 86.361 | 2.3663 | 0.84829 | 0.55023 | 4.3435 | 2.266 | 0.56491 | 0 | 100 | 578.2 | 319 | 106.3 | 103.51 | 100.56 | 308 | 3 | 90.96 | 41.93 | 4 | 37.14 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.4 | 0 | 37.91 | 64 | 64 | 100.25 | 87.7 | 84.69 | 0 | 100.56 | 2.26 | 89.95 | 42.7 | 106.28 | 12.54 | 103.51 | 110 | 0 | 15694 | 80.11 | 114.93 | 219.04 | 213.11 | 218.5 | 0 | 34.93 | 49.94 | 13234 | 90.96 | 41.93 | 37.14 | 0.87 | 41.93 | 0 | 606 | 430.9 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 312.4 | 0 | 306.1 | 100.57 | 15694 | 15694 | 315
03/26/22 10:31:01.202 | 584.2277 | 1367.6439 | 53.7582 | 43.5363 | 10.222 | 31.3095 | 50.9241 | 0 | 1790.5364 | 89.0314 | 79.9744 | 9.057 | 24.862 | 69.5959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.975 | 460.98 | 458.26 | 462.17 | 411.17 | 442.87 | 420.06 | 314.72 | 0.53869 | 0.063883 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7038248.8225 | 8106834.7367 | 8106834.7367 | 62.4292 | 62.1887 | 1.0018 | 0.998 | 684591.4816 | 893709.8477 | 460.47 | 0.47994 | 0 | 0 | 31.3095 | 24.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017915 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 610.6797 | 1368.0159 | 55.0104 | 44.3253 | 30.8623 | 1787.2918 | 77.0546 | 25.3285 | 459.9011 | 0.0065254 | 60.0015 | 0.52353 | 1.0769 | 86.4001 | 2.3584 | 0.8511 | 0.55286 | 4.3443 | 2.2495 | 0.56676 | 0 | 100 | 578.5 | 317 | 106.25 | 103.51 | 100.61 | 308.6 | 3 | 90.94 | 41.94 | 4 | 37.15 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.43 | 0 | 37.93 | 64 | 64 | 100.2 | 87.67 | 84.71 | 0 | 100.61 | 2.26 | 89.96 | 42.71 | 106.28 | 12.57 | 103.51 | 110 | 0 | 15694 | 80.11 | 114.9 | 219.04 | 213.11 | 218.5 | 0 | 34.79 | 49.79 | 13239 | 90.95 | 41.94 | 37.16 | 0.85 | 41.94 | 0 | 605 | 427.3 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.8 | 315.1 | 0 | 308.8 | 100.66 | 15693 | 15694 | 318
03/26/22 10:31:06.202 | 583.9571 | 1366.8491 | 53.7592 | 43.5383 | 10.2209 | 31.6007 | 50.9251 | 0 | 1787.3779 | 89.0334 | 79.9766 | 9.0568 | 24.4634 | 69.6099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9751 | 460.9801 | 458.2601 | 462.1701 | 411.1701 | 442.8701 | 420.0601 | 314.7201 | 0.53894 | 0.18895 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7035293.1093 | 8093854.3474 | 8093854.3474 | 62.4292 | 62.1887 | 1.0018 | 0.998 | 684325.3617 | 892334.0479 | 460.4701 | 0.47994 | 0 | 0 | 31.6007 | 24.4634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017917 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 610.3757 | 1368.0341 | 54.9984 | 44.3189 | 30.8685 | 1787.3228 | 77.0969 | 25.321 | 459.9053 | 0.0065346 | 60.0013 | 0.52365 | 1.0643 | 86.4391 | 2.3364 | 0.85351 | 0.55526 | 4.3248 | 2.2325 | 0.56815 | 0 | 100 | 578.7 | 316 | 106.3 | 103.51 | 100.64 | 306 | 3 | 90.96 | 41.95 | 4 | 37.16 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.43 | 0 | 37.93 | 64 | 64 | 100.23 | 87.69 | 84.71 | 0 | 100.64 | 2.26 | 89.96 | 42.71 | 106.3 | 12.54 | 103.51 | 110 | 0 | 15694 | 80.11 | 114.88 | 219.16 | 213.21 | 218.62 | 0 | 34.72 | 49.75 | 13244 | 90.96 | 41.95 | 37.16 | 0.84 | 41.95 | 0 | 605 | 430.7 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 311.8 | 0 | 305.6 | 100.61 | 15693 | 15694 | 314
03/26/22 10:31:11.202 | 585.159 | 1370.3328 | 53.7613 | 43.5431 | 10.2182 | 31.5295 | 50.9011 | 0 | 1782.1137 | 89.0415 | 79.9847 | 9.0568 | 24.3173 | 69.6223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.969 | 460.89 | 458.17 | 462.08 | 411.24 | 443.07 | 420.07 | 314.73 | 0.53785 | 0.68819 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7049672.4081 | 8067895.496 | 8067895.496 | 62.4292 | 62.1886 | 1.0018 | 0.998 | 685937.2934 | 889504.4115 | 460.38 | 0.48004 | 0 | 0 | 31.5295 | 24.3173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017926 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 610.0714 | 1368.0566 | 54.9862 | 44.3122 | 30.8749 | 1787.3526 | 77.1388 | 25.3118 | 459.9093 | 0.0065432 | 60.0011 | 0.52378 | 1.0524 | 86.4777 | 2.3087 | 0.85538 | 0.55735 | 4.2877 | 2.215 | 0.56921 | 0 | 100 | 578.6 | 316 | 106.38 | 103.53 | 100.63 | 308.5 | 3 | 90.99 | 41.95 | 4 | 37.16 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.45 | 0 | 37.94 | 62 | 62 | 100.3 | 87.71 | 84.71 | 0 | 100.63 | 2.26 | 89.98 | 42.73 | 106.35 | 12.53 | 103.53 | 110 | 0 | 15694 | 80.11 | 114.88 | 219.16 | 213.21 | 218.62 | 0 | 34.67 | 49.77 | 13250 | 91 | 41.95 | 37.16 | 0.84 | 41.95 | 0 | 605 | 432.3 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.4 | 313.6 | 0 | 307.4 | 100.59 | 15694 | 15694 | 316
03/26/22 10:31:16.202 | 586.1688 | 1372.9288 | 53.7622 | 43.5457 | 10.2165 | 30.8374 | 50.9065 | 0 | 1783.8116 | 89.0473 | 79.9909 | 9.0564 | 25.2638 | 69.6347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9691 | 460.8901 | 458.1701 | 462.0801 | 411.2401 | 443.0701 | 420.0701 | 314.7301 | 0.53693 | 0.72598 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7061232.7223 | 8076289.4467 | 8076289.4467 | 62.4291 | 62.1885 | 1.0018 | 0.998 | 687236.7141 | 890351.0803 | 460.3801 | 0.48004 | 0 | 0 | 30.8374 | 25.2638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016209 | 0.017907 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 609.7695 | 1368.0909 | 54.9737 | 44.3052 | 30.8758 | 1787.3532 | 77.1806 | 25.3091 | 459.913 | 0.0065511 | 60.0009 | 0.5239 | 1.0426 | 86.5162 | 2.335 | 0.8567 | 0.55906 | 4.2872 | 2.1973 | 0.57011 | 0 | 100 | 578.2 | 315 | 106.35 | 103.53 | 100.56 | 306.8 | 3 | 90.99 | 41.95 | 4 | 37.16 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.5 | 0 | 37.93 | 62 | 62 | 100.4 | 87.78 | 84.77 | 0 | 100.56 | 2.27 | 90.01 | 42.71 | 106.35 | 12.54 | 103.53 | 110 | 0 | 15694 | 80.11 | 114.88 | 219.16 | 213.21 | 218.62 | 0 | 34.65 | 49.79 | 13255 | 90.99 | 41.95 | 37.16 | 0.84 | 41.95 | 0 | 606 | 431.6 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 312.7 | 0 | 306.4 | 100.64 | 15693 | 15694 | 315
03/26/22 10:31:21.202 | 586.2495 | 1373.0629 | 53.7634 | 43.549 | 10.2144 | 31.6943 | 50.9075 | 0 | 1791.388 | 89.0558 | 80.001 | 9.0549 | 23.9754 | 69.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9721 | 460.8801 | 458.1401 | 462.0701 | 411.2701 | 443.1501 | 420.0301 | 314.7501 | 0.53689 | 0.3635 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7063046.8223 | 8107493.5353 | 8107493.5353 | 62.4291 | 62.1885 | 1.0018 | 0.998 | 687451.0829 | 894085.1545 | 460.3634 | 0.48295 | 0 | 0 | 31.6943 | 23.9754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016213 | 0.017908 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 609.4668 | 1368.1186 | 54.9611 | 44.2982 | 30.88 | 1787.397 | 77.2224 | 25.3014 | 459.9165 | 0.0065588 | 60.0008 | 0.52403 | 1.031 | 86.5546 | 2.3642 | 0.85774 | 0.56059 | 4.288 | 2.1788 | 0.57091 | 0 | 100 | 578.9 | 315 | 106.4 | 103.53 | 100.68 | 308 | 3 | 91.02 | 41.95 | 4 | 37.16 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.53 | 0 | 37.94 | 62 | 62 | 100.48 | 87.82 | 84.77 | 0 | 100.68 | 2.27 | 90.02 | 42.73 | 106.4 | 12.51 | 103.53 | 110 | 0 | 15694 | 80.11 | 114.88 | 219.16 | 213.21 | 218.62 | 0 | 34.63 | 49.82 | 13259 | 91.02 | 41.95 | 37.16 | 0.84 | 41.95 | 0 | 606 | 431.9 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.4 | 312.2 | 0 | 305.9 | 100.61 | 15693 | 15694 | 315
03/26/22 10:31:26.202 | 584.6324 | 1369.8425 | 53.7665 | 43.5538 | 10.2127 | 31.2824 | 50.9193 | 0 | 1783.8168 | 89.0709 | 80.0182 | 9.0527 | 24.4033 | 69.6087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.973 | 460.87 | 458.13 | 462.07 | 411.3 | 443.21 | 419.97 | 314.75 | 0.53837 | 0.5579 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7043126.1442 | 8071938.0881 | 8071938.0881 | 62.4291 | 62.1883 | 1.0018 | 0.998 | 685691.6366 | 890349.99 | 460.3567 | 0.48368 | 0 | 0 | 31.2824 | 24.4033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016214 | 0.017923 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 609.1537 | 1368.1297 | 54.9481 | 44.2908 | 30.8848 | 1787.4591 | 77.2639 | 25.2922 | 459.9201 | 0.0065665 | 60.0006 | 0.52416 | 1.0165 | 86.5928 | 2.3757 | 0.85809 | 0.56164 | 4.2681 | 2.1602 | 0.57165 | 0 | 100 | 578.6 | 316 | 106.45 | 103.55 | 100.63 | 308.6 | 3 | 91.04 | 41.95 | 4 | 37.16 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.55 | 0 | 37.93 | 62 | 62 | 100.5 | 87.84 | 84.69 | 0 | 100.63 | 2.27 | 90.03 | 42.71 | 106.45 | 12.51 | 103.55 | 110 | 0 | 15694 | 80.11 | 114.88 | 219.16 | 213.21 | 218.62 | 0 | 34.6 | 49.82 | 13264 | 91.04 | 41.95 | 37.16 | 0.84 | 41.95 | 0 | 606 | 431.4 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 314.5 | 0 | 308.2 | 100.61 | 15695 | 15694 | 316
03/26/22 10:31:31.202 | 584.5159 | 1369.538 | 53.7692 | 43.5562 | 10.2129 | 30.8041 | 50.9257 | 0 | 1786.676 | 89.0808 | 80.0292 | 9.0516 | 25.4545 | 69.6132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.973 | 460.87 | 458.13 | 462.07 | 411.3 | 443.21 | 419.97 | 314.75 | 0.53848 | 0.37208 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7041300.9798 | 8085133.0247 | 8085133.0247 | 62.4291 | 62.1882 | 1.0018 | 0.998 | 685539.0959 | 891775.6032 | 460.3567 | 0.48368 | 0 | 0 | 30.8041 | 25.4545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017908 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 608.8376 | 1368.1367 | 54.9351 | 44.2834 | 30.8842 | 1787.4916 | 77.3054 | 25.2938 | 459.9236 | 0.0065742 | 60.0005 | 0.5243 | 1.0032 | 86.6309 | 2.378 | 0.85811 | 0.56248 | 4.2396 | 2.141 | 0.57237 | 0 | 100 | 578.8 | 315 | 106.4 | 103.55 | 100.66 | 307.9 | 3 | 91.02 | 41.95 | 4 | 37.16 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.58 | 0 | 37.94 | 62 | 62 | 100.5 | 87.84 | 84.64 | 0 | 100.66 | 2.27 | 90.05 | 42.73 | 106.43 | 12.52 | 103.55 | 110 | 0 | 15694 | 80.14 | 114.9 | 219.16 | 213.21 | 218.62 | 0 | 34.57 | 49.84 | 13269 | 91.03 | 41.95 | 37.16 | 0.84 | 41.95 | 0 | 606 | 430 | 458.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 314.9 | 0 | 308.6 | 100.64 | 15693 | 15694 | 317
03/26/22 10:31:36.202 | 583.6038 | 1367.2155 | 53.7728 | 43.5587 | 10.2141 | 31.0262 | 50.9261 | 0 | 1788.8643 | 89.0925 | 80.0415 | 9.0509 | 25.41 | 69.6211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9831 | 460.9101 | 458.1601 | 462.1201 | 411.3301 | 443.2901 | 419.9001 | 314.7801 | 0.53937 | 0.091483 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7030313.5586 | 8096976.2323 | 8096976.2323 | 62.4291 | 62.1881 | 1.0018 | 0.998 | 684407.4374 | 893116.2812 | 460.3968 | 0.48581 | 0 | 0 | 31.0262 | 25.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017912 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 608.5207 | 1368.1324 | 54.9217 | 44.2756 | 30.8819 | 1787.5175 | 77.3465 | 25.2958 | 459.9276 | 0.0065828 | 60.0004 | 0.52444 | 0.98956 | 86.6687 | 2.379 | 0.85741 | 0.56275 | 4.2336 | 2.1218 | 0.57315 | 0 | 100 | 578.5 | 317 | 106.38 | 103.55 | 100.61 | 306.9 | 3 | 91 | 41.96 | 4 | 37.18 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.55 | 0 | 37.94 | 62 | 62 | 100.52 | 87.84 | 84.62 | 0 | 100.61 | 2.27 | 90.03 | 42.73 | 106.33 | 12.56 | 103.58 | 110 | 0 | 15694 | 80.14 | 114.9 | 219.16 | 213.21 | 218.62 | 0 | 34.51 | 49.79 | 13275 | 90.99 | 41.96 | 37.18 | 0.83 | 41.96 | 0 | 606 | 427.4 | 458.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 313.7 | 0 | 307.5 | 100.68 | 15693 | 15694 | 317
03/26/22 10:31:41.202 | 585.1319 | 1370.3483 | 53.7795 | 43.5618 | 10.2177 | 30.7396 | 50.934 | 0 | 1789.819 | 89.1097 | 80.0571 | 9.0526 | 25.7139 | 69.6198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9891 | 460.9801 | 458.1901 | 462.2001 | 411.3401 | 443.4101 | 419.7001 | 314.8001 | 0.538 | 0.27453 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7048652.5985 | 8100525.4101 | 8100525.4101 | 62.4291 | 62.1879 | 1.0018 | 0.998 | 685944.2476 | 893340.5979 | 460.4567 | 0.49226 | 0 | 0 | 30.7396 | 25.7139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016211 | 0.017903 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 608.2051 | 1368.1252 | 54.9084 | 44.2677 | 30.8812 | 1787.5454 | 77.3876 | 25.2957 | 459.9319 | 0.0065921 | 60.0003 | 0.52459 | 0.97628 | 86.7065 | 2.3764 | 0.8564 | 0.56282 | 4.2264 | 2.1019 | 0.57398 | 0 | 100 | 579 | 317 | 106.38 | 103.58 | 100.7 | 307.2 | 3 | 91 | 41.98 | 4 | 37.18 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.55 | 0 | 37.95 | 62 | 62 | 100.52 | 87.85 | 84.56 | 0 | 100.7 | 2.26 | 90.03 | 42.74 | 106.4 | 12.56 | 103.58 | 110 | 0 | 15694 | 80.14 | 114.9 | 219.16 | 213.21 | 218.62 | 0 | 34.48 | 49.83 | 13280 | 91.02 | 41.96 | 37.18 | 0.83 | 41.96 | 0 | 606 | 431.8 | 458.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.6 | 313.4 | 0 | 307.1 | 100.63 | 15694 | 15694 | 315
03/26/22 10:31:46.201 | 584.2682 | 1367.9226 | 53.7843 | 43.5636 | 10.2207 | 30.7765 | 50.9241 | 0 | 1791.1454 | 89.1194 | 80.0644 | 9.055 | 25.103 | 69.6293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.989 | 460.98 | 458.19 | 462.2 | 411.34 | 443.41 | 419.7 | 314.8 | 0.53879 | 0.055346 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7038272.3676 | 8107925.5452 | 8107925.5452 | 62.4291 | 62.1878 | 1.0018 | 0.998 | 684729.8451 | 894001.6504 | 460.4567 | 0.49226 | 0 | 0 | 30.7765 | 25.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016215 | 0.017907 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 607.8865 | 1368.0881 | 54.8949 | 44.2596 | 30.8825 | 1787.609 | 77.4283 | 25.2902 | 459.9365 | 0.006602 | 60.0003 | 0.52474 | 0.95869 | 86.744 | 2.3264 | 0.85486 | 0.56229 | 4.1935 | 2.0823 | 0.57487 | 0 | 100 | 578.5 | 318 | 106.43 | 103.58 | 100.64 | 308 | 3 | 91.02 | 41.96 | 4 | 37.18 | 42.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.55 | 0 | 37.95 | 62 | 62 | 100.58 | 87.88 | 84.5 | 0 | 100.64 | 2.26 | 90.03 | 42.74 | 106.43 | 12.56 | 103.58 | 110 | 0 | 15694 | 80.14 | 114.9 | 219.16 | 213.21 | 218.73 | 0 | 34.49 | 49.92 | 13285 | 91.02 | 41.96 | 37.18 | 0.85 | 41.96 | 0 | 606 | 430.5 | 458.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 315.1 | 0 | 308.8 | 100.64 | 15692 | 15694 | 317
03/26/22 10:31:51.201 | 584.6123 | 1368.16 | 53.79 | 43.5656 | 10.2243 | 31.0216 | 50.916 | 0 | 1785.3445 | 89.1296 | 80.0713 | 9.0583 | 24.534 | 69.6331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9901 | 461.0601 | 458.2401 | 462.2801 | 411.3501 | 443.3901 | 419.5301 | 314.8001 | 0.53848 | 0.34693 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7042505.5295 | 8088536.8342 | 8088536.8342 | 62.4291 | 62.1877 | 1.0018 | 0.998 | 684925.9728 | 891656.7146 | 460.5268 | 0.49653 | 0 | 0 | 31.0216 | 24.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016214 | 0.017914 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 607.5967 | 1368.0766 | 54.8814 | 44.2511 | 30.886 | 1787.6011 | 77.4683 | 25.2818 | 459.9414 | 0.0066125 | 60.0003 | 0.52486 | 0.94652 | 86.7812 | 2.3201 | 0.85308 | 0.56121 | 4.1944 | 2.0632 | 0.57591 | 0 | 100 | 578.5 | 316 | 106.48 | 103.58 | 100.63 | 308.4 | 3 | 91.06 | 41.95 | 4 | 37.16 | 42.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.58 | 0 | 37.94 | 62 | 62 | 100.55 | 87.86 | 84.43 | 0 | 100.63 | 2.27 | 90.05 | 42.73 | 106.48 | 12.52 | 103.58 | 110 | 0 | 15694 | 80.14 | 114.9 | 219.16 | 213.21 | 218.73 | 0 | 34.5 | 49.91 | 13290 | 91.06 | 41.95 | 37.16 | 0.86 | 41.95 | 0 | 606 | 431.5 | 458.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 314.7 | 0 | 308.4 | 100.61 | 15693 | 15694 | 316
03/26/22 10:31:56.202 | 584.0621 | 1366.7407 | 53.7926 | 43.5667 | 10.2259 | 31.1511 | 50.9245 | 0 | 1783.2336 | 89.1339 | 80.074 | 9.0598 | 24.3988 | 69.6326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.99 | 461.06 | 458.24 | 462.28 | 411.35 | 443.39 | 419.53 | 314.8 | 0.53898 | 0.42835 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7036105.1006 | 8075581.2012 | 8075581.2012 | 62.4291 | 62.1877 | 1.0018 | 0.998 | 684137.8737 | 890051.3774 | 460.5267 | 0.49653 | 0 | 0 | 31.1511 | 24.3988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017921 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 607.3191 | 1368.066 | 54.868 | 44.2425 | 30.8895 | 1787.5673 | 77.508 | 25.2742 | 459.9465 | 0.0066235 | 60.0003 | 0.52498 | 0.93565 | 86.8182 | 2.3218 | 0.85113 | 0.55979 | 4.205 | 2.0442 | 0.57702 | 0 | 100 | 578.2 | 315 | 106.53 | 103.6 | 100.56 | 306.9 | 3 | 91.09 | 41.96 | 4 | 37.18 | 42.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.65 | 0 | 37.94 | 62 | 62 | 100.65 | 87.92 | 84.37 | 0 | 100.56 | 2.27 | 90.09 | 42.73 | 106.55 | 12.52 | 103.6 | 110 | 0 | 15694 | 80.16 | 114.9 | 219.27 | 213.32 | 218.73 | 0 | 34.42 | 49.85 | 13294 | 91.08 | 41.96 | 37.18 | 0.85 | 41.96 | 0 | 606 | 432.3 | 458.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.1 | 313.7 | 0 | 307.4 | 100.54 | 15695 | 15694 | 315
03/26/22 10:32:01.202 | 584.1383 | 1366.2401 | 53.802 | 43.571 | 10.231 | 29.8096 | 50.9071 | 0 | 1786.2631 | 89.1489 | 80.0851 | 9.0638 | 26.4115 | 69.6541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9941 | 461.1201 | 458.2701 | 462.3201 | 411.3401 | 443.2201 | 419.3001 | 314.7301 | 0.53879 | 0.1828 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7035831.6241 | 8095162.4628 | 8095162.4628 | 62.4291 | 62.1875 | 1.0018 | 0.998 | 683886.86 | 891561.9867 | 460.5701 | 0.49938 | 0 | 0 | 29.8096 | 26.4115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017911 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 607.0619 | 1368.06 | 54.8548 | 44.2338 | 30.8906 | 1787.5297 | 77.5469 | 25.2681 | 459.9516 | 0.0066345 | 60.0003 | 0.52509 | 0.92488 | 86.8547 | 2.3291 | 0.84919 | 0.55801 | 4.2205 | 2.0258 | 0.57808 | 0 | 100 | 577.9 | 316 | 106.6 | 103.63 | 100.54 | 307.2 | 3 | 91.12 | 41.95 | 4 | 37.16 | 42.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.67 | 0 | 37.94 | 62 | 62 | 100.7 | 87.95 | 84.3 | 0 | 100.52 | 2.27 | 90.11 | 42.73 | 106.58 | 12.54 | 103.65 | 110 | 0 | 15694 | 80.16 | 114.9 | 219.27 | 213.32 | 218.73 | 0 | 34.36 | 49.77 | 13299 | 91.11 | 41.95 | 37.16 | 0.9 | 41.95 | 0 | 606 | 427.8 | 458.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.9 | 313.4 | 0 | 307.2 | 100.5 | 15693 | 15694 | 316
03/26/22 10:32:06.201 | 585.171 | 1368.449 | 53.8062 | 43.5731 | 10.2331 | 29.975 | 50.9117 | 0 | 1789.8345 | 89.1566 | 80.091 | 9.0656 | 26.2399 | 69.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9871 | 461.1001 | 458.2401 | 462.3001 | 411.3701 | 443.2001 | 419.2301 | 314.7201 | 0.53783 | 0.13872 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7048363.6052 | 8111007.5903 | 8111007.5903 | 62.429 | 62.1875 | 1.0018 | 0.998 | 684976.9019 | 893184.1613 | 460.5467 | 0.50085 | 0 | 0 | 29.975 | 26.2399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017908 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 606.8199 | 1368.0628 | 54.8418 | 44.2251 | 30.8854 | 1787.5239 | 77.5855 | 25.2711 | 459.9573 | 0.0066468 | 60.0003 | 0.52518 | 0.91258 | 86.891 | 2.3292 | 0.84721 | 0.55599 | 4.2171 | 2.0076 | 0.57911 | 0 | 100 | 578.2 | 317 | 106.45 | 103.65 | 100.56 | 307.1 | 3 | 91.04 | 41.94 | 4 | 37.15 | 42.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.6 | 0 | 37.93 | 62 | 62 | 100.65 | 87.92 | 84.26 | 0 | 100.52 | 2.27 | 90.06 | 42.71 | 106.45 | 12.6 | 103.65 | 110 | 0 | 15694 | 80.16 | 114.88 | 219.27 | 213.32 | 218.73 | 0 | 34.26 | 49.67 | 13304 | 91.06 | 41.94 | 37.15 | 0.93 | 41.94 | 0 | 606 | 429.1 | 458.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.2 | 314.8 | 0 | 308.5 | 100.56 | 15693 | 15694 | 316
03/26/22 10:32:11.201 | 585.1657 | 1368.2323 | 53.8081 | 43.574 | 10.2341 | 30.7483 | 50.9234 | 0 | 1790.33 | 89.1604 | 80.0936 | 9.0668 | 25.3091 | 69.6764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9871 | 461.1001 | 458.2401 | 462.3001 | 411.3701 | 443.2001 | 419.2301 | 314.7201 | 0.53783 | 0.097544 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7049023.2938 | 8114972.7224 | 8114972.7224 | 62.429 | 62.1874 | 1.0018 | 0.998 | 684883.7933 | 893590.692 | 460.5468 | 0.50085 | 0 | 0 | 30.7483 | 25.3091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.0179 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 606.5891 | 1368.0544 | 54.8291 | 44.2164 | 30.8843 | 1787.5515 | 77.6233 | 25.2708 | 459.9631 | 0.0066593 | 60.0004 | 0.52526 | 0.89754 | 86.9267 | 2.3258 | 0.84545 | 0.55384 | 4.2191 | 1.9903 | 0.57974 | 0 | 100 | 578.5 | 316 | 106.45 | 103.65 | 100.61 | 306.9 | 3 | 91.04 | 41.95 | 4 | 37.16 | 42.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.6 | 0 | 37.94 | 62 | 62 | 100.68 | 87.93 | 84.22 | 0 | 100.54 | 2.27 | 90.06 | 42.73 | 106.45 | 12.61 | 103.65 | 110 | 0 | 15694 | 80.16 | 114.88 | 219.27 | 213.32 | 218.73 | 0 | 34.19 | 49.67 | 13309 | 91.04 | 41.95 | 37.16 | 0.9 | 41.95 | 0 | 605 | 431.1 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 313.1 | 0 | 306.9 | 100.61 | 15693 | 15694 | 316
03/26/22 10:32:16.201 | 584.8586 | 1367.0194 | 53.8143 | 43.5764 | 10.2378 | 30.9473 | 50.9226 | 0 | 1787.5224 | 89.174 | 80.1019 | 9.0721 | 24.8637 | 69.6665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9831 | 461.1001 | 458.2301 | 462.2701 | 411.3701 | 443.0201 | 419.1101 | 314.6701 | 0.53803 | 0.15937 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7045489.5131 | 8106394.697 | 8106394.697 | 62.429 | 62.1873 | 1.0018 | 0.998 | 684276.4196 | 892188.2427 | 460.5334 | 0.50014 | 0 | 0 | 30.9473 | 24.8637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017913 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 606.3706 | 1368.0484 | 54.8167 | 44.2078 | 30.8861 | 1787.5986 | 77.6604 | 25.2655 | 459.9691 | 0.0066724 | 60.0005 | 0.52533 | 0.88139 | 86.9621 | 2.3264 | 0.84389 | 0.55163 | 4.2239 | 1.9736 | 0.58006 | 0 | 100 | 578.2 | 317 | 106.55 | 103.65 | 100.56 | 305.4 | 3 | 91.09 | 41.95 | 4 | 37.16 | 42.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.65 | 0 | 37.94 | 62 | 62 | 100.65 | 87.92 | 84.13 | 0 | 100.56 | 2.27 | 90.09 | 42.73 | 106.55 | 12.56 | 103.65 | 110 | 0 | 15694 | 80.18 | 114.88 | 219.27 | 213.32 | 218.73 | 0 | 34.09 | 49.59 | 13314 | 91.09 | 41.95 | 37.16 | 0.9 | 41.95 | 0 | 606 | 430.9 | 458.8 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.4 | 314 | 0 | 307.7 | 100.59 | 15695 | 15694 | 316
03/26/22 10:32:21.201 | 585.0546 | 1367.3652 | 53.8156 | 43.5769 | 10.2387 | 31.5408 | 50.9129 | 0 | 1788.0488 | 89.1771 | 80.1034 | 9.0737 | 24.0762 | 69.6929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.983 | 461.1 | 458.23 | 462.27 | 411.37 | 443.02 | 419.11 | 314.67 | 0.53785 | 0.15673 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7048369.5344 | 8109347.9156 | 8109347.9156 | 62.429 | 62.1873 | 1.0018 | 0.998 | 684449.4454 | 892450.7922 | 460.5334 | 0.50014 | 0 | 0 | 31.5408 | 24.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017906 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 606.1634 | 1368.0458 | 54.8045 | 44.1992 | 30.8905 | 1787.6063 | 77.6971 | 25.2553 | 459.9754 | 0.006686 | 60.0005 | 0.52539 | 0.86712 | 86.997 | 2.327 | 0.84248 | 0.54941 | 4.2234 | 1.9572 | 0.58 | 0 | 100 | 578.2 | 318 | 106.5 | 103.65 | 100.57 | 308.2 | 3 | 91.07 | 41.94 | 4 | 37.15 | 42.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.63 | 0 | 37.93 | 62 | 62 | 100.63 | 87.91 | 84.07 | 0 | 100.57 | 2.27 | 90.07 | 42.71 | 106.5 | 12.58 | 103.65 | 110 | 0 | 15694 | 80.2 | 114.86 | 219.27 | 213.32 | 218.73 | 0 | 34.02 | 49.61 | 13319 | 91.07 | 41.94 | 37.15 | 0.91 | 41.94 | 0 | 606 | 428.5 | 458.8 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 314.5 | 0 | 308.2 | 100.57 | 15693 | 15694 | 315
03/26/22 10:32:26.201 | 585.1334 | 1367.2723 | 53.8186 | 43.5778 | 10.2408 | 30.9271 | 50.915 | 0 | 1788.1159 | 89.1844 | 80.1063 | 9.0781 | 25.0155 | 69.6834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9801 | 461.1001 | 458.2301 | 462.2501 | 411.4201 | 442.9701 | 419.1401 | 314.6601 | 0.53776 | 0.096356 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7048774.1026 | 8114615.5889 | 8114615.5889 | 62.429 | 62.1873 | 1.0018 | 0.998 | 684402.8126 | 892483.8746 | 460.5268 | 0.4987 | 0 | 0 | 30.9271 | 25.0155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.01791 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 605.9763 | 1368.0437 | 54.793 | 44.191 | 30.8946 | 1787.5824 | 77.7326 | 25.2437 | 459.9819 | 0.0067 | 60.0006 | 0.52544 | 0.85478 | 87.0311 | 2.3267 | 0.84166 | 0.54749 | 4.1997 | 1.9425 | 0.57959 | 0 | 100 | 578.9 | 318 | 106.55 | 103.65 | 100.66 | 308.8 | 3 | 91.09 | 41.96 | 4 | 37.18 | 42.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.7 | 0 | 37.95 | 62 | 62 | 100.7 | 87.95 | 84.07 | 0 | 100.66 | 2.27 | 90.1 | 42.74 | 106.58 | 12.54 | 103.65 | 110 | 0 | 15694 | 80.2 | 114.86 | 219.27 | 213.32 | 218.73 | 0 | 34.01 | 49.72 | 13324 | 91.11 | 41.96 | 37.18 | 0.89 | 41.96 | 0 | 606 | 431.8 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579 | 313.5 | 0 | 307.2 | 100.7 | 15693 | 15694 | 318
03/26/22 10:32:31.201 | 584.4408 | 1365.466 | 53.8205 | 43.5783 | 10.2422 | 29.8512 | 50.9249 | 0 | 1791.1815 | 89.1889 | 80.1086 | 9.0803 | 26.814 | 69.7045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9791 | 461.0901 | 458.1701 | 462.1901 | 411.6301 | 442.9101 | 419.0401 | 314.6601 | 0.5384 | -0.23903 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7039483.3207 | 8132563.5866 | 8132563.5866 | 62.429 | 62.1872 | 1.0018 | 0.998 | 683498.5497 | 894013.6773 | 460.4834 | 0.50237 | 0 | 0 | 29.8512 | 26.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017903 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 605.7961 | 1368.0395 | 54.7818 | 44.183 | 30.8922 | 1787.5506 | 77.7673 | 25.2443 | 459.9884 | 0.006714 | 60.0007 | 0.52548 | 0.84294 | 87.0645 | 2.3287 | 0.84119 | 0.54587 | 4.1699 | 1.9286 | 0.5791 | 0 | 100 | 578.5 | 317 | 106.48 | 103.65 | 100.61 | 307.8 | 3 | 91.06 | 41.96 | 4 | 37.18 | 42.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.65 | 0 | 37.95 | 62 | 62 | 100.65 | 87.93 | 84.03 | 0 | 100.66 | 2.27 | 90.09 | 42.74 | 106.48 | 12.58 | 103.65 | 110 | 0 | 15694 | 80.2 | 114.86 | 219.27 | 213.32 | 218.73 | 0 | 33.97 | 49.71 | 13329 | 91.06 | 41.96 | 37.18 | 0.89 | 41.96 | 0 | 605 | 430.7 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 314 | 0 | 307.8 | 100.61 | 15693 | 15694 | 317
03/26/22 10:32:36.201 | 583.9783 | 1364.1654 | 53.8221 | 43.5784 | 10.2437 | 30.3625 | 50.9268 | 0 | 1794.9646 | 89.1936 | 80.1117 | 9.082 | 26.0096 | 69.6805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9761 | 461.0801 | 458.1301 | 462.1401 | 411.8401 | 442.9301 | 418.9801 | 314.6901 | 0.53887 | -0.50278 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7034336.943 | 8148868.9042 | 8148868.9042 | 62.429 | 62.1872 | 1.0018 | 0.998 | 682878.48 | 895759.8448 | 460.4501 | 0.50385 | 0 | 0 | 30.3625 | 26.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017887 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 605.6127 | 1368.0232 | 54.7708 | 44.1751 | 30.8873 | 1787.546 | 77.8018 | 25.2495 | 459.995 | 0.0067283 | 60.0007 | 0.52552 | 0.82895 | 87.0977 | 2.342 | 0.84072 | 0.54429 | 4.1646 | 1.9146 | 0.57789 | 0 | 100 | 578.3 | 317 | 106.43 | 103.65 | 100.57 | 307.7 | 3 | 91.03 | 41.95 | 4 | 37.16 | 42.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.58 | 0 | 37.94 | 62 | 62 | 100.68 | 87.92 | 83.96 | 0 | 100.57 | 2.27 | 90.05 | 42.71 | 106.43 | 12.62 | 103.65 | 110 | 0 | 15694 | 80.22 | 114.86 | 219.27 | 213.32 | 218.73 | 0 | 33.92 | 49.71 | 13334 | 91.03 | 41.95 | 37.16 | 0.9 | 41.95 | 0 | 605 | 431.4 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 313.7 | 0 | 307.4 | 100.57 | 15693 | 15694 | 317
03/26/22 10:32:41.201 | 584.1861 | 1364.5267 | 53.8232 | 43.5784 | 10.2448 | 30.6792 | 50.9354 | 0 | 1794.7942 | 89.1962 | 80.1133 | 9.0829 | 25.3289 | 69.6818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9761 | 461.0801 | 458.1301 | 462.1401 | 411.8401 | 442.9301 | 418.9801 | 314.6901 | 0.53868 | -0.47566 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7037134.661 | 8149573.5306 | 8149573.5306 | 62.429 | 62.1872 | 1.0018 | 0.998 | 683028.2576 | 895816.2131 | 460.4501 | 0.50385 | 0 | 0 | 30.6792 | 25.3289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017893 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 605.4301 | 1368.0155 | 54.7602 | 44.1677 | 30.8862 | 1787.5725 | 77.8353 | 25.2491 | 460.0018 | 0.0067429 | 60.0008 | 0.52557 | 0.81349 | 87.1299 | 2.3513 | 0.84059 | 0.54327 | 4.1956 | 1.9017 | 0.57607 | 0 | 100 | 578.5 | 315 | 106.43 | 103.63 | 100.61 | 306.2 | 3 | 91.03 | 41.96 | 4 | 37.18 | 42.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.58 | 0 | 37.95 | 62 | 62 | 100.65 | 87.92 | 83.94 | 0 | 100.61 | 2.27 | 90.05 | 42.74 | 106.43 | 12.6 | 103.63 | 110 | 0 | 15694 | 80.22 | 114.88 | 219.27 | 213.32 | 218.73 | 0 | 33.87 | 49.69 | 13339 | 91.03 | 41.96 | 37.18 | 0.89 | 41.96 | 0 | 605 | 432 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 312.4 | 0 | 306.2 | 100.61 | 15691 | 15694 | 315
03/26/22 10:32:46.201 | 585.7726 | 1368.4593 | 53.8268 | 43.5781 | 10.2488 | 31.3757 | 50.9164 | 0 | 1789.8397 | 89.2016 | 80.1163 | 9.0853 | 24.1143 | 69.6884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9741 | 461.0801 | 458.1001 | 462.1201 | 412.0301 | 443.0301 | 419.0001 | 314.7601 | 0.53734 | -0.025116 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7056896.5273 | 8132944.1251 | 8132944.1251 | 62.429 | 62.1871 | 1.0018 | 0.998 | 684642.7358 | 893940.5298 | 460.4334 | 0.50677 | 0 | 0 | 31.3757 | 24.1143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017891 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 605.2529 | 1368.0258 | 54.7498 | 44.1605 | 30.8935 | 1787.5871 | 77.8685 | 25.2334 | 460.0083 | 0.0067571 | 60.0008 | 0.52561 | 0.80044 | 87.1617 | 2.346 | 0.84051 | 0.54247 | 4.2031 | 1.889 | 0.57421 | 0 | 100 | 579 | 317 | 106.53 | 103.63 | 100.7 | 305.3 | 3 | 91.09 | 41.99 | 4 | 37.2 | 42.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.6 | 0 | 37.98 | 62 | 62 | 100.65 | 87.92 | 83.96 | 0 | 100.73 | 2.26 | 90.06 | 42.76 | 106.53 | 12.53 | 103.63 | 110 | 0 | 15694 | 80.22 | 114.88 | 219.39 | 213.32 | 218.85 | 0 | 33.77 | 49.65 | 13344 | 91.08 | 41.99 | 37.2 | 0.86 | 41.99 | 0 | 605 | 431.8 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579 | 315.5 | 0 | 309.3 | 100.7 | 15693 | 15694 | 317
03/26/22 10:32:51.201 | 586.4891 | 1368.7535 | 53.8308 | 43.5774 | 10.2534 | 30.858 | 50.9115 | 0 | 1786.9495 | 89.2046 | 80.1162 | 9.0884 | 24.7925 | 69.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.972 | 461.08 | 458.05 | 462.1 | 412.19 | 443.1 | 418.95 | 314.77 | 0.5367 | 0.25607 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7065011.3759 | 8118269.6972 | 8118269.6972 | 62.429 | 62.1871 | 1.0018 | 0.998 | 685143.7047 | 891900.374 | 460.41 | 0.51259 | 0 | 0 | 30.858 | 24.7925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017895 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 605.0749 | 1368.0385 | 54.7396 | 44.1535 | 30.8976 | 1787.584 | 77.9014 | 25.2248 | 460.0148 | 0.0067711 | 60.0008 | 0.52566 | 0.78872 | 87.1931 | 2.3421 | 0.84045 | 0.54185 | 4.202 | 1.8763 | 0.57234 | 0 | 100 | 578.1 | 316 | 106.6 | 103.65 | 100.64 | 306.7 | 3 | 91.12 | 41.98 | 4 | 37.19 | 42.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.67 | 0 | 37.96 | 62 | 62 | 100.7 | 87.95 | 83.98 | 0 | 100.66 | 2.27 | 90.1 | 42.75 | 106.6 | 12.53 | 103.65 | 110 | 0 | 15694 | 80.22 | 114.88 | 219.39 | 213.42 | 218.85 | 0 | 33.7 | 49.69 | 13349 | 91.12 | 41.98 | 37.19 | 0.91 | 41.98 | 0 | 605 | 430.1 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 314.2 | 0 | 307.9 | 100.61 | 15694 | 15694 | 317
03/26/22 10:32:56.201 | 586.0175 | 1367.4271 | 53.8346 | 43.5771 | 10.2575 | 31.0991 | 50.9106 | 0 | 1785.1019 | 89.2061 | 80.1147 | 9.0914 | 24.1574 | 69.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.972 | 461.08 | 458.05 | 462.1 | 412.19 | 443.1 | 418.95 | 314.77 | 0.53713 | 0.20453 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7059459.9465 | 8116881.282 | 8116881.282 | 62.429 | 62.1871 | 1.0018 | 0.998 | 684371.1451 | 891596.5415 | 460.41 | 0.51259 | 0 | 0 | 31.0991 | 24.1574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017898 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 604.888 | 1368.0477 | 54.7296 | 44.1469 | 30.8984 | 1787.551 | 77.9337 | 25.2197 | 460.0212 | 0.0067848 | 60.0007 | 0.52572 | 0.77885 | 87.2238 | 2.3355 | 0.84045 | 0.54155 | 4.1881 | 1.864 | 0.57028 | 0 | 100 | 578.4 | 317 | 106.53 | 103.65 | 100.57 | 307 | 3 | 91.08 | 41.96 | 4 | 37.18 | 42.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.67 | 0 | 37.95 | 62 | 62 | 100.73 | 87.96 | 83.92 | 0 | 100.57 | 2.27 | 90.1 | 42.74 | 106.55 | 12.56 | 103.65 | 110 | 0 | 15694 | 80.22 | 114.88 | 219.39 | 213.42 | 218.85 | 0 | 33.67 | 49.69 | 13354 | 91.09 | 41.96 | 37.18 | 0.91 | 41.96 | 0 | 605 | 429.6 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.4 | 313.3 | 0 | 307 | 100.59 | 15694 | 15694 | 317
03/26/22 10:33:01.201 | 586.2561 | 1367.5406 | 53.8357 | 43.5773 | 10.2584 | 30.9603 | 50.9125 | 0 | 1785.0296 | 89.2061 | 80.114 | 9.0921 | 24.3496 | 69.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.972 | 461.08 | 458.05 | 462.1 | 412.19 | 443.1 | 418.95 | 314.77 | 0.53692 | 0.29576 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7062280.9997 | 8112291.7419 | 8112291.7419 | 62.429 | 62.1871 | 1.0018 | 0.998 | 684536.3902 | 890942.4021 | 460.41 | 0.51259 | 0 | 0 | 30.9603 | 24.3496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017906 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 604.696 | 1368.0578 | 54.7197 | 44.1404 | 30.8994 | 1787.5154 | 77.9656 | 25.2158 | 460.0276 | 0.0067986 | 60.0007 | 0.52578 | 0.76947 | 87.254 | 2.3293 | 0.84042 | 0.5414 | 4.1822 | 1.8518 | 0.56814 | 0 | 100 | 579.1 | 316 | 106.55 | 103.65 | 100.71 | 307.8 | 3 | 91.11 | 41.98 | 4 | 37.19 | 42.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.73 | 0 | 37.95 | 62 | 62 | 100.73 | 87.96 | 83.9 | 0 | 100.7 | 2.27 | 90.13 | 42.74 | 106.58 | 12.54 | 103.65 | 110 | 0 | 15694 | 80.22 | 114.88 | 219.39 | 213.42 | 218.85 | 0 | 33.6 | 49.65 | 13359 | 91.11 | 41.98 | 37.19 | 0.9 | 41.98 | 0 | 606 | 430.7 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.1 | 314 | 0 | 307.8 | 100.71 | 15694 | 15694 | 316
03/26/22 10:33:06.200 | 586.5414 | 1367.8348 | 53.84 | 43.5788 | 10.2612 | 30.8438 | 50.8929 | 0 | 1782.1756 | 89.2065 | 80.1125 | 9.094 | 25.0861 | 69.6859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9711 | 461.0801 | 458.0001 | 462.0601 | 412.3801 | 443.1301 | 418.9101 | 314.8101 | 0.53672 | 0.46744 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7065607.9748 | 8101823.5121 | 8101823.5121 | 62.429 | 62.1871 | 1.0018 | 0.998 | 684683.453 | 889518.1093 | 460.3801 | 0.51696 | 0 | 0 | 30.8438 | 25.0861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017906 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 604.4868 | 1368.0491 | 54.7099 | 44.1343 | 30.9041 | 1787.483 | 77.997 | 25.2062 | 460.0339 | 0.0068122 | 60.0006 | 0.52586 | 0.75945 | 87.2835 | 2.3318 | 0.84037 | 0.54144 | 4.1962 | 1.8399 | 0.56585 | 0 | 100 | 578.7 | 316 | 106.63 | 103.68 | 100.64 | 306.1 | 3 | 91.13 | 41.98 | 4 | 37.19 | 42.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.8 | 0 | 37.96 | 62 | 62 | 100.8 | 88 | 83.88 | 0 | 100.64 | 2.27 | 90.17 | 42.75 | 106.6 | 12.55 | 103.68 | 110 | 0 | 15694 | 80.22 | 114.88 | 219.39 | 213.42 | 218.85 | 0 | 33.53 | 49.69 | 13364 | 91.12 | 41.98 | 37.19 | 0.9 | 41.98 | 0 | 605 | 429.7 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 313.9 | 0 | 307.7 | 100.68 | 15693 | 15694 | 315
03/26/22 10:33:11.200 | 586.6077 | 1367.9122 | 53.8413 | 43.5795 | 10.2618 | 31.01 | 50.9065 | 0 | 1782.3201 | 89.2072 | 80.1132 | 9.0939 | 24.8901 | 69.6847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.971 | 461.08 | 458 | 462.06 | 412.38 | 443.13 | 418.91 | 314.81 | 0.53666 | 0.47397 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7066551.7067 | 8102233.7972 | 8102233.7972 | 62.429 | 62.1871 | 1.0018 | 0.998 | 684722.1491 | 889590.148 | 460.38 | 0.51696 | 0 | 0 | 31.01 | 24.8901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017913 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 604.2814 | 1368.0504 | 54.7001 | 44.1282 | 30.9069 | 1787.4454 | 78.0283 | 25.2017 | 460.0401 | 0.0068257 | 60.0006 | 0.52594 | 0.75006 | 87.3129 | 2.3317 | 0.84019 | 0.54146 | 4.212 | 1.8276 | 0.5634 | 0 | 100 | 578.7 | 316 | 106.58 | 103.68 | 100.64 | 307.5 | 3 | 91.11 | 41.96 | 4 | 37.18 | 42.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.78 | 0 | 37.96 | 62 | 62 | 100.83 | 88.02 | 83.85 | 0 | 100.64 | 2.27 | 90.15 | 42.75 | 106.6 | 12.55 | 103.68 | 110 | 0 | 15694 | 80.22 | 114.88 | 219.39 | 213.42 | 218.85 | 0 | 33.58 | 49.82 | 13369 | 91.12 | 41.96 | 37.18 | 0.89 | 41.96 | 0 | 605 | 432.7 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.4 | 311.6 | 0 | 305.4 | 100.59 | 15695 | 15694 | 317
03/26/22 10:33:16.201 | 585.452 | 1365.213 | 53.8428 | 43.5809 | 10.2618 | 31.5002 | 50.9267 | 0 | 1778.9448 | 89.2096 | 80.1166 | 9.093 | 23.9446 | 69.7259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9771 | 461.0901 | 457.9901 | 462.0701 | 412.3801 | 443.1601 | 418.9701 | 314.8301 | 0.53776 | 0.52145 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7053058.6355 | 8084998.9333 | 8084998.9333 | 62.429 | 62.1871 | 1.0018 | 0.998 | 683370.9742 | 887905.0241 | 460.3834 | 0.51986 | 0 | 0 | 31.5002 | 23.9446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017922 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 604.0624 | 1368.0419 | 54.6904 | 44.1222 | 30.9147 | 1787.3813 | 78.0592 | 25.1874 | 460.0463 | 0.0068391 | 60.0005 | 0.52604 | 0.74265 | 87.3418 | 2.3392 | 0.83991 | 0.54156 | 4.2532 | 1.8155 | 0.56091 | 0 | 100 | 578.4 | 316 | 106.63 | 103.68 | 100.66 | 307.3 | 3 | 91.13 | 41.98 | 4 | 37.19 | 42.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.83 | 0 | 37.95 | 62 | 62 | 100.88 | 88.03 | 83.85 | 0 | 100.66 | 2.27 | 90.18 | 42.74 | 106.63 | 12.53 | 103.68 | 110 | 0 | 15694 | 80.22 | 114.88 | 219.39 | 213.42 | 218.85 | 0 | 33.51 | 49.73 | 13374 | 91.15 | 41.98 | 37.19 | 0.86 | 41.98 | 0 | 605 | 430.4 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 314.8 | 0 | 308.5 | 100.64 | 15692 | 15694 | 317
03/26/22 10:33:21.201 | 585.5289 | 1365.4917 | 53.8437 | 43.5826 | 10.2611 | 30.8824 | 50.9154 | 0 | 1779.688 | 89.2132 | 80.1212 | 9.092 | 25.0912 | 69.7408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9791 | 461.0901 | 458.0001 | 462.0801 | 412.3601 | 443.1501 | 419.0101 | 314.8301 | 0.53768 | 0.48007 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7053445.7751 | 8088764.9028 | 8088764.9028 | 62.429 | 62.187 | 1.0018 | 0.998 | 683510.4386 | 888275.3425 | 460.3901 | 0.51913 | 0 | 0 | 30.8824 | 25.0912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017914 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 603.8455 | 1368.0489 | 54.6806 | 44.1163 | 30.9213 | 1787.3168 | 78.0899 | 25.1753 | 460.0525 | 0.0068525 | 60.0005 | 0.52613 | 0.73626 | 87.3704 | 2.3287 | 0.83949 | 0.54166 | 4.3105 | 1.8032 | 0.55844 | 0 | 100 | 578.8 | 315 | 106.68 | 103.7 | 100.64 | 309.4 | 3 | 91.16 | 41.98 | 4 | 37.2 | 42.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.85 | 0 | 37.96 | 62 | 62 | 100.9 | 88.06 | 83.9 | 0 | 100.64 | 2.27 | 90.19 | 42.75 | 106.68 | 12.54 | 103.7 | 110 | 0 | 15694 | 80.22 | 114.88 | 219.39 | 213.42 | 218.85 | 0 | 33.42 | 49.69 | 13379 | 91.16 | 41.99 | 37.2 | 0.85 | 41.99 | 0 | 605 | 433.3 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 312 | 0 | 305.7 | 100.68 | 15694 | 15694 | 317
03/26/22 10:33:26.200 | 586.6164 | 1368.5625 | 53.8447 | 43.5845 | 10.2602 | 30.8863 | 50.9102 | 0 | 1782.9756 | 89.2177 | 80.1265 | 9.0912 | 25.2888 | 69.7127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9791 | 461.0901 | 458.0001 | 462.0801 | 412.3601 | 443.1501 | 419.0101 | 314.8301 | 0.53669 | 0.50259 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7066522.5272 | 8099954.7741 | 8099954.7741 | 62.429 | 62.187 | 1.0018 | 0.998 | 684827.9287 | 889536.9708 | 460.3901 | 0.51912 | 0 | 0 | 30.8863 | 25.2888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017915 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 603.6237 | 1368.0615 | 54.6708 | 44.1105 | 30.9231 | 1787.294 | 78.1203 | 25.1732 | 460.0587 | 0.0068658 | 60.0005 | 0.52623 | 0.72834 | 87.3986 | 2.3229 | 0.83888 | 0.54173 | 4.3267 | 1.791 | 0.55599 | 0 | 100 | 579.1 | 317 | 106.63 | 103.7 | 100.71 | 308.7 | 3 | 91.15 | 41.99 | 4 | 37.2 | 42.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.83 | 0 | 37.98 | 62 | 62 | 100.88 | 88.04 | 83.9 | 0 | 100.71 | 2.27 | 90.18 | 42.76 | 106.65 | 12.55 | 103.7 | 110 | 0 | 15694 | 80.22 | 114.88 | 219.39 | 213.42 | 218.85 | 0 | 33.37 | 49.81 | 13384 | 91.15 | 41.99 | 37.2 | 0.87 | 41.99 | 0 | 605 | 433.7 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 314.7 | 0 | 308.4 | 100.73 | 15693 | 15694 | 318
03/26/22 10:33:31.200 | 586.7774 | 1368.609 | 53.8448 | 43.5853 | 10.2596 | 30.9411 | 50.9127 | 0 | 1783.951 | 89.2202 | 80.1292 | 9.091 | 25.2846 | 69.6937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.979 | 461.09 | 458 | 462.08 | 412.36 | 443.15 | 419.01 | 314.83 | 0.53654 | 0.4349 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7068540.6469 | 8107448.4878 | 8107448.4878 | 62.429 | 62.187 | 1.0018 | 0.998 | 685070.752 | 890401.9847 | 460.39 | 0.51913 | 0 | 0 | 30.9411 | 25.2846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017915 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 603.4001 | 1368.0818 | 54.661 | 44.1048 | 30.9307 | 1787.2657 | 78.1505 | 25.1621 | 460.0649 | 0.0068791 | 60.0005 | 0.52633 | 0.7216 | 87.4264 | 2.3115 | 0.83808 | 0.54176 | 4.3318 | 1.7786 | 0.55345 | 0 | 100 | 578.7 | 317 | 106.7 | 103.7 | 100.68 | 308.7 | 3 | 91.17 | 41.99 | 4 | 37.2 | 42.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.88 | 0 | 37.99 | 62 | 62 | 100.9 | 88.06 | 83.88 | 0 | 100.68 | 2.27 | 90.21 | 42.78 | 106.73 | 12.51 | 103.7 | 110 | 0 | 15694 | 80.22 | 114.9 | 219.39 | 213.42 | 218.85 | 0 | 33.6 | 50.41 | 13389 | 91.19 | 42 | 37.21 | 0.87 | 42 | 0 | 605 | 433.6 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.1 | 313.8 | 0 | 307.5 | 100.71 | 15693 | 15694 | 316
03/26/22 10:33:36.201 | 587.909 | 1371.3288 | 53.8437 | 43.5881 | 10.2556 | 29.9389 | 50.9075 | 0 | 1787.6205 | 89.2308 | 80.1408 | 9.09 | 26.5689 | 69.7218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9901 | 461.0901 | 457.9901 | 462.0601 | 412.5901 | 443.2101 | 419.0901 | 314.9101 | 0.53564 | 0.44367 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7081316.9488 | 8119661.5271 | 8119661.5271 | 62.429 | 62.1869 | 1.0018 | 0.998 | 686626.0019 | 891670.5318 | 460.3801 | 0.51914 | 0 | 0 | 29.9389 | 26.5689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.01791 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 603.1744 | 1368.112 | 54.651 | 44.099 | 30.9254 | 1787.2481 | 78.1806 | 25.1703 | 460.0711 | 0.0068926 | 60.0006 | 0.52644 | 0.71474 | 87.454 | 2.3233 | 0.83705 | 0.5417 | 4.3285 | 1.7662 | 0.55081 | 0 | 100 | 579.5 | 316 | 106.65 | 103.72 | 100.78 | 306.9 | 3 | 91.15 | 41.99 | 4 | 37.2 | 42.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.8 | 0 | 37.98 | 62 | 62 | 100.85 | 88.03 | 83.92 | 0 | 100.78 | 2.27 | 90.17 | 42.76 | 106.6 | 12.6 | 103.72 | 110 | 0 | 15694 | 80.22 | 114.9 | 219.39 | 213.42 | 218.85 | 0 | 34.12 | 51.11 | 13394 | 91.12 | 41.99 | 37.2 | 0.88 | 41.99 | 0 | 605 | 432 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.3 | 313.9 | 0 | 307.7 | 100.75 | 15693 | 15694 | 317
03/26/22 10:33:41.201 | 585.6738 | 1366.8904 | 53.8438 | 43.5906 | 10.2531 | 30.687 | 50.9234 | 0 | 1792.0073 | 89.2399 | 80.1495 | 9.0904 | 25.591 | 69.7156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9901 | 461.0901 | 457.9801 | 462.0601 | 412.6601 | 443.2601 | 419.1101 | 314.9401 | 0.53774 | -0.17627 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7055040.8201 | 8143900.9301 | 8143900.9301 | 62.429 | 62.1868 | 1.0018 | 0.998 | 684210.5357 | 894420.295 | 460.3767 | 0.52059 | 0 | 0 | 30.687 | 25.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017903 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 602.9382 | 1368.1207 | 54.6409 | 44.0932 | 30.9228 | 1787.2719 | 78.2105 | 25.174 | 460.0773 | 0.0069059 | 60.0007 | 0.52656 | 0.70482 | 87.4815 | 2.3227 | 0.83582 | 0.54155 | 4.3358 | 1.7535 | 0.54803 | 0 | 100 | 579.2 | 316 | 106.55 | 103.72 | 100.73 | 308.3 | 3 | 91.08 | 42 | 4 | 37.21 | 42.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.73 | 0 | 37.99 | 62 | 62 | 100.8 | 88 | 83.98 | 0 | 100.73 | 2.27 | 90.13 | 42.78 | 106.53 | 12.64 | 103.72 | 110 | 0 | 15694 | 80.24 | 114.93 | 219.39 | 213.42 | 218.85 | 0 | 34.53 | 51.41 | 13399 | 91.08 | 42 | 37.21 | 0.87 | 42 | 0 | 605 | 431.3 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.4 | 312.8 | 0 | 306.5 | 100.77 | 15695 | 15694 | 315
03/26/22 10:33:46.200 | 585.7375 | 1368.0413 | 53.8458 | 43.5935 | 10.2523 | 31.9071 | 50.9276 | 0 | 1794.8097 | 89.2509 | 80.1587 | 9.0922 | 23.7587 | 69.7053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9951 | 461.1301 | 458.0101 | 462.0701 | 412.7601 | 443.2601 | 419.1001 | 314.9901 | 0.53777 | -0.32292 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7056605.0013 | 8157524.199 | 8157524.199 | 62.429 | 62.1867 | 1.0018 | 0.998 | 684337.0513 | 895951.979 | 460.4034 | 0.51983 | 0 | 0 | 31.9071 | 23.7587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017898 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 602.6869 | 1368.1112 | 54.6308 | 44.0874 | 30.9258 | 1787.3453 | 78.2403 | 25.1695 | 460.0834 | 0.0069191 | 60.0008 | 0.52669 | 0.6908 | 87.5087 | 2.3231 | 0.83429 | 0.54126 | 4.3557 | 1.7406 | 0.54518 | 0 | 100 | 579.2 | 316 | 106.55 | 103.72 | 100.77 | 306.4 | 3 | 91.09 | 42.01 | 4 | 37.23 | 42.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.75 | 0 | 38 | 62 | 62 | 100.83 | 88 | 83.94 | 0 | 100.77 | 2.27 | 90.14 | 42.79 | 106.58 | 12.62 | 103.72 | 110 | 0 | 15694 | 80.24 | 114.95 | 219.39 | 213.42 | 218.85 | 0 | 34.6 | 51.09 | 13404 | 91.11 | 42.01 | 37.23 | 0.88 | 42.01 | 0 | 605 | 433.6 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 314.5 | 0 | 308.2 | 100.73 | 15693 | 15694 | 317
03/26/22 10:33:51.200 | 586.657 | 1369.2954 | 53.8468 | 43.5945 | 10.2523 | 31.4131 | 50.9193 | 0 | 1794.3039 | 89.2546 | 80.1616 | 9.093 | 24.3106 | 69.6888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.995 | 461.13 | 458.01 | 462.07 | 412.76 | 443.26 | 419.1 | 314.99 | 0.53692 | -0.15694 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7067524.9027 | 8155103.8067 | 8155103.8067 | 62.429 | 62.1866 | 1.0018 | 0.998 | 685414.2625 | 895564.9336 | 460.4033 | 0.51983 | 0 | 0 | 31.4131 | 24.3106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017905 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 602.4376 | 1368.1118 | 54.6205 | 44.0815 | 30.9299 | 1787.4282 | 78.27 | 25.1615 | 460.0896 | 0.0069325 | 60.0009 | 0.52682 | 0.67711 | 87.5358 | 2.3234 | 0.83251 | 0.54085 | 4.3453 | 1.7275 | 0.54241 | 0 | 100 | 579.4 | 316 | 106.63 | 103.7 | 100.77 | 307 | 3 | 91.13 | 42.01 | 4 | 37.23 | 42.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.8 | 0 | 38 | 62 | 62 | 100.88 | 88.04 | 83.9 | 0 | 100.77 | 2.27 | 90.17 | 42.79 | 106.63 | 12.58 | 103.7 | 110 | 0 | 15694 | 80.24 | 114.95 | 219.51 | 213.42 | 218.85 | 0 | 34.39 | 50.45 | 13409 | 91.12 | 42.01 | 37.23 | 0.88 | 42.01 | 0 | 606 | 428.6 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.4 | 315.1 | 0 | 308.8 | 100.77 | 15693 | 15694 | 318
03/26/22 10:33:56.201 | 586.0316 | 1367.8555 | 53.8486 | 43.5964 | 10.2522 | 30.9625 | 50.9296 | 0 | 1789.5248 | 89.2608 | 80.1665 | 9.0944 | 24.486 | 69.6442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.002 | 461.15 | 458.02 | 462.07 | 412.81 | 443.26 | 419.12 | 315.01 | 0.53753 | -0.0055665 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7059595.6394 | 8134838.4368 | 8134838.4368 | 62.429 | 62.1866 | 1.0018 | 0.998 | 684693.4117 | 893178.9533 | 460.4134 | 0.51982 | 0 | 0 | 30.9625 | 24.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017913 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 602.1856 | 1368.1107 | 54.6102 | 44.0756 | 30.9351 | 1787.4606 | 78.2996 | 25.1471 | 460.0959 | 0.0069462 | 60.001 | 0.52696 | 0.66632 | 87.5627 | 2.3235 | 0.83048 | 0.54031 | 4.339 | 1.7139 | 0.53944 | 0 | 100 | 578.3 | 317 | 106.65 | 103.7 | 100.7 | 308.9 | 3 | 91.15 | 41.99 | 4 | 37.2 | 42.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.83 | 0 | 37.99 | 62 | 62 | 100.88 | 88.04 | 83.92 | 0 | 100.7 | 2.27 | 90.18 | 42.78 | 106.65 | 12.55 | 103.7 | 110 | 0 | 15694 | 80.24 | 114.93 | 219.51 | 213.53 | 218.85 | 0 | 34.11 | 49.95 | 13414 | 91.15 | 41.99 | 37.2 | 0.9 | 41.99 | 0 | 606 | 433 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 312.6 | 0 | 306.3 | 100.64 | 15693 | 15694 | 316
03/26/22 10:34:01.200 | 585.1888 | 1366.0234 | 53.8524 | 43.6012 | 10.2512 | 31.4477 | 50.9327 | 0 | 1782.5472 | 89.2705 | 80.1735 | 9.097 | 24.3254 | 69.6492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.008 | 461.17 | 458 | 462.07 | 412.9 | 443.24 | 419.07 | 315 | 0.53829 | 0.24001 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7049871.3999 | 8105253.3124 | 8105253.3124 | 62.4289 | 62.1865 | 1.0018 | 0.998 | 683776.1548 | 889695.3634 | 460.4134 | 0.52417 | 0 | 0 | 31.4477 | 24.3254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017912 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 601.9262 | 1368.1032 | 54.5997 | 44.0696 | 30.9368 | 1787.375 | 78.329 | 25.1408 | 460.1023 | 0.0069599 | 60.0012 | 0.5271 | 0.66167 | 87.5894 | 2.3278 | 0.82801 | 0.53955 | 4.2997 | 1.7003 | 0.53639 | 0 | 100 | 578.9 | 317 | 106.73 | 103.72 | 100.68 | 306.8 | 3 | 91.19 | 41.99 | 4 | 37.2 | 42.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.85 | 0 | 37.98 | 62 | 62 | 100.92 | 88.07 | 83.88 | 0 | 100.68 | 2.27 | 90.19 | 42.76 | 106.75 | 12.52 | 103.72 | 110 | 0 | 15694 | 80.24 | 114.88 | 219.51 | 213.53 | 218.97 | 0 | 33.87 | 49.62 | 13419 | 91.2 | 41.99 | 37.2 | 0.88 | 41.99 | 0 | 605 | 432.3 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 313.7 | 0 | 307.5 | 100.64 | 15693 | 15694 | 317
03/26/22 10:34:06.200 | 585.1898 | 1366.0543 | 53.8548 | 43.6039 | 10.251 | 31.7454 | 50.9296 | 0 | 1782.2221 | 89.2744 | 80.1762 | 9.0982 | 23.8625 | 69.6909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 461.1801 | 457.9801 | 462.0601 | 413.0101 | 443.2601 | 419.0501 | 315.0101 | 0.5383 | 0.2547 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7050144.8268 | 8104301.4849 | 8104301.4849 | 62.4289 | 62.1864 | 1.0018 | 0.998 | 683791.5502 | 889532.7125 | 460.4068 | 0.52707 | 0 | 0 | 31.7454 | 23.8625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017918 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 601.6648 | 1368.0965 | 54.589 | 44.0635 | 30.9365 | 1787.3073 | 78.3583 | 25.1385 | 460.1087 | 0.0069737 | 60.0014 | 0.52724 | 0.6561 | 87.616 | 2.3318 | 0.82522 | 0.53861 | 4.2738 | 1.6862 | 0.53315 | 0 | 100 | 579.1 | 317 | 106.73 | 103.75 | 100.71 | 306.7 | 3 | 91.19 | 42 | 4 | 37.21 | 42.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.9 | 0 | 37.99 | 62 | 62 | 100.92 | 88.07 | 83.9 | 0 | 100.71 | 2.27 | 90.22 | 42.78 | 106.73 | 12.56 | 103.75 | 110 | 0 | 15694 | 80.24 | 114.86 | 219.51 | 213.53 | 218.97 | 0 | 33.7 | 49.52 | 13424 | 91.19 | 42 | 37.21 | 0.89 | 42 | 0 | 605 | 432.4 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.5 | 313.5 | 0 | 307.2 | 100.78 | 15695 | 15694 | 315
03/26/22 10:34:11.200 | 584.9202 | 1365.4298 | 53.8572 | 43.6062 | 10.2509 | 31.9982 | 50.9088 | 0 | 1781.9434 | 89.2778 | 80.1789 | 9.0988 | 23.8179 | 69.7231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 461.1801 | 457.9801 | 462.0601 | 413.0101 | 443.2601 | 419.0501 | 315.0101 | 0.53855 | 0.22724 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7047118.7846 | 8103541.7658 | 8103541.7658 | 62.4289 | 62.1864 | 1.0018 | 0.998 | 683478.8532 | 889393.2358 | 460.4068 | 0.52707 | 0 | 0 | 31.9982 | 23.8179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017922 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 601.395 | 1368.076 | 54.5783 | 44.0574 | 30.9412 | 1787.2559 | 78.3875 | 25.1323 | 460.1151 | 0.0069876 | 60.0015 | 0.5274 | 0.64902 | 87.6424 | 2.339 | 0.82209 | 0.53748 | 4.2824 | 1.6718 | 0.5297 | 0 | 100 | 579.2 | 317 | 106.8 | 103.75 | 100.73 | 306.3 | 3 | 91.23 | 42.01 | 4 | 37.23 | 42.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.95 | 0 | 38 | 62 | 62 | 101.03 | 88.13 | 83.9 | 0 | 100.73 | 2.27 | 90.25 | 42.79 | 106.8 | 12.52 | 103.75 | 110 | 0 | 15694 | 80.24 | 114.83 | 219.51 | 213.53 | 218.97 | 0 | 33.58 | 49.5 | 13429 | 91.23 | 42.01 | 37.23 | 0.88 | 42.01 | 0 | 605 | 431.2 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 313.6 | 0 | 307.4 | 100.73 | 15693 | 15694 | 317
03/26/22 10:34:16.200 | 586.0442 | 1368.0826 | 53.8619 | 43.6112 | 10.2507 | 31.1883 | 50.9206 | 0 | 1785.0142 | 89.2849 | 80.1866 | 9.0982 | 24.6919 | 69.6938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 461.2201 | 458.0001 | 462.0501 | 413.1201 | 443.1201 | 419.1001 | 315.0001 | 0.5375 | 0.20696 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7059949.2488 | 8117955.2052 | 8117955.2052 | 62.4289 | 62.1863 | 1.0018 | 0.998 | 684806.5074 | 890924.8862 | 460.4234 | 0.52633 | 0 | 0 | 31.1883 | 24.6919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017918 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 601.1347 | 1368.0887 | 54.5674 | 44.0511 | 30.947 | 1787.2319 | 78.4166 | 25.1225 | 460.1217 | 0.0070017 | 60.0016 | 0.52755 | 0.64224 | 87.6687 | 2.3331 | 0.81853 | 0.53608 | 4.289 | 1.6571 | 0.5261 | 0 | 100 | 579 | 316 | 106.78 | 103.77 | 100.7 | 306.1 | 3 | 91.21 | 42.01 | 4 | 37.23 | 42.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.98 | 0 | 38 | 62 | 62 | 101 | 88.11 | 83.9 | 0 | 100.7 | 2.27 | 90.26 | 42.79 | 106.75 | 12.57 | 103.77 | 110 | 0 | 15694 | 80.24 | 114.83 | 219.51 | 213.53 | 218.97 | 0 | 33.58 | 49.65 | 13434 | 91.2 | 42.01 | 37.23 | 0.88 | 42.01 | 0 | 605 | 430.4 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.4 | 313.7 | 0 | 307.5 | 100.77 | 15693 | 15694 | 317
03/26/22 10:34:21.200 | 586.9645 | 1370.2347 | 53.8645 | 43.6138 | 10.2507 | 30.9076 | 50.8795 | 0 | 1781.4015 | 89.2888 | 80.1919 | 9.097 | 25.0284 | 69.7268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 461.2201 | 458.0001 | 462.0501 | 413.1201 | 443.1201 | 419.1001 | 315.0001 | 0.53666 | 0.55181 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7070789.1193 | 8100788.9958 | 8100788.9958 | 62.4289 | 62.1863 | 1.0018 | 0.998 | 685883.6522 | 889121.018 | 460.4234 | 0.52633 | 0 | 0 | 30.9076 | 25.0284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.01793 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 600.8776 | 1368.0952 | 54.5565 | 44.0448 | 30.947 | 1787.2023 | 78.4457 | 25.1203 | 460.1283 | 0.0070161 | 60.0017 | 0.52769 | 0.63635 | 87.695 | 2.3375 | 0.81461 | 0.53447 | 4.3108 | 1.642 | 0.52224 | 0 | 100 | 578.9 | 317 | 106.8 | 103.8 | 100.7 | 307.3 | 3 | 91.23 | 42.01 | 4 | 37.24 | 42.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.03 | 0 | 38.01 | 62 | 62 | 101.1 | 88.17 | 83.96 | 0 | 100.7 | 2.27 | 90.29 | 42.8 | 106.8 | 12.56 | 103.8 | 110 | 0 | 15694 | 80.24 | 114.83 | 219.51 | 213.53 | 218.97 | 0 | 33.53 | 49.69 | 13439 | 91.24 | 42.03 | 37.24 | 0.88 | 42.03 | 0 | 605 | 429.9 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 313.5 | 0 | 307.3 | 100.68 | 15692 | 15694 | 317
03/26/22 10:34:26.200 | 588.3928 | 1373.4965 | 53.8683 | 43.617 | 10.2513 | 31.024 | 50.8958 | 0 | 1785.2825 | 89.295 | 80.2004 | 9.0946 | 25.088 | 69.6739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.004 | 461.23 | 457.99 | 462.02 | 413.21 | 443.09 | 419.12 | 315.01 | 0.53537 | 0.57199 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7088096.3036 | 8116396.358 | 8116396.358 | 62.4289 | 62.1862 | 1.0018 | 0.998 | 687516.1865 | 891056.9456 | 460.4134 | 0.52634 | 0 | 0 | 31.024 | 25.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017924 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 600.617 | 1368.1063 | 54.5453 | 44.0383 | 30.951 | 1787.1944 | 78.4746 | 25.113 | 460.1351 | 0.0070308 | 60.0018 | 0.52784 | 0.6292 | 87.721 | 2.3611 | 0.81023 | 0.53256 | 4.3165 | 1.6265 | 0.51794 | 0 | 100 | 579.5 | 316 | 106.88 | 103.8 | 100.78 | 308.1 | 3 | 91.27 | 42.04 | 4 | 37.25 | 42.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.08 | 0 | 38.02 | 62 | 62 | 101.13 | 88.18 | 83.94 | 0 | 100.78 | 2.27 | 90.31 | 42.81 | 106.88 | 12.53 | 103.8 | 110 | 0 | 15694 | 80.24 | 114.83 | 219.51 | 213.53 | 218.97 | 0 | 33.51 | 49.81 | 13444 | 91.27 | 42.04 | 37.25 | 0.87 | 42.04 | 0 | 605 | 434.1 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.8 | 316.3 | 0 | 310 | 100.83 | 15693 | 15694 | 318
03/26/22 10:34:31.200 | 586.7479 | 1369.6412 | 53.8712 | 43.6198 | 10.2514 | 31.1795 | 50.9174 | 0 | 1787.9817 | 89.302 | 80.2105 | 9.0915 | 25.0054 | 69.6958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0061 | 461.2201 | 457.9701 | 461.9901 | 413.3601 | 443.1301 | 419.2801 | 315.0701 | 0.53698 | 0.2154 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7068417.3331 | 8125754.3962 | 8125754.3962 | 62.4289 | 62.1861 | 1.0018 | 0.998 | 685586.2679 | 892402.7946 | 460.3934 | 0.52636 | 0 | 0 | 31.1795 | 25.0054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.01792 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 600.3543 | 1368.1123 | 54.5341 | 44.0318 | 30.9561 | 1787.1885 | 78.5035 | 25.1063 | 460.1419 | 0.0070454 | 60.0019 | 0.52799 | 0.62207 | 87.747 | 2.371 | 0.80547 | 0.53039 | 4.316 | 1.6107 | 0.51351 | 0 | 100 | 579.4 | 315 | 106.85 | 103.8 | 100.77 | 310.2 | 3 | 91.27 | 42.04 | 4 | 37.25 | 42.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.03 | 0 | 38.04 | 62 | 62 | 101.1 | 88.17 | 84.05 | 0 | 100.77 | 2.27 | 90.29 | 42.83 | 106.85 | 12.54 | 103.8 | 110 | 0 | 15694 | 80.26 | 114.83 | 219.51 | 213.53 | 218.97 | 0 | 33.49 | 49.83 | 13449 | 91.25 | 42.05 | 37.26 | 0.86 | 42.05 | 0 | 605 | 434.5 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 312.2 | 0 | 305.9 | 100.82 | 15694 | 15694 | 316
03/26/22 10:34:36.200 | 585.4817 | 1366.7613 | 53.8734 | 43.6226 | 10.2508 | 31.2778 | 50.9253 | 0 | 1787.7959 | 89.3103 | 80.2218 | 9.0885 | 24.5627 | 69.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 461.22 | 457.97 | 461.99 | 413.36 | 443.13 | 419.28 | 315.07 | 0.53814 | 0.080314 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7053251.8503 | 8121789.5888 | 8121789.5888 | 62.4289 | 62.186 | 1.0018 | 0.998 | 684144.6365 | 892308.5273 | 460.3934 | 0.52636 | 0 | 0 | 31.2778 | 24.5627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017919 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 600.0871 | 1368.1071 | 54.5227 | 44.025 | 30.9614 | 1787.191 | 78.5322 | 25.0977 | 460.1488 | 0.0070603 | 60.002 | 0.52814 | 0.61407 | 87.7728 | 2.3729 | 0.80011 | 0.52777 | 4.3163 | 1.5948 | 0.50839 | 0 | 100 | 579.2 | 316 | 106.8 | 103.8 | 100.73 | 307.6 | 3 | 91.23 | 42.04 | 4 | 37.25 | 42.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.03 | 0 | 38.02 | 62 | 62 | 101.1 | 88.17 | 84 | 0 | 100.73 | 2.27 | 90.29 | 42.81 | 106.83 | 12.56 | 103.8 | 110 | 0 | 15694 | 80.26 | 114.86 | 219.51 | 213.53 | 218.97 | 0 | 33.39 | 49.7 | 13454 | 91.24 | 42.05 | 37.26 | 0.84 | 42.05 | 0 | 606 | 430.5 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 315.4 | 0 | 309.1 | 100.82 | 15693 | 15694 | 316
03/26/22 10:34:41.200 | 586.7079 | 1369.7083 | 53.8765 | 43.6263 | 10.2502 | 30.2875 | 50.9272 | 0 | 1789.3184 | 89.3233 | 80.2372 | 9.0861 | 26.1521 | 69.6586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.004 | 461.22 | 457.98 | 461.97 | 413.59 | 443.2 | 419.47 | 315.2 | 0.53724 | 0.174 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7067153.0559 | 8128299.6036 | 8128299.6036 | 62.4289 | 62.1859 | 1.0018 | 0.998 | 685619.6275 | 893066.3324 | 460.39 | 0.52347 | 0 | 0 | 30.2875 | 26.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017914 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 599.8202 | 1368.1022 | 54.5111 | 44.0181 | 30.9606 | 1787.19 | 78.5609 | 25.0969 | 460.1558 | 0.0070753 | 60.0021 | 0.5283 | 0.6063 | 87.7985 | 2.3693 | 0.79438 | 0.52488 | 4.3163 | 1.5785 | 0.50305 | 0 | 100 | 579.7 | 317 | 106.9 | 103.8 | 100.82 | 308.5 | 3 | 91.27 | 42.05 | 4 | 37.26 | 42.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.08 | 0 | 38.04 | 62 | 62 | 101.13 | 88.18 | 84.05 | 0 | 100.82 | 2.27 | 90.31 | 42.83 | 106.9 | 12.52 | 103.8 | 110 | 0 | 15694 | 80.26 | 114.86 | 219.51 | 213.53 | 218.97 | 0 | 33.28 | 49.68 | 13459 | 91.28 | 42.05 | 37.26 | 0.82 | 42.05 | 0 | 605 | 432 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 313.4 | 0 | 307.1 | 100.89 | 15695 | 15694 | 315
03/26/22 10:34:46.199 | 586.8095 | 1369.3212 | 53.8797 | 43.629 | 10.2507 | 30.8065 | 50.9123 | 0 | 1792.5905 | 89.3335 | 80.2484 | 9.0851 | 25.5411 | 69.7074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0021 | 461.2201 | 457.9801 | 461.9801 | 413.6101 | 443.2001 | 419.5401 | 315.2201 | 0.53718 | 0.053791 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7068769.3078 | 8139896.1928 | 8139896.1928 | 62.4289 | 62.1858 | 1.0018 | 0.998 | 685717.6788 | 894499.8628 | 460.3934 | 0.52419 | 0 | 0 | 30.8065 | 25.5411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017905 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 599.552 | 1368.0965 | 54.4995 | 44.0111 | 30.9589 | 1787.2197 | 78.5894 | 25.1014 | 460.1628 | 0.0070904 | 60.0021 | 0.52847 | 0.59677 | 87.8242 | 2.3638 | 0.78823 | 0.52161 | 4.3271 | 1.5621 | 0.49743 | 0 | 100 | 580.1 | 318 | 106.88 | 103.8 | 100.89 | 309.1 | 3 | 91.27 | 42.06 | 4 | 37.28 | 42.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105 | 0 | 38.05 | 62 | 62 | 101.08 | 88.15 | 84.09 | 0 | 100.89 | 2.27 | 90.27 | 42.84 | 106.88 | 12.53 | 103.8 | 110 | 0 | 15694 | 80.26 | 114.86 | 219.51 | 213.53 | 218.97 | 0 | 33.23 | 49.72 | 13464 | 91.27 | 42.06 | 37.28 | 0.83 | 42.06 | 0 | 605 | 430.4 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.8 | 314.6 | 0 | 308.3 | 100.83 | 15695 | 15694 | 316
03/26/22 10:34:51.199 | 586.1268 | 1367.489 | 53.8831 | 43.6314 | 10.2518 | 30.4446 | 50.9212 | 0 | 1793.9014 | 89.3429 | 80.2577 | 9.0851 | 25.7877 | 69.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.002 | 461.22 | 457.98 | 461.98 | 413.61 | 443.2 | 419.54 | 315.22 | 0.5378 | -0.13543 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7060358.2871 | 8146959.1475 | 8146959.1475 | 62.4289 | 62.1857 | 1.0018 | 0.998 | 684854.6711 | 895271.3483 | 460.3934 | 0.52419 | 0 | 0 | 30.4446 | 25.7877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017899 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 599.2988 | 1368.093 | 54.4879 | 44.004 | 30.9598 | 1787.258 | 78.6178 | 25.1007 | 460.1698 | 0.0071056 | 60.0022 | 0.52862 | 0.58771 | 87.8497 | 2.3642 | 0.78175 | 0.51789 | 4.3556 | 1.5457 | 0.49161 | 0 | 100 | 579.7 | 316 | 106.83 | 103.8 | 100.82 | 307.7 | 3 | 91.24 | 42.06 | 4 | 37.28 | 42.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105 | 0 | 38.05 | 62 | 62 | 101.05 | 88.14 | 84.03 | 0 | 100.82 | 2.27 | 90.27 | 42.84 | 106.8 | 12.57 | 103.8 | 110 | 0 | 15694 | 80.29 | 114.88 | 219.63 | 213.63 | 218.97 | 0 | 33.25 | 49.96 | 13468 | 91.24 | 42.06 | 37.28 | 0.87 | 42.06 | 0 | 605 | 430.8 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 313.1 | 0 | 306.9 | 100.82 | 15694 | 15694 | 316
03/26/22 10:34:56.199 | 585.7526 | 1366.9265 | 53.8912 | 43.6368 | 10.2544 | 30.455 | 50.9156 | 0 | 1796.2187 | 89.362 | 80.2755 | 9.0866 | 25.5506 | 69.6962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.003 | 461.22 | 457.99 | 461.96 | 413.69 | 443.25 | 419.62 | 315.28 | 0.53825 | -0.34103 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7055782.4259 | 8159340.8051 | 8159340.8051 | 62.4288 | 62.1855 | 1.0018 | 0.998 | 684226.5224 | 896505.0976 | 460.39 | 0.5213 | 0 | 0 | 30.455 | 25.5506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017893 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 599.0495 | 1368.0877 | 54.4763 | 43.9967 | 30.9565 | 1787.3156 | 78.646 | 25.1025 | 460.1768 | 0.0071207 | 60.0022 | 0.52877 | 0.5772 | 87.8751 | 2.3657 | 0.77498 | 0.51383 | 4.4052 | 1.5291 | 0.48566 | 0 | 100 | 580.1 | 317 | 106.83 | 103.8 | 100.83 | 308.7 | 3 | 91.24 | 42.05 | 4 | 37.26 | 42.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.98 | 0 | 38.04 | 62 | 62 | 101.05 | 88.15 | 84 | 0 | 100.83 | 2.27 | 90.26 | 42.83 | 106.83 | 12.56 | 103.8 | 110 | 0 | 15694 | 80.29 | 114.93 | 219.63 | 213.63 | 219.08 | 0 | 33.69 | 50.84 | 13473 | 91.24 | 42.05 | 37.26 | 0.88 | 42.05 | 0 | 605 | 431.1 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 315 | 0 | 308.7 | 100.89 | 15693 | 15694 | 317
03/26/22 10:35:01.199 | 586.0395 | 1367.4065 | 53.8961 | 43.6402 | 10.2558 | 31.1419 | 50.9125 | 0 | 1794.8407 | 89.371 | 80.2831 | 9.0879 | 24.4402 | 69.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0031 | 461.2201 | 457.9901 | 461.9601 | 413.6901 | 443.2501 | 419.6201 | 315.2801 | 0.53798 | -0.2131 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7059838.7479 | 8152973.6016 | 8152973.6016 | 62.4288 | 62.1854 | 1.0018 | 0.998 | 684466.5668 | 895816.296 | 460.3901 | 0.5213 | 0 | 0 | 31.1419 | 24.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017905 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 598.8188 | 1368.1023 | 54.4648 | 43.9894 | 30.9605 | 1787.3736 | 78.6739 | 25.09 | 460.1838 | 0.0070923 | 60.0022 | 0.52891 | 0.56839 | 87.9004 | 2.3533 | 0.76804 | 0.50941 | 4.4353 | 1.5127 | 0.47953 | 0 | 100 | 580.1 | 316 | 106.75 | 103.77 | 100.89 | 307.6 | 3 | 91.2 | 42.06 | 4 | 37.28 | 42.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 104.98 | 0 | 38.05 | 62 | 62 | 101 | 88.11 | 84.03 | 0 | 100.89 | 2.27 | 90.26 | 42.84 | 106.75 | 12.57 | 103.77 | 110 | 0 | 15694 | 80.29 | 114.95 | 219.63 | 213.63 | 219.08 | 0 | 34.21 | 51.32 | 13479 | 91.2 | 42.06 | 37.28 | 0.85 | 42.06 | 0 | 605 | 432.6 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 313.2 | 0 | 306.9 | 100.87 | 15693 | 15694 | 317
03/26/22 10:35:06.199 | 585.9012 | 1366.8594 | 53.9017 | 43.6442 | 10.2575 | 31.2482 | 50.921 | 0 | 1790.2061 | 89.3795 | 80.2897 | 9.0899 | 24.2586 | 69.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 461.2 | 458 | 461.95 | 413.78 | 443.36 | 419.84 | 315.38 | 0.53828 | 0.0069553 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7058260.8287 | 8133474.7976 | 8133474.7976 | 62.4288 | 62.1853 | 1.0018 | 0.998 | 684192.4828 | 893502.2567 | 460.3833 | 0.51768 | 0 | 0 | 31.2482 | 24.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017906 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 598.5905 | 1368.1091 | 54.4534 | 43.982 | 30.9611 | 1787.404 | 78.7016 | 25.0831 | 460.1906 | 0.007107 | 60.0022 | 0.52905 | 0.56075 | 87.9255 | 2.3479 | 0.76094 | 0.50471 | 4.4358 | 1.4962 | 0.47353 | 0 | 100 | 580 | 316 | 106.9 | 103.75 | 100.87 | 307.9 | 3 | 91.28 | 42.06 | 4 | 37.28 | 42.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.05 | 0 | 38.05 | 62 | 62 | 101.1 | 88.17 | 84.05 | 0 | 100.87 | 2.27 | 90.3 | 42.84 | 106.93 | 12.46 | 103.75 | 110 | 0 | 15694 | 80.31 | 114.98 | 219.63 | 213.63 | 219.08 | 0 | 34.19 | 50.83 | 13484 | 91.29 | 42.06 | 37.28 | 0.83 | 42.06 | 0 | 605 | 431.7 | 458.4 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 312.6 | 0 | 306.3 | 100.82 | 15694 | 15694 | 316
03/26/22 10:35:11.199 | 586.339 | 1367.4942 | 53.912 | 43.6515 | 10.2605 | 31.5002 | 50.9216 | 0 | 1785.4012 | 89.3917 | 80.2982 | 9.0936 | 24.3174 | 69.7334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9881 | 461.1301 | 457.9401 | 461.9001 | 413.7801 | 443.5701 | 420.0201 | 315.3901 | 0.5379 | 0.30623 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7063749.2799 | 8114981.6662 | 8114981.6662 | 62.4288 | 62.1852 | 1.0018 | 0.998 | 684509.7775 | 891102.9678 | 460.3234 | 0.51775 | 0 | 0 | 31.5002 | 24.3174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017906 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 598.3641 | 1368.1022 | 54.4421 | 43.9747 | 30.9609 | 1787.4049 | 78.729 | 25.0813 | 460.1974 | 0.0070781 | 60.0022 | 0.52919 | 0.55379 | 87.9505 | 2.3475 | 0.75374 | 0.49975 | 4.4354 | 1.4798 | 0.46729 | 0 | 100 | 579.5 | 316 | 106.93 | 103.77 | 100.78 | 307.6 | 3 | 91.29 | 42.08 | 4 | 37.29 | 42.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.05 | 0 | 38.05 | 62 | 62 | 101.13 | 88.18 | 84.05 | 0 | 100.78 | 2.27 | 90.3 | 42.84 | 106.95 | 12.47 | 103.77 | 110 | 0 | 15694 | 80.31 | 114.98 | 219.63 | 213.63 | 219.08 | 0 | 33.91 | 50.24 | 13489 | 91.31 | 42.08 | 37.29 | 0.84 | 42.08 | 0 | 605 | 431.8 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.2 | 312.8 | 0 | 306.5 | 100.9 | 15693 | 15694 | 317
03/26/22 10:35:16.199 | 586.8934 | 1368.7019 | 53.9154 | 43.6543 | 10.2611 | 31.6268 | 50.9098 | 0 | 1784.7458 | 89.3952 | 80.3 | 9.0952 | 24.2683 | 69.7297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9881 | 461.1301 | 457.9401 | 461.9001 | 413.7801 | 443.5701 | 420.0201 | 315.3901 | 0.53739 | 0.40933 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7070537.679 | 8113413.7869 | 8113413.7869 | 62.4288 | 62.1852 | 1.0018 | 0.998 | 685114.1367 | 890775.5829 | 460.3234 | 0.51775 | 0 | 0 | 31.6268 | 24.2683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017903 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 598.1432 | 1368.095 | 54.4309 | 43.9673 | 30.9642 | 1787.4028 | 78.7562 | 25.0759 | 460.2038 | 0.0070703 | 60.0022 | 0.52932 | 0.54691 | 87.9753 | 2.3436 | 0.74645 | 0.49459 | 4.4366 | 1.4634 | 0.46094 | 0 | 100 | 580 | 315 | 106.9 | 103.82 | 100.87 | 307 | 3 | 91.28 | 42.06 | 4 | 37.28 | 42.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.08 | 0 | 38.05 | 61 | 61 | 101.18 | 88.21 | 84.05 | 0 | 100.87 | 2.27 | 90.31 | 42.84 | 106.88 | 12.56 | 103.82 | 110 | 0 | 15694 | 80.33 | 114.98 | 219.63 | 213.63 | 219.08 | 0 | 33.66 | 49.86 | 13494 | 91.27 | 42.05 | 37.26 | 0.9 | 42.05 | 0 | 605 | 430.6 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 313.8 | 0 | 307.5 | 100.82 | 15694 | 15694 | 316
03/26/22 10:35:21.199 | 587.0738 | 1369.0064 | 53.9217 | 43.6597 | 10.262 | 31.0299 | 50.9173 | 0 | 1787.1663 | 89.4011 | 80.3024 | 9.0986 | 24.9593 | 69.6826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9871 | 461.0901 | 457.9101 | 461.8601 | 413.8001 | 443.6501 | 420.1301 | 315.4001 | 0.53724 | 0.24661 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7072183.846 | 8128268.8038 | 8128268.8038 | 62.4288 | 62.1851 | 1.0018 | 0.998 | 685266.287 | 891983.3348 | 460.2868 | 0.51634 | 0 | 0 | 31.0299 | 24.9593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.0179 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 597.9351 | 1368.0897 | 54.4199 | 43.96 | 30.9675 | 1787.4104 | 78.7828 | 25.0669 | 460.21 | 0.0070835 | 60.0022 | 0.52945 | 0.53946 | 87.9997 | 2.3405 | 0.73931 | 0.48928 | 4.435 | 1.4475 | 0.45455 | 0 | 100 | 580 | 317 | 106.93 | 103.82 | 100.87 | 308.6 | 3 | 91.29 | 42.06 | 4 | 37.28 | 42.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.13 | 0 | 38.05 | 61 | 61 | 101.27 | 88.26 | 84.05 | 0 | 100.87 | 2.27 | 90.34 | 42.84 | 106.95 | 12.52 | 103.82 | 110 | 0 | 15694 | 80.33 | 114.98 | 219.63 | 213.63 | 219.08 | 0 | 33.5 | 49.71 | 13499 | 91.31 | 42.06 | 37.28 | 0.91 | 42.06 | 0 | 605 | 428.6 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 314.7 | 0 | 308.5 | 100.82 | 15694 | 15694 | 318
03/26/22 10:35:26.199 | 586.8585 | 1368.2632 | 53.9313 | 43.6674 | 10.2638 | 31.0976 | 50.927 | 0 | 1789.4939 | 89.4078 | 80.3053 | 9.1024 | 24.6789 | 69.7061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9871 | 461.0501 | 457.8701 | 461.8101 | 413.8001 | 443.7301 | 420.2101 | 315.4001 | 0.53744 | 0.048089 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7069644.4337 | 8141917.2415 | 8141917.2415 | 62.4287 | 62.1851 | 1.0018 | 0.998 | 684893.8553 | 893144.6677 | 460.2434 | 0.51567 | 0 | 0 | 31.0976 | 24.6789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017895 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 597.7328 | 1368.0864 | 54.4091 | 43.9527 | 30.9685 | 1787.4227 | 78.8092 | 25.0632 | 460.2158 | 0.0070962 | 60.0022 | 0.52957 | 0.53163 | 88.024 | 2.3384 | 0.73212 | 0.48382 | 4.4367 | 1.4316 | 0.44804 | 0 | 100 | 580.1 | 316 | 106.9 | 103.82 | 100.89 | 307.1 | 3 | 91.28 | 42.06 | 4 | 37.28 | 42.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.05 | 0 | 38.05 | 61 | 61 | 101.2 | 88.22 | 84.05 | 0 | 100.89 | 2.27 | 90.3 | 42.84 | 106.9 | 12.54 | 103.82 | 110 | 0 | 15694 | 80.33 | 114.95 | 219.63 | 213.63 | 219.08 | 0 | 33.37 | 49.63 | 13503 | 91.28 | 42.06 | 37.28 | 0.89 | 42.06 | 0 | 605 | 431.5 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 313.4 | 0 | 307.1 | 100.89 | 15693 | 15694 | 316
03/26/22 10:35:31.199 | 585.6777 | 1365.373 | 53.9349 | 43.6701 | 10.2649 | 31.0596 | 50.9195 | 0 | 1789.5352 | 89.41 | 80.3059 | 9.1041 | 24.7068 | 69.7003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9871 | 461.0501 | 457.8701 | 461.8101 | 413.8001 | 443.7301 | 420.2101 | 315.4001 | 0.53852 | -0.14797 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7055384.1679 | 8143614.5906 | 8143614.5906 | 62.4287 | 62.1851 | 1.0018 | 0.998 | 683446.9972 | 893165.1897 | 460.2434 | 0.51567 | 0 | 0 | 31.0596 | 24.7068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017899 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 597.5273 | 1368.0627 | 54.3985 | 43.9455 | 30.9666 | 1787.4423 | 78.8352 | 25.064 | 460.2217 | 0.0070219 | 60.0022 | 0.5297 | 0.52195 | 88.048 | 2.3442 | 0.72495 | 0.47828 | 4.4382 | 1.4157 | 0.44135 | 0 | 100 | 579.9 | 318 | 106.9 | 103.82 | 100.85 | 307.5 | 3 | 91.28 | 42.06 | 4 | 37.28 | 42.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.08 | 0 | 38.05 | 61 | 61 | 101.2 | 88.22 | 84.05 | 0 | 100.85 | 2.27 | 90.31 | 42.84 | 106.9 | 12.54 | 103.82 | 110 | 0 | 15694 | 80.33 | 114.95 | 219.63 | 213.74 | 219.08 | 0 | 33.27 | 49.65 | 13509 | 91.28 | 42.06 | 37.28 | 0.89 | 42.06 | 0 | 605 | 433.4 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 314.3 | 0 | 308.1 | 100.82 | 15695 | 15694 | 315
03/26/22 10:35:36.199 | 584.6562 | 1362.7874 | 53.9399 | 43.6735 | 10.2664 | 31.3798 | 50.9156 | 0 | 1785.2877 | 89.413 | 80.3064 | 9.1066 | 24.1499 | 69.7094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 460.98 | 457.82 | 461.73 | 413.83 | 443.82 | 420.38 | 315.4 | 0.53946 | -0.077895 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7043355.3774 | 8125871.7317 | 8125871.7317 | 62.4287 | 62.1851 | 1.0018 | 0.998 | 682152.5022 | 891045.174 | 460.1767 | 0.51212 | 0 | 0 | 31.3798 | 24.1499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.01791 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 597.3333 | 1368.0522 | 54.3881 | 43.9384 | 30.972 | 1787.4389 | 78.8608 | 25.0524 | 460.227 | 0.0070117 | 60.0022 | 0.52981 | 0.51464 | 88.0717 | 2.3637 | 0.71791 | 0.47278 | 4.4396 | 1.4002 | 0.43485 | 0 | 100 | 579.7 | 316 | 106.93 | 103.82 | 100.82 | 309 | 3 | 91.31 | 42.08 | 4 | 37.29 | 42.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.1 | 0 | 38.05 | 61 | 61 | 101.25 | 88.25 | 84 | 0 | 100.82 | 2.27 | 90.33 | 42.84 | 106.93 | 12.53 | 103.82 | 110 | 0 | 15694 | 80.35 | 114.95 | 219.75 | 213.74 | 219.08 | 0 | 33.31 | 49.93 | 13514 | 91.29 | 42.08 | 37.29 | 0.89 | 42.08 | 0 | 605 | 432.3 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 314.7 | 0 | 308.5 | 100.82 | 15694 | 15694 | 316
03/26/22 10:35:41.199 | 586.0337 | 1365.7137 | 53.9465 | 43.6779 | 10.2686 | 31.4552 | 50.9319 | 0 | 1780.8854 | 89.4165 | 80.3078 | 9.1087 | 24.6976 | 69.7338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.994 | 460.94 | 457.78 | 461.69 | 413.82 | 443.92 | 420.4 | 315.38 | 0.53816 | 0.3423 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7060010.3547 | 8108328.6517 | 8108328.6517 | 62.4287 | 62.185 | 1.0018 | 0.998 | 683616.9814 | 888847.7638 | 460.1367 | 0.51217 | 0 | 0 | 31.4552 | 24.6976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017912 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 597.1448 | 1368.0508 | 54.3778 | 43.9315 | 30.977 | 1787.4018 | 78.8861 | 25.0449 | 460.2323 | 0.0069795 | 60.0023 | 0.52993 | 0.50977 | 88.095 | 2.365 | 0.71091 | 0.46734 | 4.4697 | 1.3849 | 0.4282 | 0 | 100 | 580 | 315 | 106.95 | 103.85 | 100.85 | 305.2 | 3 | 91.31 | 42.08 | 4 | 37.29 | 42.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.13 | 0 | 38.05 | 61 | 61 | 101.27 | 88.28 | 83.9 | 0 | 100.85 | 2.27 | 90.34 | 42.84 | 106.95 | 12.54 | 103.85 | 110 | 0 | 15694 | 80.35 | 114.95 | 219.75 | 213.74 | 219.08 | 0 | 33.49 | 50.19 | 13519 | 91.31 | 42.08 | 37.29 | 0.89 | 42.08 | 0 | 605 | 432.1 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 311.4 | 0 | 305.2 | 100.87 | 15693 | 15694 | 315
03/26/22 10:35:46.199 | 586.6442 | 1366.9678 | 53.95 | 43.6802 | 10.2698 | 31.2323 | 50.9305 | 0 | 1784.5239 | 89.4193 | 80.3093 | 9.11 | 24.6729 | 69.7429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9941 | 460.9401 | 457.7801 | 461.6901 | 413.8201 | 443.9201 | 420.4001 | 315.3801 | 0.5376 | 0.21297 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7067165.0625 | 8125962.0837 | 8125962.0837 | 62.4287 | 62.185 | 1.0018 | 0.998 | 684244.5986 | 890663.5592 | 460.1367 | 0.51217 | 0 | 0 | 31.2323 | 24.6729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.01791 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 596.9547 | 1368.0474 | 54.3677 | 43.9247 | 30.981 | 1787.3761 | 78.9111 | 25.0399 | 460.2373 | 0.0068384 | 60.0023 | 0.53004 | 0.50404 | 88.1181 | 2.3675 | 0.70383 | 0.46191 | 4.4933 | 1.3695 | 0.42154 | 0 | 100 | 579.9 | 318 | 106.98 | 103.87 | 100.85 | 309 | 3 | 91.31 | 42.08 | 4 | 37.29 | 42.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.18 | 0 | 38.05 | 61 | 61 | 101.33 | 88.29 | 83.85 | 0 | 100.85 | 2.27 | 90.37 | 42.84 | 106.98 | 12.56 | 103.87 | 110 | 0 | 15694 | 80.35 | 114.98 | 219.75 | 213.74 | 219.08 | 0 | 33.62 | 50.5 | 13524 | 91.31 | 42.08 | 37.29 | 0.89 | 42.08 | 0 | 605 | 430.7 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 313.4 | 0 | 307.1 | 100.82 | 15695 | 15694 | 315
03/26/22 10:35:51.199 | 586.8278 | 1367.3033 | 53.9519 | 43.6814 | 10.2705 | 31.3247 | 50.9278 | 0 | 1787.0682 | 89.4214 | 80.3107 | 9.1107 | 24.5875 | 69.7396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9951 | 460.9401 | 457.7601 | 461.6701 | 413.8801 | 443.8801 | 420.3301 | 315.3701 | 0.53742 | 0.090883 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7069457.243 | 8138144.6009 | 8138144.6009 | 62.4287 | 62.185 | 1.0018 | 0.998 | 684412.437 | 891933.2839 | 460.1234 | 0.51363 | 0 | 0 | 31.3247 | 24.5875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017902 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 596.7619 | 1368.0388 | 54.3576 | 43.9179 | 30.984 | 1787.3926 | 78.9358 | 25.0335 | 460.242 | 0.0066962 | 60.0023 | 0.53015 | 0.4957 | 88.1408 | 2.3674 | 0.69671 | 0.45655 | 4.4866 | 1.3542 | 0.41561 | 0 | 100 | 579.7 | 315 | 106.93 | 103.87 | 100.77 | 306.7 | 3 | 91.31 | 42.09 | 4 | 37.3 | 42.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.18 | 0 | 38.05 | 61 | 61 | 101.27 | 88.28 | 83.88 | 0 | 100.78 | 2.27 | 90.37 | 42.84 | 106.95 | 12.56 | 103.87 | 110 | 0 | 15694 | 80.37 | 114.98 | 219.75 | 213.74 | 219.08 | 0 | 33.77 | 50.54 | 13529 | 91.31 | 42.09 | 37.3 | 0.86 | 42.09 | 0 | 605 | 431.5 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.4 | 314 | 0 | 307.7 | 100.77 | 15693 | 15694 | 315
03/26/22 10:35:56.199 | 586.4944 | 1366.364 | 53.9553 | 43.6835 | 10.2718 | 30.8708 | 50.9224 | 0 | 1789.1275 | 89.4276 | 80.3154 | 9.1121 | 25.017 | 69.7383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.994 | 460.96 | 457.76 | 461.66 | 413.93 | 443.79 | 420.24 | 315.36 | 0.5377 | -0.10008 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7065038.1753 | 8149242.7551 | 8149242.7551 | 62.4287 | 62.1849 | 1.0018 | 0.998 | 683942.106 | 892960.4014 | 460.1267 | 0.51435 | 0 | 0 | 30.8708 | 25.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017905 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 596.5725 | 1368.0425 | 54.3476 | 43.9113 | 30.9839 | 1787.4156 | 78.9603 | 25.0323 | 460.2463 | 0.0067056 | 60.0023 | 0.53026 | 0.48764 | 88.1633 | 2.3635 | 0.68949 | 0.45126 | 4.4881 | 1.339 | 0.41018 | 0 | 100 | 579.4 | 316 | 106.98 | 103.87 | 100.77 | 307 | 3 | 91.32 | 42.09 | 4 | 37.3 | 42.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.15 | 0 | 38.05 | 61 | 61 | 101.27 | 88.26 | 83.79 | 0 | 100.77 | 2.27 | 90.35 | 42.84 | 107 | 12.54 | 103.87 | 110 | 0 | 15694 | 80.37 | 114.98 | 219.75 | 213.74 | 219.2 | 0 | 33.66 | 50.24 | 13533 | 91.33 | 42.09 | 37.3 | 0.88 | 42.09 | 0 | 605 | 430.6 | 458.5 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.4 | 314.5 | 0 | 308.3 | 100.77 | 15693 | 15694 | 317
03/26/22 10:36:01.199 | 586.4807 | 1366.7098 | 53.9562 | 43.6841 | 10.2721 | 30.7575 | 50.9232 | 0 | 1787.3779 | 89.4296 | 80.317 | 9.1126 | 25.0462 | 69.7354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9941 | 460.9601 | 457.7601 | 461.6601 | 413.9301 | 443.7901 | 420.2401 | 315.3601 | 0.53772 | -0.077396 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7064779.0123 | 8147134.7617 | 8147134.7617 | 62.4287 | 62.1849 | 1.0018 | 0.998 | 683916.2604 | 892707.8793 | 460.1267 | 0.51435 | 0 | 0 | 30.7575 | 25.0462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017912 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 596.3806 | 1368.0495 | 54.3377 | 43.9048 | 30.982 | 1787.4562 | 78.9844 | 25.0327 | 460.2507 | 0.0064762 | 60.0023 | 0.53038 | 0.47823 | 88.1854 | 2.3575 | 0.68212 | 0.44601 | 4.4543 | 1.3239 | 0.40462 | 0 | 100 | 579.4 | 316 | 106.95 | 103.89 | 100.77 | 308.2 | 3 | 91.32 | 42.09 | 4 | 37.3 | 43.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.2 | 0 | 38.06 | 61 | 61 | 101.38 | 88.3 | 83.73 | 0 | 100.77 | 2.27 | 90.38 | 42.85 | 106.95 | 12.59 | 103.89 | 110 | 0 | 15694 | 80.39 | 114.98 | 219.75 | 213.74 | 219.2 | 0 | 33.55 | 50.12 | 13538 | 91.31 | 42.08 | 37.29 | 0.93 | 42.08 | 0 | 605 | 432.7 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 312.8 | 0 | 306.6 | 100.73 | 15693 | 15694 | 316
03/26/22 10:36:06.199 | 586.9254 | 1366.9678 | 53.9614 | 43.6866 | 10.2748 | 31.6832 | 50.9071 | 0 | 1783.3162 | 89.4405 | 80.3253 | 9.1152 | 23.876 | 69.702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9961 | 461.0201 | 457.8001 | 461.7201 | 413.9501 | 443.7901 | 420.1701 | 315.3301 | 0.53726 | 0.27903 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7070935.6508 | 8124151.6919 | 8124151.6919 | 62.4287 | 62.1848 | 1.0018 | 0.99799 | 684244.0936 | 890058.6227 | 460.1801 | 0.51719 | 0 | 0 | 31.6832 | 23.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.01791 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 596.1873 | 1368.0461 | 54.3278 | 43.8984 | 30.9864 | 1787.4679 | 79.0085 | 25.0255 | 460.2549 | 0.0064852 | 60.0022 | 0.53049 | 0.47068 | 88.2075 | 2.3584 | 0.67453 | 0.44064 | 4.4384 | 1.3084 | 0.39989 | 0 | 100 | 579.6 | 317 | 107.03 | 103.92 | 100.8 | 308.5 | 3 | 91.35 | 42.1 | 4 | 37.3 | 43.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.23 | 0 | 38.06 | 61 | 61 | 101.43 | 88.34 | 83.77 | 0 | 100.8 | 2.27 | 90.39 | 42.85 | 107.05 | 12.58 | 103.94 | 110 | 0 | 15694 | 80.39 | 114.98 | 219.75 | 213.74 | 219.2 | 0 | 33.53 | 50.1 | 13543 | 91.36 | 42.09 | 37.3 | 0.96 | 42.09 | 0 | 605 | 432.4 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 315.4 | 0 | 309.2 | 100.82 | 15690 | 15694 | 317
03/26/22 10:36:11.199 | 587.9485 | 1369.0735 | 53.9649 | 43.688 | 10.2769 | 31.2396 | 50.9247 | 0 | 1782.4078 | 89.4476 | 80.3308 | 9.1168 | 24.6779 | 69.7226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9961 | 461.0501 | 457.8201 | 461.7501 | 413.9201 | 443.7801 | 420.1601 | 315.3301 | 0.53632 | 0.44767 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7082866.0911 | 8122373.2093 | 8122373.2093 | 62.4287 | 62.1848 | 1.0018 | 0.99799 | 685297.9521 | 889604.5245 | 460.2068 | 0.51861 | 0 | 0 | 31.2396 | 24.6779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.01792 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 595.9806 | 1368.0265 | 54.318 | 43.892 | 30.9945 | 1787.4423 | 79.0324 | 25.0126 | 460.2588 | 0.0064938 | 60.0021 | 0.53062 | 0.46403 | 88.2293 | 2.3408 | 0.66669 | 0.43526 | 4.451 | 1.2929 | 0.39554 | 0 | 100 | 580 | 315 | 107.1 | 103.94 | 100.87 | 307.9 | 3 | 91.38 | 42.09 | 4 | 37.3 | 43.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.3 | 0 | 38.07 | 61 | 61 | 101.5 | 88.38 | 83.73 | 0 | 100.87 | 2.27 | 90.43 | 42.86 | 107.13 | 12.54 | 103.94 | 110 | 0 | 15694 | 80.39 | 114.95 | 219.75 | 213.74 | 219.2 | 0 | 33.46 | 50 | 13548 | 91.4 | 42.09 | 37.3 | 0.94 | 42.09 | 0 | 605 | 431.5 | 458.6 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 314.8 | 0 | 308.6 | 100.87 | 15693 | 15694 | 316
03/26/22 10:36:16.199 | 588.6821 | 1370.725 | 53.9669 | 43.6891 | 10.2778 | 30.8492 | 50.9263 | 0 | 1781.1021 | 89.4533 | 80.3361 | 9.1172 | 25.4782 | 69.7515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 461.05 | 457.82 | 461.75 | 413.92 | 443.78 | 420.16 | 315.33 | 0.53565 | 0.66044 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7091354.4281 | 8113542.2092 | 8113542.2092 | 62.4287 | 62.1847 | 1.0018 | 0.99799 | 686098.7109 | 888501.4785 | 460.2067 | 0.51861 | 0 | 0 | 30.8492 | 25.4782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017917 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 595.7782 | 1368.023 | 54.3081 | 43.8857 | 30.9937 | 1787.3886 | 79.0561 | 25.0151 | 460.2627 | 0.0065021 | 60.002 | 0.53074 | 0.4596 | 88.2509 | 2.3362 | 0.65858 | 0.42981 | 4.4798 | 1.2773 | 0.39157 | 0 | 100 | 579.8 | 317 | 107.05 | 103.94 | 100.83 | 309 | 3 | 91.36 | 42.08 | 4 | 37.29 | 42.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.33 | 0 | 38.06 | 61 | 61 | 101.53 | 88.4 | 83.66 | 0 | 100.83 | 2.27 | 90.45 | 42.85 | 107.08 | 12.57 | 103.94 | 110 | 0 | 15694 | 80.39 | 114.93 | 219.75 | 213.74 | 219.2 | 0 | 33.41 | 49.92 | 13553 | 91.37 | 42.08 | 37.29 | 0.92 | 42.08 | 0 | 606 | 432 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 313 | 0 | 306.8 | 100.82 | 15693 | 15694 | 315
03/26/22 10:36:21.198 | 588.3445 | 1369.858 | 53.9677 | 43.6898 | 10.2779 | 30.7057 | 50.923 | 0 | 1783.0065 | 89.4565 | 80.3397 | 9.1168 | 25.7863 | 69.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.999 | 461.09 | 457.87 | 461.78 | 413.93 | 443.72 | 420.13 | 315.33 | 0.53596 | 0.45102 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7087163.8157 | 8126379.6909 | 8126379.6909 | 62.4287 | 62.1847 | 1.0018 | 0.99799 | 685690.4956 | 889902.1429 | 460.2467 | 0.51639 | 0 | 0 | 30.7057 | 25.7863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017915 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 595.5741 | 1368.0209 | 54.2982 | 43.8793 | 30.9926 | 1787.3487 | 79.0797 | 25.0192 | 460.2665 | 0.0065103 | 60.0019 | 0.53087 | 0.4541 | 88.2724 | 2.3344 | 0.6502 | 0.42421 | 4.4867 | 1.2613 | 0.38801 | 0 | 100 | 579.7 | 314 | 107.05 | 103.94 | 100.82 | 305 | 3 | 91.36 | 42.09 | 4 | 37.3 | 42.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.28 | 0 | 38.06 | 61 | 61 | 101.48 | 88.37 | 83.66 | 0 | 100.82 | 2.27 | 90.42 | 42.85 | 107.05 | 12.58 | 103.94 | 110 | 0 | 15694 | 80.39 | 114.9 | 219.75 | 213.85 | 219.2 | 0 | 33.23 | 49.68 | 13558 | 91.36 | 42.09 | 37.3 | 0.89 | 42.09 | 0 | 606 | 433.1 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 313 | 0 | 306.8 | 100.89 | 15694 | 15694 | 316
03/26/22 10:36:26.198 | 588.261 | 1369.667 | 53.97 | 43.6921 | 10.2779 | 31.8159 | 50.9255 | 0 | 1784.3484 | 89.4685 | 80.3526 | 9.1159 | 24.1094 | 69.7573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.003 | 461.12 | 457.9 | 461.8 | 413.94 | 443.68 | 420.16 | 315.33 | 0.53604 | 0.40949 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7087134.5583 | 8129726.1852 | 8129726.1852 | 62.4287 | 62.1845 | 1.0018 | 0.99799 | 685594.8071 | 890570.0981 | 460.2734 | 0.51564 | 0 | 0 | 31.8159 | 24.1094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017921 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 595.3838 | 1368.0529 | 54.2883 | 43.8731 | 30.9996 | 1787.3174 | 79.1031 | 25.0084 | 460.2703 | 0.0065184 | 60.0017 | 0.53098 | 0.4509 | 88.2936 | 2.3172 | 0.64145 | 0.41847 | 4.4878 | 1.2455 | 0.38478 | 0 | 100 | 580.1 | 317 | 107.03 | 103.94 | 100.89 | 308.4 | 3 | 91.35 | 42.1 | 4 | 37.31 | 42.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.25 | 0 | 38.09 | 61 | 61 | 101.43 | 88.33 | 83.71 | 0 | 100.89 | 2.27 | 90.41 | 42.86 | 107 | 12.61 | 103.94 | 110 | 0 | 15694 | 80.39 | 114.9 | 219.87 | 213.85 | 219.2 | 0 | 33.06 | 49.6 | 13563 | 91.33 | 42.11 | 37.33 | 0.86 | 42.11 | 0 | 606 | 432.8 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.8 | 315.3 | 0 | 309 | 100.83 | 15693 | 15694 | 316
03/26/22 10:36:31.198 | 588.8179 | 1370.9314 | 53.9715 | 43.6934 | 10.2782 | 31.7303 | 50.9226 | 0 | 1785.298 | 89.4756 | 80.3596 | 9.1161 | 24.1387 | 69.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0031 | 461.1201 | 457.9001 | 461.8001 | 413.9401 | 443.6801 | 420.1601 | 315.3301 | 0.53553 | 0.43539 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7093768.6483 | 8134225.7524 | 8134225.7524 | 62.4286 | 62.1845 | 1.0018 | 0.99799 | 686227.659 | 891043.1188 | 460.2734 | 0.51564 | 0 | 0 | 31.7303 | 24.1387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017921 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 595.1979 | 1368.0981 | 54.2784 | 43.8668 | 31.0025 | 1787.3037 | 79.1264 | 25.0027 | 460.274 | 0.0065265 | 60.0016 | 0.53109 | 0.4474 | 88.3148 | 2.2932 | 0.63235 | 0.41254 | 4.4902 | 1.2293 | 0.38149 | 0 | 100 | 580.9 | 313 | 107.05 | 103.94 | 101.04 | 307.2 | 3 | 91.36 | 42.13 | 4 | 37.34 | 42.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.3 | 0 | 38.1 | 60 | 60 | 101.5 | 88.38 | 83.66 | 0 | 101.04 | 2.27 | 90.43 | 42.89 | 107.1 | 12.56 | 103.94 | 110 | 0 | 15694 | 80.41 | 114.9 | 219.87 | 213.85 | 219.2 | 0 | 33.04 | 49.87 | 13568 | 91.38 | 42.13 | 37.34 | 0.85 | 42.13 | 0 | 605 | 432.2 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.6 | 316.4 | 0 | 310.1 | 100.97 | 15695 | 15694 | 318
03/26/22 10:36:36.198 | 588.6548 | 1370.5599 | 53.9735 | 43.6954 | 10.2781 | 31.8835 | 50.9369 | 0 | 1781.5924 | 89.4862 | 80.3702 | 9.116 | 23.963 | 69.7743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 461.21 | 457.99 | 461.87 | 414.11 | 443.8 | 420.41 | 315.48 | 0.53593 | 0.63071 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7091938.3286 | 8117043.7341 | 8117043.7341 | 62.4286 | 62.1844 | 1.0018 | 0.99799 | 686041.5798 | 889192.2134 | 460.3567 | 0.51409 | 0 | 0 | 31.8835 | 23.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017935 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 595.0021 | 1368.1218 | 54.2685 | 43.8605 | 31.0049 | 1787.2703 | 79.1496 | 24.9995 | 460.2779 | 0.006535 | 60.0015 | 0.53121 | 0.44391 | 88.3358 | 2.2915 | 0.62287 | 0.40642 | 4.5054 | 1.2129 | 0.37824 | 0 | 100 | 580.2 | 316 | 107.13 | 103.94 | 100.9 | 307.7 | 3 | 91.41 | 42.11 | 4 | 37.33 | 42.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.38 | 0 | 38.07 | 60 | 60 | 101.65 | 88.47 | 83.68 | 0 | 100.9 | 2.28 | 90.47 | 42.86 | 107.13 | 12.54 | 103.94 | 110 | 0 | 15694 | 80.41 | 114.9 | 219.87 | 213.85 | 219.2 | 0 | 33.31 | 50.4 | 13573 | 91.42 | 42.1 | 37.31 | 0.85 | 42.1 | 0 | 606 | 430.2 | 458.7 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 316 | 0 | 309.7 | 100.89 | 15691 | 15694 | 316
03/26/22 10:36:41.198 | 589.4338 | 1372.4849 | 53.9747 | 43.6975 | 10.2773 | 31.3822 | 50.9532 | 0 | 1781.3498 | 89.4944 | 80.3791 | 9.1152 | 24.8146 | 69.7804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.015 | 461.24 | 458.02 | 461.89 | 414.13 | 443.82 | 420.47 | 315.51 | 0.53528 | 0.74974 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7100883.397 | 8116265.9401 | 8116265.9401 | 62.4286 | 62.1843 | 1.0018 | 0.99799 | 687005.1177 | 889069.936 | 460.3834 | 0.51334 | 0 | 0 | 31.3822 | 24.8146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.01793 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 594.7987 | 1368.139 | 54.2585 | 43.8542 | 31.0094 | 1787.2443 | 79.1727 | 24.9961 | 460.2821 | 0.0065439 | 60.0015 | 0.53134 | 0.43918 | 88.3567 | 2.3017 | 0.61295 | 0.40005 | 4.5285 | 1.1962 | 0.37499 | 0 | 100 | 580 | 316 | 107.23 | 103.94 | 100.87 | 308.6 | 3 | 91.46 | 42.11 | 4 | 37.33 | 42.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.43 | 0 | 38.07 | 60 | 60 | 101.7 | 88.49 | 83.64 | 0 | 100.87 | 2.28 | 90.5 | 42.86 | 107.23 | 12.49 | 103.94 | 110 | 0 | 15694 | 80.41 | 114.9 | 219.87 | 213.85 | 219.32 | 0 | 33.55 | 50.62 | 13578 | 91.45 | 42.11 | 37.33 | 0.84 | 42.11 | 0 | 606 | 431.6 | 458.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.3 | 315.4 | 0 | 309.1 | 100.92 | 15693 | 15694 | 317
03/26/22 10:36:46.198 | 588.9264 | 1371.3702 | 53.9755 | 43.6988 | 10.2768 | 31.1418 | 50.9462 | 0 | 1785.3806 | 89.4988 | 80.3841 | 9.1147 | 24.8373 | 69.7565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0151 | 461.2401 | 458.0201 | 461.8901 | 414.1301 | 443.8201 | 420.4701 | 315.5101 | 0.53574 | 0.45317 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7094560.5172 | 8134179.8563 | 8134179.8563 | 62.4286 | 62.1842 | 1.0018 | 0.99799 | 686447.0834 | 891081.0057 | 460.3834 | 0.51334 | 0 | 0 | 31.1418 | 24.8373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.01792 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 594.5954 | 1368.1601 | 54.2484 | 43.8479 | 31.0134 | 1787.2397 | 79.1956 | 24.9885 | 460.2865 | 0.0065534 | 60.0014 | 0.53146 | 0.43383 | 88.3774 | 2.3139 | 0.60251 | 0.39339 | 4.5299 | 1.1795 | 0.37149 | 0 | 100 | 580.1 | 317 | 107.25 | 103.97 | 100.9 | 309.4 | 3 | 91.46 | 42.11 | 4 | 37.33 | 42.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.4 | 0 | 38.09 | 60 | 60 | 101.7 | 88.49 | 83.64 | 0 | 100.9 | 2.28 | 90.49 | 42.88 | 107.25 | 12.5 | 103.97 | 110 | 0 | 15694 | 80.41 | 114.9 | 219.87 | 213.85 | 219.32 | 0 | 33.56 | 50.43 | 13583 | 91.46 | 42.11 | 37.33 | 0.84 | 42.11 | 0 | 606 | 431.7 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 315.6 | 0 | 309.4 | 100.89 | 15692 | 15694 | 314
03/26/22 10:36:51.198 | 588.1439 | 1369.6773 | 53.9777 | 43.7019 | 10.2758 | 30.5884 | 50.9377 | 0 | 1792.5389 | 89.5103 | 80.3965 | 9.1138 | 25.6404 | 69.7652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0101 | 461.2901 | 458.0501 | 461.9101 | 414.2101 | 443.8201 | 420.4701 | 315.5401 | 0.5365 | -0.068016 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7084649.9745 | 8166869.5385 | 8166869.5385 | 62.4286 | 62.1841 | 1.0018 | 0.99799 | 685599.6366 | 894652.0107 | 460.4167 | 0.51403 | 0 | 0 | 30.5884 | 25.6404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017914 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 594.3918 | 1368.1841 | 54.2383 | 43.8415 | 31.0143 | 1787.2336 | 79.2185 | 24.984 | 460.291 | 0.0065632 | 60.0014 | 0.53159 | 0.4287 | 88.3979 | 2.3122 | 0.59155 | 0.38642 | 4.5248 | 1.1624 | 0.36799 | 0 | 100 | 580.1 | 317 | 107.2 | 103.99 | 100.85 | 306.3 | 3 | 91.44 | 42.11 | 4 | 37.31 | 43.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.4 | 0 | 38.09 | 60 | 60 | 101.7 | 88.49 | 83.6 | 0 | 100.85 | 2.28 | 90.49 | 42.88 | 107.18 | 12.57 | 103.99 | 110 | 0 | 15694 | 80.41 | 114.9 | 219.87 | 213.85 | 219.32 | 0 | 33.45 | 50.3 | 13588 | 91.42 | 42.1 | 37.31 | 0.95 | 42.1 | 0 | 606 | 429.6 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.9 | 313.7 | 0 | 307.4 | 100.85 | 15693 | 15694 | 316
03/26/22 10:36:56.198 | 588.0737 | 1369.378 | 53.9782 | 43.7026 | 10.2756 | 30.2209 | 50.943 | 0 | 1792.9518 | 89.5132 | 80.3996 | 9.1136 | 26.3551 | 69.7817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0101 | 461.2901 | 458.0501 | 461.9101 | 414.2101 | 443.8201 | 420.4701 | 315.5401 | 0.53657 | -0.095928 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7083642.2299 | 8168140.9136 | 8168140.9136 | 62.4286 | 62.1841 | 1.0018 | 0.99799 | 685524.7018 | 894754.8325 | 460.4168 | 0.51403 | 0 | 0 | 30.2209 | 26.3551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017888 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 594.1791 | 1368.1924 | 54.2281 | 43.8352 | 31.0102 | 1787.2522 | 79.2412 | 24.9907 | 460.2955 | 0.0065729 | 60.0013 | 0.53173 | 0.42126 | 88.4183 | 2.3138 | 0.57994 | 0.37907 | 4.5415 | 1.1451 | 0.36451 | 0 | 100 | 580.3 | 314 | 107.2 | 104.01 | 100.94 | 309.3 | 3 | 91.44 | 42.1 | 4 | 37.31 | 43.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.38 | 0 | 38.09 | 60 | 60 | 101.63 | 88.45 | 83.58 | 0 | 100.94 | 2.27 | 90.47 | 42.88 | 107.2 | 12.57 | 104.01 | 110 | 0 | 15694 | 80.41 | 114.88 | 219.87 | 213.85 | 219.32 | 0 | 33.45 | 50.18 | 13593 | 91.44 | 42.1 | 37.31 | 0.97 | 42.1 | 0 | 605 | 431 | 458.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.4 | 314.2 | 0 | 308 | 100.94 | 15692 | 15694 | 316
03/26/22 10:37:01.199 | 585.9171 | 1364.5782 | 53.9818 | 43.7066 | 10.2752 | 30.805 | 50.929 | 0 | 1803.0054 | 89.5297 | 80.4168 | 9.1129 | 25.1566 | 69.7619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.01 | 461.31 | 458.07 | 461.92 | 414.21 | 443.83 | 420.58 | 315.57 | 0.53859 | -0.96043 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7058017.7098 | 8213189.2406 | 8213189.2406 | 62.4286 | 62.1839 | 1.0018 | 0.99799 | 683047.0804 | 899873.0347 | 460.4334 | 0.51328 | 0 | 0 | 30.805 | 25.1566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017892 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 593.9463 | 1368.1593 | 54.2179 | 43.8287 | 31.0091 | 1787.3352 | 79.2638 | 24.9895 | 460.3 | 0.0065826 | 60.0013 | 0.53188 | 0.40769 | 88.4386 | 2.3226 | 0.56772 | 0.37133 | 4.6905 | 1.1275 | 0.36094 | 0 | 100 | 580.6 | 316 | 107.13 | 104.01 | 100.97 | 309 | 3 | 91.4 | 42.1 | 4 | 37.31 | 43.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.3 | 0 | 38.09 | 60 | 60 | 101.6 | 88.44 | 83.47 | 0 | 100.97 | 2.27 | 90.43 | 42.88 | 107.13 | 12.59 | 103.99 | 110 | 0 | 15694 | 80.41 | 114.88 | 219.87 | 213.95 | 219.32 | 0 | 33.33 | 49.98 | 13599 | 91.4 | 42.1 | 37.31 | 0.97 | 42.1 | 0 | 606 | 434.8 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.2 | 315.6 | 0 | 309.3 | 100.9 | 15694 | 15694 | 318
03/26/22 10:37:06.197 | 587.1949 | 1367.3962 | 53.9854 | 43.709 | 10.2764 | 30.7181 | 50.9304 | 0 | 1792.1312 | 89.5386 | 80.4243 | 9.1143 | 24.9756 | 69.7618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.005 | 461.31 | 458.07 | 461.93 | 414.06 | 443.73 | 420.52 | 315.49 | 0.53728 | -0.17834 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7073330.2677 | 8164647.434 | 8164647.434 | 62.4286 | 62.1838 | 1.0018 | 0.99799 | 684457.4377 | 894444.732 | 460.4367 | 0.514 | 0 | 0 | 30.7181 | 24.9756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017904 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 593.7098 | 1368.1181 | 54.2076 | 43.8223 | 31.01 | 1787.4128 | 79.2864 | 24.9865 | 460.3044 | 0.0065921 | 60.0012 | 0.53204 | 0.39368 | 88.4589 | 2.3174 | 0.55489 | 0.3632 | 4.7804 | 1.1095 | 0.35767 | 0 | 100 | 580.1 | 317 | 107.25 | 103.99 | 100.89 | 308.8 | 3 | 91.45 | 42.11 | 4 | 37.33 | 43.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.4 | 0 | 38.1 | 60 | 60 | 101.67 | 88.48 | 83.47 | 0 | 100.89 | 2.27 | 90.49 | 42.89 | 107.25 | 12.53 | 103.99 | 110 | 0 | 15694 | 80.41 | 114.83 | 219.87 | 213.95 | 219.32 | 0 | 33.18 | 49.82 | 13604 | 91.46 | 42.11 | 37.33 | 0.95 | 42.11 | 0 | 606 | 431 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 314.4 | 0 | 308.1 | 100.82 | 15693 | 15694 | 316
03/26/22 10:37:11.198 | 587.8293 | 1369.1148 | 53.9897 | 43.7116 | 10.2782 | 30.6293 | 50.9443 | 0 | 1788.0075 | 89.5462 | 80.4304 | 9.1158 | 25.7913 | 69.7767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.004 | 461.33 | 458.1 | 461.95 | 413.86 | 443.61 | 420.44 | 315.4 | 0.53655 | 0.12982 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7080817.0023 | 8146730.4958 | 8146730.4958 | 62.4286 | 62.1837 | 1.0018 | 0.99799 | 685097.9556 | 892249.4147 | 460.46 | 0.51253 | 0 | 0 | 30.6293 | 25.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017894 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 593.4897 | 1368.1044 | 54.1973 | 43.8158 | 31.0087 | 1787.3932 | 79.3088 | 24.9867 | 460.3088 | 0.0066017 | 60.0011 | 0.53219 | 0.38727 | 88.479 | 2.3067 | 0.54153 | 0.35453 | 4.7717 | 1.0913 | 0.35428 | 0 | 100 | 579 | 316 | 107.25 | 104.03 | 100.7 | 307 | 3 | 91.46 | 42.11 | 4 | 37.33 | 43.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.4 | 0 | 38.1 | 60 | 60 | 101.67 | 88.48 | 83.36 | 0 | 100.7 | 2.27 | 90.49 | 42.89 | 107.2 | 12.61 | 104.05 | 110 | 0 | 15694 | 80.43 | 114.83 | 219.87 | 213.95 | 219.32 | 0 | 33.05 | 49.74 | 13608 | 91.44 | 42.11 | 37.33 | 0.99 | 42.11 | 0 | 606 | 433.7 | 458.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.1 | 313.3 | 0 | 307 | 100.71 | 15693 | 15694 | 315
03/26/22 10:37:16.198 | 588.5146 | 1370.1521 | 53.9915 | 43.7128 | 10.2788 | 30.8035 | 50.9466 | 0 | 1789.5403 | 89.5492 | 80.433 | 9.1163 | 25.6073 | 69.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.004 | 461.33 | 458.1 | 461.95 | 413.86 | 443.61 | 420.44 | 315.4 | 0.53593 | 0.1246 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7089297.1074 | 8155318.4531 | 8155318.4531 | 62.4286 | 62.1837 | 1.0018 | 0.99799 | 685836.6856 | 893150.4706 | 460.46 | 0.51253 | 0 | 0 | 30.8035 | 25.6073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01621 | 0.017897 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 593.29 | 1368.1195 | 54.1871 | 43.8093 | 31.0031 | 1787.3878 | 79.331 | 24.9919 | 460.3133 | 0.0066113 | 60.001 | 0.53233 | 0.38176 | 88.499 | 2.3111 | 0.52785 | 0.34535 | 4.7688 | 1.0731 | 0.35106 | 0 | 100 | 579 | 318 | 107.15 | 104.09 | 100.7 | 307.8 | 3 | 91.41 | 42.1 | 4 | 37.31 | 43.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.38 | 0 | 38.09 | 60 | 60 | 101.67 | 88.48 | 83.34 | 0 | 100.7 | 2.27 | 90.47 | 42.88 | 107.18 | 12.68 | 104.09 | 110 | 0 | 15694 | 80.43 | 114.83 | 219.98 | 213.95 | 219.32 | 0 | 33.05 | 49.89 | 13613 | 91.41 | 42.1 | 37.31 | 1.15 | 42.1 | 0 | 606 | 432.7 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 311.7 | 0 | 305.5 | 100.73 | 15694 | 15694 | 315
03/26/22 10:37:21.198 | 588.1268 | 1369.1715 | 53.9961 | 43.7167 | 10.2794 | 30.19 | 50.935 | 0 | 1796.4664 | 89.5572 | 80.4407 | 9.1166 | 26.4419 | 69.8684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.002 | 461.31 | 458.09 | 461.96 | 413.71 | 443.61 | 420.45 | 315.36 | 0.53621 | -0.34212 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7084083.576 | 8188101.6364 | 8188101.6364 | 62.4286 | 62.1836 | 1.0018 | 0.99799 | 685345.644 | 896606.1865 | 460.4534 | 0.51326 | 0 | 0 | 30.19 | 26.4419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017877 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 593.1048 | 1368.1328 | 54.1772 | 43.8027 | 30.9978 | 1787.4083 | 79.3528 | 24.9972 | 460.3175 | 0.0066204 | 60.0009 | 0.53245 | 0.37482 | 88.5188 | 2.3331 | 0.51425 | 0.33556 | 4.7681 | 1.0552 | 0.34816 | 0 | 100 | 579.8 | 316 | 107.2 | 104.09 | 100.83 | 306.6 | 3 | 91.44 | 42.11 | 4 | 37.33 | 43.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.4 | 0 | 38.1 | 60 | 60 | 101.7 | 88.49 | 83.32 | 0 | 100.83 | 2.27 | 90.49 | 42.89 | 107.2 | 12.65 | 104.09 | 110 | 0 | 15694 | 80.43 | 114.81 | 219.98 | 213.95 | 219.32 | 0 | 33.01 | 49.84 | 13618 | 91.44 | 42.13 | 37.34 | 1.2 | 42.13 | 0 | 606 | 430.4 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 314.4 | 0 | 308.1 | 100.87 | 15693 | 15694 | 316
03/26/22 10:37:26.198 | 586.3103 | 1364.8982 | 53.9976 | 43.7179 | 10.2797 | 31.0078 | 50.9497 | 0 | 1798.9385 | 89.5596 | 80.4428 | 9.1168 | 25.0817 | 69.8585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.999 | 461.29 | 458.1 | 461.97 | 413.51 | 443.58 | 420.38 | 315.28 | 0.53774 | -0.72599 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7062920.4983 | 8198002.1318 | 8198002.1318 | 62.4286 | 62.1836 | 1.0018 | 0.99799 | 683206.5422 | 897839.7263 | 460.4533 | 0.51109 | 0 | 0 | 31.0078 | 25.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017897 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 592.9169 | 1368.1016 | 54.1675 | 43.7961 | 30.9973 | 1787.4882 | 79.3742 | 24.9974 | 460.3215 | 0.006629 | 60.0008 | 0.53258 | 0.36181 | 88.5384 | 2.3386 | 0.50095 | 0.3253 | 4.84 | 1.0379 | 0.3456 | 0 | 100 | 579.3 | 315 | 107.13 | 104.09 | 100.75 | 307.6 | 3 | 91.4 | 42.11 | 4 | 37.33 | 43.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.35 | 0 | 38.11 | 60 | 60 | 101.65 | 88.47 | 83.24 | 0 | 100.75 | 2.27 | 90.46 | 42.9 | 107.15 | 12.66 | 104.07 | 110 | 0 | 15694 | 80.43 | 114.81 | 219.98 | 213.95 | 219.32 | 0 | 32.87 | 49.76 | 13623 | 91.41 | 42.11 | 37.33 | 1.25 | 42.11 | 0 | 606 | 430.9 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 312.1 | 0 | 305.9 | 100.61 | 15694 | 15694 | 315
03/26/22 10:37:31.198 | 587.1419 | 1366.6065 | 54.0017 | 43.7203 | 10.2814 | 31.3579 | 50.928 | 0 | 1784.4671 | 89.565 | 80.4461 | 9.1189 | 24.4879 | 69.8069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9951 | 461.2701 | 458.1401 | 462.0401 | 413.0301 | 443.5001 | 420.2301 | 315.1301 | 0.53672 | 0.19422 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7073240.5033 | 8133208.2885 | 8133208.2885 | 62.4286 | 62.1836 | 1.0018 | 0.99799 | 684061.4637 | 890616.6551 | 460.4834 | 0.50889 | 0 | 0 | 31.3579 | 24.4879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.0179 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 592.7432 | 1368.0808 | 54.158 | 43.7895 | 30.9984 | 1787.5152 | 79.3953 | 24.9941 | 460.3254 | 0.0066375 | 60.0007 | 0.5327 | 0.35237 | 88.5579 | 2.3393 | 0.48768 | 0.31464 | 4.8243 | 1.0207 | 0.34297 | 0 | 100 | 578.7 | 317 | 107.25 | 104.07 | 100.64 | 307.4 | 3 | 91.46 | 42.11 | 4 | 37.33 | 43.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.43 | 0 | 38.1 | 60 | 60 | 101.73 | 88.49 | 83.17 | 0 | 100.64 | 2.27 | 90.49 | 42.89 | 107.23 | 12.62 | 104.07 | 110 | 0 | 15694 | 80.43 | 114.79 | 219.98 | 213.95 | 219.32 | 0 | 32.91 | 49.97 | 13628 | 91.45 | 42.11 | 37.33 | 1.37 | 42.11 | 0 | 606 | 432.6 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 313.7 | 0 | 307.4 | 100.52 | 15691 | 15694 | 317
03/26/22 10:37:36.197 | 587.1153 | 1366.4208 | 54.0028 | 43.7208 | 10.282 | 31.0749 | 50.9338 | 0 | 1782.6607 | 89.5661 | 80.4465 | 9.1195 | 24.7697 | 69.8061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.995 | 461.27 | 458.14 | 462.04 | 413.03 | 443.5 | 420.23 | 315.13 | 0.53674 | 0.22781 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7072796.2717 | 8129523.5701 | 8129523.5701 | 62.4286 | 62.1836 | 1.0018 | 0.99799 | 684014.9495 | 890165.8572 | 460.4834 | 0.50889 | 0 | 0 | 31.0749 | 24.7697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017898 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 592.5944 | 1368.0669 | 54.1491 | 43.7831 | 31.0023 | 1787.4954 | 79.4157 | 24.9852 | 460.3294 | 0.006646 | 60.0005 | 0.53281 | 0.34583 | 88.577 | 2.3418 | 0.47536 | 0.30382 | 4.8369 | 1.0045 | 0.3407 | 0 | 100 | 579.3 | 317 | 107.25 | 104.07 | 100.75 | 307.9 | 3 | 91.46 | 42.11 | 4 | 37.33 | 43.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.45 | 0 | 38.11 | 60 | 60 | 101.75 | 88.52 | 83.19 | 0 | 100.75 | 2.28 | 90.51 | 42.9 | 107.25 | 12.61 | 104.07 | 110 | 0 | 15694 | 80.43 | 114.79 | 219.98 | 213.95 | 219.44 | 0 | 33.04 | 50.18 | 13633 | 91.46 | 42.11 | 37.34 | 1.41 | 42.11 | 0 | 606 | 432.5 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 311.5 | 0 | 305.3 | 100.64 | 15696 | 15694 | 316
03/26/22 10:37:41.198 | 587.0338 | 1365.9717 | 54.0077 | 43.7234 | 10.2843 | 31.0755 | 50.9412 | 0 | 1785.6128 | 89.5687 | 80.4466 | 9.1221 | 25.1192 | 69.8139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9991 | 461.2801 | 458.1801 | 462.1301 | 412.5601 | 443.4001 | 419.9201 | 314.9501 | 0.53651 | 0.05537 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7071683.2324 | 8142032.2179 | 8142032.2179 | 62.4286 | 62.1835 | 1.0018 | 0.99799 | 683743.4432 | 891188.4272 | 460.5301 | 0.51028 | 0 | 0 | 31.0755 | 25.1192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017889 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 592.4604 | 1368.0483 | 54.1406 | 43.7768 | 31.0077 | 1787.4607 | 79.4356 | 24.975 | 460.3333 | 0.0066545 | 60.0004 | 0.5329 | 0.33997 | 88.5957 | 2.345 | 0.46387 | 0.293 | 4.8278 | 0.98915 | 0.33855 | 0 | 100 | 577.9 | 317 | 107.2 | 104.09 | 100.59 | 307.3 | 3 | 91.44 | 42.11 | 4 | 37.33 | 43.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.43 | 0 | 38.1 | 60 | 60 | 101.73 | 88.51 | 83.21 | 0 | 100.59 | 2.28 | 90.5 | 42.89 | 107.18 | 12.67 | 104.09 | 110 | 0 | 15694 | 80.43 | 114.79 | 219.98 | 213.95 | 219.44 | 0 | 32.96 | 49.99 | 13638 | 91.44 | 42.11 | 37.33 | 1.41 | 42.11 | 0 | 606 | 432.4 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.9 | 313.6 | 0 | 307.3 | 100.5 | 15694 | 15694 | 317
03/26/22 10:37:46.197 | 587.3624 | 1366.4878 | 54.0114 | 43.7252 | 10.2862 | 31.5203 | 50.9397 | 0 | 1786.1599 | 89.5694 | 80.4457 | 9.1237 | 24.1609 | 69.8399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.001 | 461.3 | 458.23 | 462.19 | 412.47 | 443.4 | 419.87 | 314.94 | 0.53619 | 0.070977 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7076026.9803 | 8144897.6763 | 8144897.6763 | 62.4285 | 62.1835 | 1.0018 | 0.99799 | 684001.6232 | 891461.5833 | 460.5733 | 0.50879 | 0 | 0 | 31.5203 | 24.1609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017902 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 592.3452 | 1368.0373 | 54.1325 | 43.7707 | 31.0169 | 1787.418 | 79.4549 | 24.9592 | 460.3374 | 0.0066633 | 60.0002 | 0.53298 | 0.33511 | 88.6142 | 2.3477 | 0.4532 | 0.28223 | 4.8049 | 0.97455 | 0.33643 | 0 | 100 | 578.9 | 317 | 107.2 | 104.09 | 100.68 | 306.6 | 3 | 91.44 | 42.14 | 4 | 37.35 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.43 | 0 | 38.14 | 60 | 60 | 101.75 | 88.52 | 83.17 | 0 | 100.7 | 2.27 | 90.5 | 42.92 | 107.2 | 12.65 | 104.09 | 110 | 0 | 15694 | 80.43 | 114.76 | 219.98 | 213.95 | 219.44 | 0 | 32.8 | 49.84 | 13643 | 91.44 | 42.14 | 37.35 | 1.63 | 42.14 | 0 | 606 | 431 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.6 | 314.6 | 0 | 308.3 | 100.8 | 15693 | 15694 | 318
03/26/22 10:37:51.197 | 586.113 | 1362.6945 | 54.0158 | 43.7272 | 10.2886 | 31.0288 | 50.9362 | 0 | 1778.7693 | 89.5704 | 80.445 | 9.1254 | 24.6553 | 69.8325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0021 | 461.3001 | 458.2501 | 462.2201 | 412.3901 | 443.3901 | 419.8701 | 314.9301 | 0.53732 | 0.18867 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7060582.0419 | 8119867.5398 | 8119867.5398 | 62.4285 | 62.1835 | 1.0018 | 0.99799 | 682415.274 | 888543.2587 | 460.5901 | 0.50804 | 0 | 0 | 31.0288 | 24.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017916 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 592.235 | 1368.009 | 54.1248 | 43.7647 | 31.0221 | 1787.3322 | 79.4737 | 24.9487 | 460.3416 | 0.0066724 | 60.0001 | 0.53305 | 0.3314 | 88.6323 | 2.3737 | 0.44324 | 0.27156 | 4.7931 | 0.96053 | 0.33461 | 0 | 100 | 578.8 | 315 | 107.35 | 104.11 | 100.66 | 306.1 | 3 | 91.52 | 42.15 | 4 | 37.36 | 43.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.53 | 0 | 38.14 | 60 | 60 | 101.83 | 88.56 | 83.13 | 0 | 100.66 | 2.28 | 90.55 | 42.92 | 107.35 | 12.59 | 104.11 | 110 | 0 | 15694 | 80.43 | 114.76 | 219.98 | 213.95 | 219.44 | 0 | 32.72 | 49.88 | 13648 | 91.52 | 42.15 | 37.36 | 1.69 | 42.15 | 0 | 606 | 430 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 313.3 | 0 | 307.1 | 100.57 | 15693 | 15694 | 315
03/26/22 10:37:56.197 | 585.6868 | 1362.1681 | 54.0174 | 43.7281 | 10.2894 | 30.7377 | 50.9395 | 0 | 1777.5307 | 89.5709 | 80.4452 | 9.1257 | 25.1639 | 69.8135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0021 | 461.3001 | 458.2501 | 462.2201 | 412.3901 | 443.3901 | 419.8701 | 314.9301 | 0.53771 | 0.2623 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7055147.1312 | 8108436.0197 | 8108436.0197 | 62.4285 | 62.1835 | 1.0018 | 0.99799 | 681839.0768 | 887154.883 | 460.5901 | 0.50804 | 0 | 0 | 30.7377 | 25.1639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.0179 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 592.1321 | 1367.9562 | 54.1178 | 43.7591 | 31.0174 | 1787.2402 | 79.4917 | 24.9537 | 460.3458 | 0.0066815 | 59.9999 | 0.53312 | 0.32645 | 88.6499 | 2.3974 | 0.43486 | 0.2617 | 4.8215 | 0.94803 | 0.33291 | 0 | 100 | 578.7 | 317 | 107.3 | 104.13 | 100.68 | 306.8 | 3 | 91.49 | 42.14 | 4 | 37.35 | 43.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.48 | 0 | 38.13 | 60 | 60 | 101.75 | 88.52 | 83.17 | 0 | 100.68 | 2.27 | 90.53 | 42.91 | 107.3 | 12.64 | 104.13 | 110 | 0 | 15694 | 80.43 | 114.76 | 219.98 | 213.95 | 219.44 | 0 | 32.71 | 49.91 | 13653 | 91.49 | 42.14 | 37.35 | 1.68 | 42.14 | 0 | 606 | 429.5 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 313.1 | 0 | 306.8 | 100.64 | 15693 | 15694 | 317
03/26/22 10:38:01.197 | 586.7823 | 1364.5834 | 54.0212 | 43.7308 | 10.2904 | 31.3829 | 50.9404 | 0 | 1783.2439 | 89.5736 | 80.4476 | 9.1261 | 24.3576 | 69.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.002 | 461.3 | 458.25 | 462.22 | 412.39 | 443.39 | 419.87 | 314.93 | 0.53671 | 0.1181 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7068907.0563 | 8133880.9093 | 8133880.9093 | 62.4285 | 62.1835 | 1.0018 | 0.99799 | 683047.9227 | 890005.9814 | 460.59 | 0.50804 | 0 | 0 | 31.3829 | 24.3576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017905 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 592.0508 | 1367.9285 | 54.1114 | 43.7539 | 31.0126 | 1787.2266 | 79.5092 | 24.9567 | 460.35 | 0.0066906 | 59.9998 | 0.53316 | 0.3187 | 88.667 | 2.4074 | 0.42754 | 0.25265 | 4.8293 | 0.9365 | 0.33115 | 0 | 100 | 579 | 317 | 107.35 | 104.13 | 100.7 | 307.9 | 3 | 91.52 | 42.14 | 4 | 37.35 | 43.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.5 | 0 | 38.13 | 60 | 60 | 101.8 | 88.55 | 83.15 | 0 | 100.7 | 2.28 | 90.54 | 42.91 | 107.35 | 12.6 | 104.13 | 110 | 0 | 15694 | 80.43 | 114.76 | 219.98 | 213.95 | 219.44 | 0 | 32.68 | 49.95 | 13658 | 91.53 | 42.15 | 37.36 | 1.77 | 42.15 | 0 | 606 | 431.5 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 316.1 | 0 | 309.8 | 100.73 | 15694 | 15694 | 316
03/26/22 10:38:06.197 | 587.618 | 1366.7407 | 54.0234 | 43.7326 | 10.2908 | 30.891 | 50.942 | 0 | 1783.5691 | 89.5762 | 80.4502 | 9.126 | 24.9596 | 69.8403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.009 | 461.37 | 458.35 | 462.3 | 412.29 | 443.2 | 419.79 | 314.9 | 0.53589 | 0.18566 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7078736.7902 | 8138096.5229 | 8138096.5229 | 62.4285 | 62.1835 | 1.0018 | 0.99799 | 683998.5189 | 890428.1431 | 460.6733 | 0.50433 | 0 | 0 | 30.891 | 24.9596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017901 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.9717 | 1367.8978 | 54.1054 | 43.7491 | 31.0132 | 1787.2457 | 79.5261 | 24.9528 | 460.3549 | 0.0067011 | 59.9996 | 0.53321 | 0.30904 | 88.6836 | 2.3869 | 0.42109 | 0.24451 | 4.8079 | 0.92574 | 0.32938 | 0 | 100 | 578.9 | 317 | 107.4 | 104.13 | 100.68 | 306.7 | 3 | 91.54 | 42.15 | 4 | 37.36 | 44.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.55 | 0 | 38.14 | 60 | 60 | 101.85 | 88.58 | 83.13 | 0 | 100.68 | 2.28 | 90.57 | 42.92 | 107.4 | 12.59 | 104.13 | 110 | 0 | 15694 | 80.43 | 114.76 | 219.98 | 213.95 | 219.44 | 0 | 32.65 | 50.03 | 13663 | 91.54 | 42.15 | 37.36 | 1.88 | 42.15 | 0 | 606 | 431.3 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 315 | 0 | 308.7 | 100.61 | 15693 | 15694 | 318
03/26/22 10:38:11.197 | 588.5577 | 1368.5884 | 54.0269 | 43.7356 | 10.2912 | 30.9697 | 50.9451 | 0 | 1786.6502 | 89.5808 | 80.4557 | 9.1251 | 24.8743 | 69.8118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0111 | 461.4101 | 458.3801 | 462.3201 | 412.3401 | 443.1301 | 419.7701 | 314.9101 | 0.53505 | 0.16536 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7089900.3891 | 8150928.3827 | 8150928.3827 | 62.4285 | 62.1834 | 1.0018 | 0.99799 | 685060.1312 | 891880.2259 | 460.7034 | 0.5043 | 0 | 0 | 30.9697 | 24.8743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017906 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.9013 | 1367.8895 | 54.0998 | 43.7446 | 31.0179 | 1787.2429 | 79.5426 | 24.9447 | 460.3601 | 0.0067124 | 59.9995 | 0.53324 | 0.3016 | 88.6997 | 2.3819 | 0.4153 | 0.23722 | 4.8081 | 0.91553 | 0.32739 | 0 | 100 | 578.6 | 315 | 107.33 | 104.15 | 100.75 | 308.8 | 3 | 91.5 | 42.15 | 4 | 37.36 | 44.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.55 | 0 | 38.13 | 60 | 60 | 101.83 | 88.56 | 83.17 | 0 | 100.75 | 2.28 | 90.57 | 42.91 | 107.33 | 12.64 | 104.15 | 110 | 0 | 15694 | 80.43 | 114.76 | 219.98 | 213.95 | 219.44 | 0 | 32.66 | 50.05 | 13668 | 91.5 | 42.14 | 37.35 | 1.98 | 42.14 | 0 | 606 | 434.1 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.8 | 312.6 | 0 | 306.4 | 100.66 | 15693 | 15694 | 316
03/26/22 10:38:16.197 | 588.4471 | 1368.4335 | 54.0297 | 43.7391 | 10.2906 | 31.2188 | 50.9526 | 0 | 1788.3017 | 89.5866 | 80.4628 | 9.1237 | 24.7533 | 69.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.011 | 461.46 | 458.43 | 462.36 | 412.36 | 443.02 | 419.74 | 314.92 | 0.53517 | 0.098873 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7088818.526 | 8155302.345 | 8155302.345 | 62.4285 | 62.1834 | 1.0018 | 0.99799 | 684974.7317 | 892528.2299 | 460.75 | 0.50353 | 0 | 0 | 31.2188 | 24.7533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017905 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.8362 | 1367.8896 | 54.0943 | 43.7403 | 31.0229 | 1787.2303 | 79.559 | 24.938 | 460.3657 | 0.0067244 | 59.9994 | 0.53326 | 0.29648 | 88.7157 | 2.3819 | 0.40973 | 0.23022 | 4.8023 | 0.9054 | 0.32546 | 0 | 100 | 579.2 | 317 | 107.33 | 104.17 | 100.73 | 307.7 | 3 | 91.52 | 42.14 | 4 | 37.35 | 43.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.58 | 0 | 38.11 | 60 | 60 | 101.88 | 88.59 | 83.17 | 0 | 100.73 | 2.28 | 90.58 | 42.9 | 107.38 | 12.65 | 104.17 | 110 | 0 | 15694 | 80.43 | 114.76 | 219.98 | 213.95 | 219.44 | 0 | 32.76 | 50.35 | 13673 | 91.52 | 42.14 | 37.35 | 1.82 | 42.14 | 0 | 606 | 427.1 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 313.7 | 0 | 307.4 | 100.73 | 15693 | 15694 | 317
03/26/22 10:38:21.197 | 587.5941 | 1366.6736 | 54.0324 | 43.743 | 10.2894 | 31.3197 | 50.9631 | 0 | 1786.7534 | 89.5938 | 80.472 | 9.1217 | 24.8306 | 69.8461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0131 | 461.5401 | 458.5001 | 462.4101 | 412.5701 | 443.0701 | 419.7401 | 315.0301 | 0.53614 | 0.035241 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7078602.0282 | 8150519.2074 | 8150519.2074 | 62.4285 | 62.1833 | 1.0018 | 0.99799 | 684057.5242 | 892169.0444 | 460.8167 | 0.50273 | 0 | 0 | 31.3197 | 24.8306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017911 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.7528 | 1367.8537 | 54.0893 | 43.7365 | 31.0247 | 1787.1981 | 79.5749 | 24.9365 | 460.3715 | 0.006737 | 59.9992 | 0.5333 | 0.29061 | 88.7312 | 2.3548 | 0.40488 | 0.22439 | 4.7798 | 0.89596 | 0.32359 | 0 | 100 | 580 | 317 | 107.38 | 104.19 | 100.83 | 308.8 | 3 | 91.54 | 42.14 | 4 | 37.35 | 43.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.6 | 0 | 38.13 | 60 | 60 | 101.9 | 88.6 | 83.11 | 0 | 100.83 | 2.28 | 90.59 | 42.91 | 107.38 | 12.66 | 104.19 | 110 | 0 | 15694 | 80.43 | 114.76 | 219.98 | 213.95 | 219.44 | 0 | 33.01 | 50.78 | 13678 | 91.53 | 42.15 | 37.35 | 1.6 | 42.15 | 0 | 606 | 429.4 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 315.1 | 0 | 308.8 | 100.87 | 15694 | 15694 | 317
03/26/22 10:38:26.198 | 587.8545 | 1367.5045 | 54.0339 | 43.7448 | 10.2891 | 31.4354 | 50.9614 | 0 | 1785.489 | 89.5979 | 80.4768 | 9.1211 | 24.5819 | 69.8374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.013 | 461.54 | 458.5 | 462.41 | 412.57 | 443.07 | 419.74 | 315.03 | 0.5359 | 0.19662 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7081849.6701 | 8140754.1455 | 8140754.1455 | 62.4285 | 62.1832 | 1.0018 | 0.99799 | 684382.9638 | 891194.7919 | 460.8167 | 0.50273 | 0 | 0 | 31.4354 | 24.5819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017913 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.6721 | 1367.8365 | 54.0846 | 43.7331 | 31.0267 | 1787.1704 | 79.5905 | 24.9346 | 460.3776 | 0.00675 | 59.9991 | 0.53334 | 0.28591 | 88.7463 | 2.3459 | 0.40045 | 0.21934 | 4.7751 | 0.88686 | 0.32165 | 0 | 100 | 579.7 | 318 | 107.33 | 104.21 | 100.8 | 309.3 | 3 | 91.5 | 42.16 | 4 | 37.38 | 43.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.6 | 0 | 38.14 | 60 | 60 | 101.9 | 88.6 | 83.17 | 0 | 100.8 | 2.28 | 90.59 | 42.92 | 107.33 | 12.7 | 104.21 | 110 | 0 | 15694 | 80.43 | 114.76 | 219.98 | 214.06 | 219.44 | 0 | 33.19 | 50.84 | 13683 | 91.5 | 42.16 | 37.38 | 1.38 | 42.16 | 0 | 606 | 432.2 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 315.6 | 0 | 309.3 | 100.82 | 15695 | 15694 | 318
03/26/22 10:38:31.197 | 588.1242 | 1367.8865 | 54.0379 | 43.7488 | 10.2891 | 31.3881 | 50.9528 | 0 | 1780.5035 | 89.6097 | 80.4891 | 9.1206 | 23.9075 | 69.8143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.012 | 461.6 | 458.52 | 462.47 | 412.66 | 443.25 | 419.72 | 315.13 | 0.53582 | 0.54109 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7085080.4088 | 8115973.3407 | 8115973.3407 | 62.4285 | 62.1831 | 1.0018 | 0.99799 | 684700.526 | 888632.6051 | 460.8634 | 0.50847 | 0 | 0 | 31.3881 | 23.9075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017917 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.603 | 1367.8559 | 54.0801 | 43.73 | 31.0282 | 1787.1488 | 79.6059 | 24.9318 | 460.3839 | 0.0067636 | 59.999 | 0.53337 | 0.28387 | 88.761 | 2.3317 | 0.39645 | 0.21514 | 4.7965 | 0.87817 | 0.31906 | 0 | 100 | 579.3 | 316 | 107.53 | 104.23 | 100.75 | 307.2 | 3 | 91.61 | 42.16 | 4 | 37.38 | 43.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.65 | 0 | 38.15 | 60 | 60 | 101.93 | 88.62 | 83.17 | 0 | 100.75 | 2.28 | 90.62 | 42.94 | 107.53 | 12.62 | 104.23 | 110 | 0 | 15694 | 80.43 | 114.76 | 219.98 | 214.06 | 219.44 | 0 | 33.21 | 50.6 | 13688 | 91.61 | 42.16 | 37.38 | 1.34 | 42.16 | 0 | 606 | 432.9 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.3 | 311.8 | 0 | 305.6 | 100.75 | 15692 | 15694 | 317
03/26/22 10:38:36.197 | 588.2286 | 1368.1703 | 54.0393 | 43.7505 | 10.2888 | 31.4227 | 50.9319 | 0 | 1777.9436 | 89.6153 | 80.4954 | 9.1199 | 23.8977 | 69.8283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 461.6001 | 458.5201 | 462.4701 | 412.6601 | 443.2501 | 419.7201 | 315.1301 | 0.53573 | 0.71294 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7086370.1149 | 8103656.9345 | 8103656.9345 | 62.4285 | 62.183 | 1.0018 | 0.99799 | 684842.5403 | 887354.1287 | 460.8634 | 0.50847 | 0 | 0 | 31.4227 | 23.8977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017923 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.5311 | 1367.8726 | 54.0758 | 43.7271 | 31.0279 | 1787.1005 | 79.6212 | 24.932 | 460.3904 | 0.0067778 | 59.9989 | 0.5334 | 0.28327 | 88.7755 | 2.3231 | 0.39266 | 0.21139 | 4.8453 | 0.86956 | 0.3167 | 0 | 100 | 580.7 | 317 | 107.53 | 104.25 | 100.94 | 308.4 | 3 | 91.6 | 42.16 | 4 | 37.38 | 43.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.7 | 0 | 38.15 | 60 | 60 | 101.98 | 88.64 | 83.13 | 0 | 100.94 | 2.28 | 90.64 | 42.94 | 107.5 | 12.65 | 104.25 | 110 | 0 | 15694 | 80.43 | 114.76 | 219.98 | 214.06 | 219.44 | 0 | 33.01 | 50.17 | 13693 | 91.6 | 42.16 | 37.38 | 1.33 | 42.16 | 0 | 606 | 432.6 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.3 | 315.4 | 0 | 309.2 | 100.92 | 15692 | 15694 | 316
03/26/22 10:38:41.197 | 587.9073 | 1367.5097 | 54.0408 | 43.7527 | 10.2881 | 31.0443 | 50.9399 | 0 | 1780.5086 | 89.6225 | 80.5034 | 9.119 | 24.3916 | 69.8663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.01 | 461.6 | 458.53 | 462.5 | 412.73 | 443.45 | 419.77 | 315.22 | 0.53617 | 0.52012 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7082168.9658 | 8115118.6425 | 8115118.6425 | 62.4285 | 62.183 | 1.0018 | 0.99799 | 684511.7922 | 888633.2055 | 460.8767 | 0.50917 | 0 | 0 | 31.0443 | 24.3916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017933 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.445 | 1367.8771 | 54.0718 | 43.7246 | 31.0267 | 1787.0922 | 79.6362 | 24.9322 | 460.3971 | 0.0067705 | 59.9988 | 0.53344 | 0.28016 | 88.7897 | 2.3216 | 0.38919 | 0.20837 | 4.8553 | 0.86127 | 0.31413 | 0 | 100 | 580.1 | 315 | 107.53 | 104.25 | 100.89 | 306.9 | 3 | 91.61 | 42.16 | 4 | 37.38 | 43.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.73 | 0 | 38.15 | 60 | 60 | 102 | 88.66 | 83.19 | 0 | 100.89 | 2.28 | 90.66 | 42.94 | 107.53 | 12.64 | 104.25 | 110 | 0 | 15694 | 80.43 | 114.74 | 219.98 | 214.06 | 219.44 | 0 | 32.8 | 49.96 | 13698 | 91.61 | 42.16 | 37.38 | 1.27 | 42.16 | 0 | 606 | 429.8 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 312.8 | 0 | 306.5 | 100.87 | 15697 | 15694 | 317
03/26/22 10:38:46.197 | 588.3664 | 1368.6761 | 54.0442 | 43.7565 | 10.2877 | 31.6123 | 50.9544 | 0 | 1778.8313 | 89.636 | 80.5175 | 9.1184 | 24.2954 | 69.9002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.008 | 461.61 | 458.54 | 462.55 | 412.81 | 443.79 | 419.83 | 315.35 | 0.53598 | 0.6912 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7088283.8187 | 8107759.9615 | 8107759.9615 | 62.4285 | 62.1828 | 1.0018 | 0.99799 | 685080.0078 | 887915.3863 | 460.9 | 0.51204 | 0 | 0 | 31.6123 | 24.2954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017936 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.3592 | 1367.891 | 54.0678 | 43.7223 | 31.0295 | 1787.0728 | 79.6511 | 24.9285 | 460.4039 | 0.006785 | 59.9986 | 0.53348 | 0.2786 | 88.8036 | 2.3186 | 0.38583 | 0.20564 | 4.8803 | 0.85302 | 0.31145 | 0 | 100 | 579.8 | 318 | 107.58 | 104.27 | 100.8 | 306 | 3 | 91.63 | 42.18 | 4 | 37.39 | 43.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.75 | 0 | 38.16 | 60 | 60 | 102.03 | 88.67 | 83.15 | 0 | 100.8 | 2.28 | 90.67 | 42.95 | 107.6 | 12.63 | 104.27 | 110 | 0 | 15694 | 80.43 | 114.71 | 219.98 | 214.06 | 219.44 | 0 | 32.75 | 49.97 | 13703 | 91.63 | 42.18 | 37.39 | 1.23 | 42.18 | 0 | 606 | 430.8 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.8 | 312.2 | 0 | 306 | 100.83 | 15693 | 15694 | 318
03/26/22 10:38:51.196 | 588.6158 | 1369.1406 | 54.047 | 43.7587 | 10.2883 | 31.1474 | 50.9788 | 0 | 1782.2788 | 89.645 | 80.5262 | 9.1188 | 25.2491 | 69.8907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.008 | 461.61 | 458.54 | 462.55 | 412.81 | 443.79 | 419.83 | 315.35 | 0.53575 | 0.52656 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7090794.2575 | 8123922.284 | 8123922.284 | 62.4284 | 62.1827 | 1.0018 | 0.99799 | 685327.8844 | 889513.6479 | 460.9 | 0.51204 | 0 | 0 | 31.1474 | 25.2491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017927 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.2725 | 1367.9092 | 54.064 | 43.7201 | 31.0348 | 1787.0482 | 79.666 | 24.9237 | 460.4107 | 0.0067781 | 59.9985 | 0.53353 | 0.27779 | 88.8175 | 2.3155 | 0.38252 | 0.20312 | 4.8933 | 0.84471 | 0.30874 | 0 | 100 | 580.4 | 315 | 107.53 | 104.29 | 100.85 | 306.6 | 3 | 91.61 | 42.19 | 4 | 37.4 | 43.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.75 | 0 | 38.16 | 60 | 60 | 102.05 | 88.67 | 83.17 | 0 | 100.85 | 2.28 | 90.67 | 42.95 | 107.55 | 12.68 | 104.29 | 110 | 0 | 15694 | 80.43 | 114.71 | 219.98 | 214.06 | 219.44 | 0 | 32.67 | 49.92 | 13708 | 91.61 | 42.19 | 37.4 | 1.22 | 42.19 | 0 | 606 | 427.2 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.4 | 312.9 | 0 | 306.6 | 100.94 | 15693 | 15694 | 315
03/26/22 10:38:56.197 | 587.7823 | 1367.0607 | 54.0516 | 43.7623 | 10.2893 | 30.9184 | 50.9579 | 0 | 1790.1081 | 89.6607 | 80.5406 | 9.1201 | 25.5197 | 69.8729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0081 | 461.6101 | 458.5401 | 462.5701 | 412.8401 | 443.9601 | 419.8701 | 315.4201 | 0.53663 | -0.052179 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7080549.1221 | 8161063.6442 | 8161063.6442 | 62.4284 | 62.1826 | 1.0018 | 0.99799 | 684286.58 | 893419.1422 | 460.9067 | 0.51348 | 0 | 0 | 30.9184 | 25.5197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016243 | 0.01792 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.1753 | 1367.9142 | 54.0603 | 43.7182 | 31.0343 | 1787.0132 | 79.6807 | 24.9273 | 460.4175 | 0.0067928 | 59.9983 | 0.53358 | 0.27705 | 88.8311 | 2.3183 | 0.37935 | 0.20101 | 4.8796 | 0.83657 | 0.306 | 0 | 100 | 579.8 | 317 | 107.6 | 104.29 | 100.83 | 308.9 | 3 | 91.65 | 42.18 | 4 | 37.39 | 43.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.73 | 0 | 38.16 | 60 | 60 | 102.03 | 88.67 | 83.21 | 0 | 100.83 | 2.28 | 90.66 | 42.95 | 107.6 | 12.64 | 104.29 | 110 | 0 | 15694 | 80.43 | 114.71 | 219.98 | 214.06 | 219.44 | 0 | 32.59 | 49.96 | 13713 | 91.65 | 42.18 | 37.39 | 1.21 | 42.18 | 0 | 606 | 432.9 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 316.2 | 0 | 309.9 | 100.82 | 15696 | 15694 | 318
03/26/22 10:39:01.196 | 587.1791 | 1365.5692 | 54.0542 | 43.7642 | 10.29 | 31.5063 | 50.9519 | 0 | 1789.7365 | 89.669 | 80.5478 | 9.1212 | 24.7349 | 69.8618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 461.6 | 458.54 | 462.57 | 412.79 | 444.02 | 419.87 | 315.42 | 0.53718 | -0.11491 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7073796.2286 | 8159424.0773 | 8159424.0773 | 62.4284 | 62.1825 | 1.0018 | 0.99799 | 683539.8613 | 893232.7023 | 460.9034 | 0.51276 | 0 | 0 | 31.5063 | 24.7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016242 | 0.017923 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 591.0648 | 1367.8978 | 54.0566 | 43.7163 | 31.0376 | 1787.0095 | 79.6954 | 24.9259 | 460.4244 | 0.0067424 | 59.9982 | 0.53364 | 0.27307 | 88.8446 | 2.3225 | 0.37618 | 0.19906 | 4.8774 | 0.82835 | 0.30308 | 0 | 100 | 579.5 | 316 | 107.6 | 104.29 | 100.78 | 306.9 | 3 | 91.65 | 42.18 | 4 | 37.39 | 43.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.7 | 0 | 38.16 | 60 | 60 | 101.98 | 88.66 | 83.19 | 0 | 100.82 | 2.28 | 90.64 | 42.95 | 107.6 | 12.64 | 104.29 | 110 | 0 | 15694 | 80.46 | 114.71 | 220.1 | 214.06 | 219.44 | 0 | 32.68 | 50.18 | 13718 | 91.65 | 42.18 | 37.39 | 1.19 | 42.18 | 0 | 606 | 429.1 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.5 | 313.1 | 0 | 306.9 | 100.78 | 15693 | 15694 | 316
03/26/22 10:39:06.197 | 588.7641 | 1369.058 | 54.0585 | 43.767 | 10.2915 | 31.6622 | 50.9635 | 0 | 1786.3095 | 89.68 | 80.5575 | 9.1225 | 24.3738 | 69.8857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 461.6001 | 458.5301 | 462.5601 | 412.8601 | 444.0801 | 419.9101 | 315.4601 | 0.5358 | 0.30337 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7093024.6295 | 8144536.5813 | 8144536.5813 | 62.4284 | 62.1824 | 1.0018 | 0.99799 | 685286.0094 | 891521.0527 | 460.8967 | 0.51349 | 0 | 0 | 31.6622 | 24.3738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017926 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 590.9646 | 1367.921 | 54.053 | 43.7147 | 31.0444 | 1786.9882 | 79.7099 | 24.919 | 460.4311 | 0.0067135 | 59.998 | 0.5337 | 0.27265 | 88.858 | 2.3063 | 0.37306 | 0.19741 | 4.8698 | 0.82026 | 0.30014 | 0 | 100 | 580 | 316 | 107.65 | 104.29 | 100.87 | 308.9 | 3 | 91.66 | 42.2 | 4 | 37.41 | 43.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.78 | 0 | 38.19 | 60 | 60 | 102.05 | 88.68 | 83.15 | 0 | 100.94 | 2.28 | 90.68 | 42.97 | 107.65 | 12.63 | 104.29 | 110 | 0 | 15694 | 80.46 | 114.71 | 220.1 | 214.06 | 219.44 | 0 | 32.68 | 50.16 | 13723 | 91.67 | 42.2 | 37.41 | 1.24 | 42.2 | 0 | 606 | 428.8 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.9 | 315.1 | 0 | 308.8 | 100.85 | 15695 | 15694 | 317
03/26/22 10:39:11.196 | 589.6773 | 1371.2617 | 54.0628 | 43.7698 | 10.293 | 31.4948 | 50.974 | 0 | 1784.3794 | 89.6905 | 80.5672 | 9.1232 | 24.1266 | 69.9105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 461.6001 | 458.5301 | 462.5601 | 412.8601 | 444.0801 | 419.9101 | 315.4601 | 0.53497 | 0.53022 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7103873.0207 | 8137008.3601 | 8137008.3601 | 62.4284 | 62.1823 | 1.0018 | 0.99799 | 686264.9577 | 890649.4087 | 460.8967 | 0.51349 | 0 | 0 | 31.4948 | 24.1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017932 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 590.8661 | 1367.959 | 54.0495 | 43.7132 | 31.05 | 1786.9527 | 79.7244 | 24.9106 | 460.4378 | 0.0066628 | 59.9979 | 0.53375 | 0.27383 | 88.8712 | 2.3047 | 0.36993 | 0.19594 | 4.8654 | 0.81215 | 0.29705 | 0 | 100 | 579.7 | 314 | 107.63 | 104.31 | 100.82 | 306.1 | 3 | 91.66 | 42.21 | 4 | 37.43 | 43.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.8 | 0 | 38.19 | 60 | 60 | 102.13 | 88.72 | 83.21 | 0 | 100.85 | 2.28 | 90.7 | 42.97 | 107.63 | 12.65 | 104.31 | 110 | 0 | 15694 | 80.46 | 114.74 | 220.1 | 214.06 | 219.44 | 0 | 32.75 | 50.4 | 13728 | 91.66 | 42.21 | 37.43 | 1.35 | 42.21 | 0 | 606 | 427.6 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.5 | 314.7 | 0 | 308.4 | 100.78 | 15693 | 15694 | 317
03/26/22 10:39:16.197 | 588.2525 | 1367.5613 | 54.0684 | 43.7745 | 10.2939 | 31.086 | 50.9755 | 0 | 1783.4091 | 89.7062 | 80.5833 | 9.1229 | 25.1089 | 69.9196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0091 | 461.6201 | 458.5401 | 462.5301 | 412.9001 | 443.9201 | 419.9001 | 315.4301 | 0.53622 | 0.37031 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7086348.8545 | 8132468.8328 | 8132468.8328 | 62.4284 | 62.1821 | 1.0018 | 0.99799 | 684536.4135 | 890069.966 | 460.8968 | 0.51132 | 0 | 0 | 31.086 | 25.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017935 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 590.7574 | 1367.9795 | 54.046 | 43.7118 | 31.0536 | 1786.9062 | 79.7389 | 24.9053 | 460.4443 | 0.0065898 | 59.9978 | 0.53382 | 0.27467 | 88.8843 | 2.3107 | 0.36678 | 0.19457 | 4.8624 | 0.80393 | 0.29397 | 0 | 100 | 579.9 | 316 | 107.63 | 104.33 | 100.85 | 307.8 | 3 | 91.66 | 42.2 | 4 | 37.41 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.85 | 0 | 38.19 | 60 | 60 | 102.1 | 88.71 | 83.24 | 0 | 100.85 | 2.28 | 90.71 | 42.97 | 107.63 | 12.67 | 104.33 | 110 | 0 | 15694 | 80.46 | 114.74 | 220.1 | 214.06 | 219.44 | 0 | 32.89 | 50.54 | 13733 | 91.66 | 42.2 | 37.41 | 1.42 | 42.2 | 0 | 606 | 430.2 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.9 | 314 | 0 | 307.8 | 100.85 | 15693 | 15694 | 316
03/26/22 10:39:21.196 | 588.6293 | 1368.4851 | 54.0709 | 43.7774 | 10.2935 | 31.2148 | 50.9835 | 0 | 1785.7728 | 89.7135 | 80.5915 | 9.122 | 25.0475 | 69.9221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.009 | 461.62 | 458.54 | 462.53 | 412.9 | 443.92 | 419.9 | 315.43 | 0.53587 | 0.30551 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7091001.375 | 8142378.7861 | 8142378.7861 | 62.4284 | 62.182 | 1.0018 | 0.99799 | 684998.7203 | 891248.5405 | 460.8967 | 0.51132 | 0 | 0 | 31.2148 | 25.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017931 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 590.639 | 1367.9874 | 54.0426 | 43.7105 | 31.0544 | 1786.8825 | 79.7533 | 24.9069 | 460.4508 | 0.0065605 | 59.9977 | 0.53389 | 0.27336 | 88.8973 | 2.31 | 0.36358 | 0.1933 | 4.8574 | 0.79567 | 0.29107 | 0 | 100 | 580.2 | 316 | 107.58 | 104.33 | 100.9 | 308.4 | 3 | 91.63 | 42.21 | 4 | 37.43 | 43.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.85 | 0 | 38.19 | 60 | 60 | 102.13 | 88.72 | 83.24 | 0 | 100.9 | 2.28 | 90.72 | 42.97 | 107.58 | 12.69 | 104.33 | 110 | 0 | 15694 | 80.46 | 114.74 | 220.1 | 214.06 | 219.44 | 0 | 32.92 | 50.48 | 13738 | 91.63 | 42.23 | 37.44 | 1.49 | 42.23 | 0 | 606 | 433.5 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.8 | 313.6 | 0 | 307.4 | 101.01 | 15693 | 15694 | 315
03/26/22 10:39:26.196 | 589.3909 | 1370.2966 | 54.0746 | 43.7814 | 10.2932 | 30.7404 | 50.9806 | 0 | 1786.645 | 89.7232 | 80.6024 | 9.1208 | 25.295 | 69.9588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0091 | 461.6401 | 458.5401 | 462.4901 | 413.0801 | 443.9201 | 419.9901 | 315.4901 | 0.53528 | 0.3738 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7099759.7834 | 8145545.8022 | 8145545.8022 | 62.4284 | 62.1819 | 1.0018 | 0.99799 | 685905.3086 | 891682.3596 | 460.8901 | 0.50988 | 0 | 0 | 30.7404 | 25.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017928 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 590.5326 | 1368.0278 | 54.0391 | 43.7092 | 31.0527 | 1786.8693 | 79.7677 | 24.9106 | 460.4571 | 0.006574 | 59.9976 | 0.53395 | 0.27359 | 88.9103 | 2.2861 | 0.36035 | 0.19212 | 4.8548 | 0.78738 | 0.28813 | 0 | 100 | 580.9 | 318 | 107.68 | 104.33 | 101.03 | 309.4 | 3 | 91.69 | 42.24 | 4 | 37.45 | 43.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.85 | 0 | 38.21 | 60 | 60 | 102.15 | 88.74 | 83.19 | 0 | 101.03 | 2.28 | 90.72 | 43 | 107.7 | 12.63 | 104.33 | 110 | 0 | 15694 | 80.46 | 114.76 | 220.1 | 214.06 | 219.44 | 0 | 32.82 | 50.34 | 13743 | 91.7 | 42.24 | 37.45 | 1.46 | 42.24 | 0 | 606 | 431.9 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.6 | 312.7 | 0 | 306.4 | 100.97 | 15692 | 15694 | 315
03/26/22 10:39:31.197 | 588.6812 | 1368.5935 | 54.0809 | 43.7873 | 10.2936 | 31.4806 | 51.012 | 0 | 1789.5352 | 89.7366 | 80.6177 | 9.1189 | 24.0244 | 69.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0061 | 461.6701 | 458.5401 | 462.4601 | 413.2401 | 443.7401 | 419.9901 | 315.5001 | 0.53594 | 0.15652 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7091861.0676 | 8155582.7102 | 8155582.7102 | 62.4284 | 62.1818 | 1.0018 | 0.99799 | 685052.5236 | 893122.6956 | 460.8901 | 0.50988 | 0 | 0 | 31.4806 | 24.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017924 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 590.4237 | 1368.0642 | 54.0358 | 43.7081 | 31.0543 | 1786.8893 | 79.7821 | 24.9072 | 460.4635 | 0.0065226 | 59.9975 | 0.53402 | 0.27226 | 88.9232 | 2.2419 | 0.35707 | 0.191 | 4.8584 | 0.77898 | 0.28501 | 0 | 100 | 580.6 | 316 | 107.7 | 104.35 | 100.99 | 308.6 | 3 | 91.7 | 42.24 | 4 | 37.45 | 43.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.88 | 0 | 38.21 | 60 | 60 | 102.17 | 88.75 | 83.21 | 0 | 100.92 | 2.28 | 90.72 | 43 | 107.7 | 12.65 | 104.35 | 110 | 0 | 15694 | 80.48 | 114.76 | 220.1 | 214.06 | 219.44 | 0 | 32.81 | 50.34 | 13748 | 91.7 | 42.24 | 37.45 | 1.44 | 42.24 | 0 | 606 | 433.8 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.6 | 314.8 | 0 | 308.6 | 100.97 | 15693 | 15694 | 316
03/26/22 10:39:36.196 | 589.3181 | 1370.0386 | 54.0846 | 43.7907 | 10.2939 | 31.3778 | 50.9763 | 0 | 1788.4617 | 89.7438 | 80.6259 | 9.1179 | 24.5687 | 69.9473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 461.67 | 458.54 | 462.46 | 413.24 | 443.74 | 419.99 | 315.5 | 0.53536 | 0.31284 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7099442.5904 | 8150435.0454 | 8150435.0454 | 62.4283 | 62.1817 | 1.0018 | 0.99799 | 685775.6973 | 892585.8254 | 460.89 | 0.50988 | 0 | 0 | 31.3778 | 24.5687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017927 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 590.3134 | 1368.1029 | 54.0324 | 43.7069 | 31.0587 | 1786.9275 | 79.7965 | 24.9011 | 460.4696 | 0.0064491 | 59.9973 | 0.53408 | 0.26977 | 88.9361 | 2.2152 | 0.35373 | 0.18992 | 4.8434 | 0.77048 | 0.28209 | 0 | 100 | 580.1 | 316 | 107.73 | 104.35 | 100.89 | 308.2 | 3 | 91.71 | 42.25 | 4 | 37.46 | 43.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.88 | 0 | 38.23 | 60 | 60 | 102.17 | 88.75 | 83.28 | 0 | 100.97 | 2.28 | 90.74 | 43.01 | 107.73 | 12.63 | 104.35 | 110 | 0 | 15694 | 80.48 | 114.76 | 220.1 | 214.06 | 219.44 | 0 | 32.82 | 50.38 | 13753 | 91.71 | 42.25 | 37.46 | 1.45 | 42.25 | 0 | 606 | 430.6 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 314.5 | 0 | 308.2 | 100.89 | 15694 | 15694 | 316
03/26/22 10:39:41.196 | 589.6309 | 1370.6115 | 54.0889 | 43.7949 | 10.294 | 30.8957 | 50.9808 | 0 | 1789.0759 | 89.7515 | 80.635 | 9.1165 | 25.1871 | 69.9369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.005 | 461.71 | 458.57 | 462.47 | 413.36 | 443.77 | 420.07 | 315.58 | 0.53522 | 0.36843 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7102811.0932 | 8149533.7108 | 8149533.7108 | 62.4283 | 62.1816 | 1.0018 | 0.99799 | 686132.0445 | 892533.2962 | 460.9167 | 0.50913 | 0 | 0 | 30.8957 | 25.1871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017915 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 590.1951 | 1368.128 | 54.0291 | 43.7059 | 31.0618 | 1786.9516 | 79.8108 | 24.8953 | 460.4759 | 0.0063973 | 59.9972 | 0.53416 | 0.26769 | 88.9488 | 2.2179 | 0.35031 | 0.18888 | 4.8432 | 0.76195 | 0.27942 | 0 | 100 | 580.7 | 317 | 107.63 | 104.35 | 100.99 | 308.5 | 3 | 91.66 | 42.26 | 4 | 37.48 | 43.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.88 | 0 | 38.23 | 60 | 60 | 102.15 | 88.74 | 83.26 | 0 | 101.04 | 2.28 | 90.74 | 43.01 | 107.63 | 12.68 | 104.35 | 110 | 0 | 15694 | 80.48 | 114.76 | 220.1 | 214.06 | 219.44 | 0 | 32.83 | 50.33 | 13758 | 91.66 | 42.25 | 37.46 | 1.45 | 42.25 | 0 | 607 | 432 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 315.2 | 0 | 308.9 | 100.89 | 15695 | 15694 | 317
03/26/22 10:39:46.196 | 589.8966 | 1371.2205 | 54.0986 | 43.8035 | 10.2952 | 29.9389 | 50.9928 | 0 | 1794.8355 | 89.7645 | 80.6503 | 9.1142 | 26.4283 | 69.9766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0001 | 461.8101 | 458.6301 | 462.5201 | 413.5201 | 443.7601 | 420.0401 | 315.6601 | 0.53511 | 0.046696 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7105139.5713 | 8178259.6284 | 8178259.6284 | 62.4283 | 62.1815 | 1.0018 | 0.99799 | 686366.6528 | 895763.5267 | 460.9867 | 0.51122 | 0 | 0 | 29.9389 | 26.4283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017911 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 590.068 | 1368.136 | 54.0258 | 43.7049 | 31.0565 | 1786.9838 | 79.825 | 24.9022 | 460.4822 | 0.0063458 | 59.9971 | 0.53424 | 0.26398 | 88.9615 | 2.2238 | 0.34683 | 0.18788 | 4.869 | 0.75331 | 0.277 | 0 | 100 | 580.5 | 316 | 107.65 | 104.35 | 101.13 | 307.9 | 3 | 91.67 | 42.28 | 4 | 37.49 | 43.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.83 | 0 | 38.25 | 60 | 60 | 102.13 | 88.72 | 83.21 | 0 | 101.13 | 2.28 | 90.71 | 43.04 | 107.65 | 12.67 | 104.35 | 110 | 0 | 15694 | 80.5 | 114.76 | 220.1 | 214.06 | 219.56 | 0 | 32.74 | 50.3 | 13763 | 91.67 | 42.28 | 37.49 | 1.43 | 42.28 | 0 | 606 | 429.7 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.5 | 314.1 | 0 | 307.9 | 100.96 | 15694 | 15694 | 316
03/26/22 10:39:51.195 | 590.0894 | 1371.5146 | 54.104 | 43.8077 | 10.2963 | 30.1112 | 50.9949 | 0 | 1793.9994 | 89.7703 | 80.6566 | 9.1136 | 26.1921 | 69.9889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0001 | 461.8101 | 458.6301 | 462.5201 | 413.5201 | 443.7601 | 420.0401 | 315.6601 | 0.53494 | 0.13506 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7107611.3287 | 8173640.6866 | 8173640.6866 | 62.4283 | 62.1814 | 1.0018 | 0.99799 | 686513.6607 | 895345.3849 | 460.9868 | 0.51122 | 0 | 0 | 30.1112 | 26.1921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017907 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 589.928 | 1368.1173 | 54.0225 | 43.7039 | 31.0505 | 1787.0227 | 79.8392 | 24.9104 | 460.4887 | 0.0063165 | 59.9969 | 0.53433 | 0.25812 | 88.9742 | 2.1805 | 0.34327 | 0.1869 | 4.897 | 0.74462 | 0.27501 | 0 | 100 | 580.3 | 317 | 107.63 | 104.33 | 100.92 | 308 | 3 | 91.66 | 42.28 | 4 | 37.49 | 43.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.8 | 0 | 38.25 | 60 | 60 | 102.13 | 88.72 | 83.21 | 0 | 100.92 | 2.28 | 90.7 | 43.04 | 107.6 | 12.67 | 104.33 | 110 | 0 | 15694 | 80.5 | 114.76 | 220.1 | 214.06 | 219.56 | 0 | 32.8 | 50.38 | 13767 | 91.66 | 42.28 | 37.49 | 1.55 | 42.28 | 0 | 607 | 433 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.5 | 314.7 | 0 | 308.4 | 100.96 | 15692 | 15694 | 317
03/26/22 10:39:56.196 | 589.2394 | 1369.3625 | 54.1153 | 43.8167 | 10.2986 | 30.6156 | 50.9951 | 0 | 1793.7466 | 89.7809 | 80.6677 | 9.1132 | 25.3522 | 69.9799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 461.85 | 458.65 | 462.53 | 413.61 | 443.77 | 420.01 | 315.7 | 0.53578 | 0.03706 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7097759.365 | 8171943.0393 | 8171943.0393 | 62.4283 | 62.1813 | 1.0018 | 0.99799 | 685389.464 | 895297.6509 | 461.01 | 0.51192 | 0 | 0 | 30.6156 | 25.3522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017903 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 589.7848 | 1368.0915 | 54.0193 | 43.703 | 31.0505 | 1787.069 | 79.8534 | 24.9092 | 460.4953 | 0.0063307 | 59.9967 | 0.53443 | 0.25185 | 88.9867 | 2.1387 | 0.33963 | 0.18593 | 4.9225 | 0.73581 | 0.27319 | 0 | 100 | 580.6 | 316 | 107.65 | 104.31 | 100.94 | 306.1 | 3 | 91.67 | 42.26 | 4 | 37.48 | 43.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.8 | 0 | 38.25 | 60 | 60 | 102.1 | 88.71 | 83.19 | 0 | 100.94 | 2.28 | 90.7 | 43.04 | 107.68 | 12.62 | 104.31 | 110 | 0 | 15694 | 80.5 | 114.76 | 220.1 | 214.06 | 219.56 | 0 | 32.79 | 50.34 | 13773 | 91.69 | 42.26 | 37.48 | 1.7 | 42.26 | 0 | 606 | 430.5 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.9 | 315.9 | 0 | 309.6 | 100.85 | 15693 | 15694 | 316
03/26/22 10:40:01.196 | 588.9749 | 1368.418 | 54.1251 | 43.8249 | 10.3002 | 30.5868 | 50.9998 | 0 | 1791.7906 | 89.7884 | 80.6746 | 9.1138 | 25.6829 | 69.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 461.89 | 458.67 | 462.57 | 413.69 | 443.81 | 419.96 | 315.75 | 0.5361 | 0.10644 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7094595.5593 | 8163114.3609 | 8163114.3609 | 62.4282 | 62.1812 | 1.0018 | 0.99799 | 684962.7103 | 894240.5174 | 461.0434 | 0.51477 | 0 | 0 | 30.5868 | 25.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017907 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 589.6485 | 1368.0794 | 54.0161 | 43.7021 | 31.0533 | 1787.1023 | 79.8676 | 24.9047 | 460.5019 | 0.0062364 | 59.9966 | 0.53452 | 0.24753 | 88.9993 | 2.129 | 0.33592 | 0.18498 | 4.9436 | 0.72678 | 0.2712 | 0 | 100 | 580.9 | 315 | 107.63 | 104.31 | 101.03 | 308.8 | 3 | 91.66 | 42.28 | 4 | 37.49 | 44.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.83 | 0 | 38.25 | 60 | 60 | 102.1 | 88.71 | 83.19 | 0 | 101.03 | 2.28 | 90.71 | 43.04 | 107.65 | 12.67 | 104.33 | 110 | 0 | 15694 | 80.52 | 114.76 | 220.1 | 214.17 | 219.56 | 0 | 32.82 | 50.47 | 13778 | 91.66 | 42.28 | 37.49 | 1.76 | 42.28 | 0 | 606 | 433.4 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.8 | 313.5 | 0 | 307.2 | 101.01 | 15693 | 15694 | 315
03/26/22 10:40:06.196 | 589.3012 | 1370.6218 | 54.1368 | 43.8343 | 10.3025 | 31.3415 | 51.0019 | 0 | 1788.5133 | 89.7951 | 80.6796 | 9.1155 | 24.7645 | 70.0046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9941 | 461.9001 | 458.6701 | 462.5701 | 413.7201 | 443.8201 | 419.9401 | 315.7601 | 0.53582 | 0.226 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7098859.9957 | 8157786.1063 | 8157786.1063 | 62.4282 | 62.1812 | 1.0018 | 0.99799 | 685223.219 | 893608.8558 | 461.0467 | 0.51549 | 0 | 0 | 31.3415 | 24.7645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016215 | 0.01791 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 589.5151 | 1368.0746 | 54.013 | 43.7013 | 31.056 | 1787.1084 | 79.8817 | 24.9009 | 460.5085 | 0.0062507 | 59.9964 | 0.53461 | 0.24535 | 89.0117 | 2.1261 | 0.33211 | 0.18404 | 4.9471 | 0.71773 | 0.2698 | 0 | 100 | 581 | 317 | 107.58 | 104.33 | 101.04 | 310.4 | 3 | 91.63 | 42.28 | 4 | 37.49 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.83 | 0 | 38.25 | 60 | 60 | 102.1 | 88.71 | 83.19 | 0 | 101.04 | 2.28 | 90.71 | 43.04 | 107.6 | 12.68 | 104.33 | 110 | 0 | 15694 | 80.52 | 114.79 | 220.1 | 214.17 | 219.56 | 0 | 32.91 | 50.63 | 13782 | 91.65 | 42.28 | 37.49 | 1.66 | 42.28 | 0 | 606 | 430.3 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.3 | 315.3 | 0 | 309 | 101.1 | 15693 | 15694 | 315
03/26/22 10:40:11.196 | 590.3479 | 1371.1998 | 54.1404 | 43.8371 | 10.3033 | 30.9357 | 51.0025 | 0 | 1789.0036 | 89.7968 | 80.6803 | 9.1165 | 24.9662 | 70.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9941 | 461.9001 | 458.6701 | 462.5701 | 413.7201 | 443.8201 | 419.9401 | 315.7601 | 0.53487 | 0.4513 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7111433.6694 | 8151978.5174 | 8151978.5174 | 62.4282 | 62.1812 | 1.0018 | 0.99799 | 686354.4425 | 892848.8291 | 461.0467 | 0.51549 | 0 | 0 | 30.9357 | 24.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.01791 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 589.3825 | 1368.0717 | 54.0098 | 43.7004 | 31.0624 | 1787.1147 | 79.8957 | 24.8913 | 460.5151 | 0.006265 | 59.9962 | 0.5347 | 0.2435 | 89.0241 | 2.1214 | 0.32822 | 0.18309 | 4.9488 | 0.70844 | 0.26832 | 0 | 100 | 580.7 | 318 | 107.63 | 104.35 | 100.99 | 309.2 | 3 | 91.66 | 42.28 | 4 | 37.49 | 43.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.85 | 0 | 38.26 | 60 | 60 | 102.13 | 88.72 | 83.17 | 0 | 100.99 | 2.28 | 90.72 | 43.05 | 107.6 | 12.7 | 104.35 | 110 | 0 | 15693 | 80.52 | 114.79 | 220.1 | 214.17 | 219.56 | 0 | 33.07 | 50.73 | 13787 | 91.65 | 42.29 | 37.5 | 1.53 | 42.29 | 0 | 606 | 433.7 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.5 | 314.9 | 0 | 308.6 | 100.96 | 15694 | 15693 | 317
03/26/22 10:40:16.195 | 589.4633 | 1368.9909 | 54.1476 | 43.8431 | 10.3045 | 30.8202 | 51.0151 | 0 | 1786.7534 | 89.7998 | 80.6809 | 9.1188 | 25.277 | 70.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.993 | 461.91 | 458.68 | 462.57 | 413.72 | 443.81 | 419.93 | 315.75 | 0.53566 | 0.41586 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7100673.3067 | 8144152.0518 | 8144152.0518 | 62.4282 | 62.1811 | 1.0018 | 0.99799 | 685248.4573 | 891725.7348 | 461.0533 | 0.51476 | 0 | 0 | 30.8202 | 25.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017894 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 589.2489 | 1368.0654 | 54.0067 | 43.6996 | 31.0658 | 1787.0859 | 79.9096 | 24.8856 | 460.5219 | 0.0062795 | 59.996 | 0.5348 | 0.24342 | 89.0364 | 2.1169 | 0.32421 | 0.18213 | 4.9357 | 0.69895 | 0.2665 | 0 | 100 | 580.6 | 315 | 107.63 | 104.36 | 100.97 | 308.7 | 3 | 91.66 | 42.28 | 4 | 37.49 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.85 | 0 | 38.24 | 60 | 60 | 102.2 | 88.77 | 83.17 | 0 | 100.97 | 2.28 | 90.72 | 43.04 | 107.63 | 12.69 | 104.36 | 110 | 0 | 15693 | 80.52 | 114.79 | 220.22 | 214.17 | 219.56 | 0 | 33 | 50.49 | 13792 | 91.67 | 42.28 | 37.49 | 1.62 | 42.28 | 0 | 606 | 428.5 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 315.7 | 0 | 309.4 | 100.89 | 15689 | 15693 | 317
03/26/22 10:40:21.195 | 587.6867 | 1365.4659 | 54.1577 | 43.8533 | 10.3045 | 31.4765 | 51.0021 | 0 | 1789.8965 | 89.8032 | 80.6803 | 9.1229 | 24.3993 | 70.0203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 461.9 | 458.67 | 462.54 | 413.76 | 443.73 | 419.94 | 315.74 | 0.53726 | -0.11228 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7079951.6434 | 8166465.6202 | 8166465.6202 | 62.4282 | 62.1811 | 1.0018 | 0.99799 | 683181.3879 | 893958.9587 | 461.0367 | 0.51334 | 0 | 0 | 31.4765 | 24.3993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017906 | 0.0119 | 0.00479 | 0.011584 | 0.0119 | 589.1053 | 1368.0388 | 54.0037 | 43.6988 | 31.0716 | 1787.0721 | 79.9235 | 24.8787 | 460.5285 | 0.0062722 | 59.9958 | 0.5349 | 0.24107 | 89.0486 | 2.1269 | 0.3201 | 0.18116 | 4.9206 | 0.68923 | 0.26435 | 0 | 100 | 580.5 | 317 | 107.65 | 104.36 | 100.96 | 308.6 | 3 | 91.67 | 42.26 | 4 | 37.48 | 44.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.9 | 0 | 38.25 | 60 | 60 | 102.2 | 88.77 | 83.17 | 0 | 100.96 | 2.28 | 90.75 | 43.04 | 107.7 | 12.68 | 104.36 | 110 | 0 | 15693 | 80.54 | 114.76 | 220.22 | 214.17 | 219.56 | 0 | 32.85 | 50.17 | 13798 | 91.7 | 42.26 | 37.48 | 1.81 | 42.26 | 0 | 606 | 433.1 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.6 | 316.7 | 0 | 310.4 | 100.97 | 15695 | 15693 | 318
03/26/22 10:40:26.196 | 588.9549 | 1367.8039 | 54.1636 | 43.8591 | 10.3046 | 30.7831 | 50.9852 | 0 | 1782.542 | 89.8048 | 80.6795 | 9.1253 | 25.2328 | 70.0047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 461.9 | 458.67 | 462.54 | 413.76 | 443.73 | 419.94 | 315.74 | 0.5361 | 0.50581 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7094515.3794 | 8130634.8554 | 8130634.8554 | 62.4281 | 62.1811 | 1.0018 | 0.99799 | 684653.5592 | 889624.1329 | 461.0367 | 0.51334 | 0 | 0 | 30.7831 | 25.2328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017914 | 0.011584 | 0.00479 | 0.011584 | 0.0119 | 588.9756 | 1368.0408 | 54.0006 | 43.6981 | 31.0747 | 1787.0346 | 79.9372 | 24.8768 | 460.5351 | 0.0062863 | 59.9957 | 0.53499 | 0.2421 | 89.0607 | 2.1265 | 0.31583 | 0.18015 | 4.9292 | 0.67936 | 0.26226 | 0 | 100 | 580.3 | 317 | 107.73 | 104.35 | 100.92 | 310.1 | 3 | 91.71 | 42.29 | 4 | 37.5 | 44.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.93 | 0 | 38.26 | 60 | 60 | 102.25 | 88.79 | 83.21 | 0 | 100.92 | 2.28 | 90.76 | 43.05 | 107.73 | 12.63 | 104.35 | 110 | 0 | 15693 | 80.56 | 114.76 | 220.22 | 214.17 | 219.56 | 0 | 32.69 | 50.16 | 13803 | 91.71 | 42.29 | 37.5 | 1.89 | 42.29 | 0 | 606 | 429.9 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.8 | 315.9 | 0 | 309.6 | 101.01 | 15691 | 15693 | 315
03/26/22 10:40:31.195 | 589.6507 | 1369.3419 | 54.1705 | 43.8653 | 10.3052 | 31.4563 | 50.9934 | 0 | 1782.4492 | 89.8065 | 80.6788 | 9.1277 | 23.9449 | 70.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.999 | 461.88 | 458.66 | 462.48 | 413.86 | 443.74 | 420.09 | 315.8 | 0.53557 | 0.61218 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7103488.2548 | 8130908.8781 | 8130908.8781 | 62.4281 | 62.1811 | 1.0018 | 0.99799 | 685423.104 | 889577.874 | 461.0067 | 0.50903 | 0 | 0 | 31.4563 | 23.9449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017914 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 588.85 | 1368.0518 | 53.9975 | 43.6973 | 31.0815 | 1786.9841 | 79.9509 | 24.8658 | 460.5416 | 0.0061483 | 59.9955 | 0.53508 | 0.24475 | 89.0727 | 2.1226 | 0.31141 | 0.17909 | 4.9427 | 0.66918 | 0.26 | 0 | 100 | 581 | 315 | 107.8 | 104.35 | 101.04 | 309.2 | 3 | 91.75 | 42.3 | 4 | 37.51 | 44.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.95 | 0 | 38.26 | 60 | 60 | 102.25 | 88.79 | 83.24 | 0 | 101.01 | 2.28 | 90.78 | 43.05 | 107.78 | 12.61 | 104.35 | 110 | 0 | 15693 | 80.56 | 114.76 | 220.22 | 214.17 | 219.56 | 0 | 32.74 | 50.18 | 13808 | 91.74 | 42.3 | 37.51 | 1.99 | 42.3 | 0 | 606 | 434.6 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.6 | 314.2 | 0 | 308 | 100.97 | 15692 | 15693 | 316
03/26/22 10:40:36.196 | 590.0749 | 1370.2915 | 54.1744 | 43.8689 | 10.3055 | 31.7005 | 51.0037 | 0 | 1782.4904 | 89.8077 | 80.6786 | 9.1291 | 23.7147 | 70.0591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.998 | 461.88 | 458.66 | 462.46 | 413.85 | 443.71 | 420.07 | 315.78 | 0.53515 | 0.66558 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7108813.2599 | 8132061.2202 | 8132061.2202 | 62.4281 | 62.1811 | 1.0018 | 0.99799 | 685898.2487 | 889598.4832 | 461 | 0.50759 | 0 | 0 | 31.7005 | 23.7147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017917 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 588.7286 | 1368.0721 | 53.9944 | 43.6965 | 31.0881 | 1786.924 | 79.9646 | 24.8555 | 460.5477 | 0.0061179 | 59.9953 | 0.53517 | 0.24872 | 89.0847 | 2.1317 | 0.30684 | 0.17799 | 4.9317 | 0.65866 | 0.25809 | 0 | 100 | 581 | 317 | 107.78 | 104.36 | 101.04 | 307.4 | 3 | 91.74 | 42.3 | 4 | 37.51 | 44.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 106 | 0 | 38.26 | 60 | 60 | 102.3 | 88.81 | 83.24 | 0 | 101.06 | 2.28 | 90.8 | 43.05 | 107.78 | 12.62 | 104.36 | 110 | 0 | 15693 | 80.58 | 114.76 | 220.22 | 214.17 | 219.56 | 0 | 32.64 | 50.19 | 13813 | 91.74 | 42.3 | 37.51 | 1.91 | 42.3 | 0 | 606 | 430.1 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581 | 313.7 | 0 | 307.4 | 101.04 | 15691 | 15693 | 317
03/26/22 10:40:41.195 | 588.9695 | 1367.8864 | 54.1768 | 43.8725 | 10.3043 | 31.4615 | 51.0043 | 0 | 1783.4452 | 89.8093 | 80.6803 | 9.129 | 23.8797 | 70.0818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.998 | 461.88 | 458.66 | 462.46 | 413.85 | 443.71 | 420.07 | 315.78 | 0.53616 | 0.44462 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7095288.7046 | 8136517.7026 | 8136517.7026 | 62.4281 | 62.1811 | 1.0018 | 0.99799 | 684694.2988 | 890074.7471 | 461 | 0.50759 | 0 | 0 | 31.4615 | 23.8797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017915 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 588.5983 | 1368.0725 | 53.9913 | 43.6956 | 31.0903 | 1786.8746 | 79.9782 | 24.8514 | 460.5536 | 0.0060657 | 59.9952 | 0.53526 | 0.25085 | 89.0966 | 2.1317 | 0.3021 | 0.17685 | 4.9217 | 0.64776 | 0.25611 | 0 | 100 | 579.1 | 317 | 108.03 | 104.4 | 100.71 | 308 | 3 | 91.86 | 42.25 | 4 | 37.46 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 106.25 | 0 | 38.21 | 60 | 60 | 102.45 | 88.9 | 83.21 | 0 | 100.73 | 2.28 | 90.91 | 43.01 | 108.05 | 12.52 | 104.4 | 110 | 0 | 15693 | 80.58 | 114.76 | 220.22 | 214.17 | 219.68 | 0 | 32.78 | 50.52 | 13818 | 91.88 | 42.24 | 37.45 | 1.77 | 42.24 | 0 | 606 | 428.7 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 313.6 | 0 | 307.3 | 100.68 | 15694 | 15693 | 315
03/26/22 10:40:46.195 | 586.4334 | 1363.2467 | 54.1738 | 43.879 | 10.2948 | 30.7001 | 50.9778 | 0 | 1787.5585 | 89.8144 | 80.6944 | 9.12 | 25.5044 | 70.0943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 461.91 | 458.66 | 462.47 | 413.4 | 443.23 | 419.57 | 315.41 | 0.53784 | -0.10111 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7064094.717 | 8149133.017 | 8149133.017 | 62.4281 | 62.181 | 1.0018 | 0.99799 | 682372.0354 | 892125.7107 | 461.0134 | 0.51047 | 0 | 0 | 30.7001 | 25.5044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017911 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 588.4528 | 1368.0442 | 53.9882 | 43.6948 | 31.0901 | 1786.86 | 79.9919 | 24.8551 | 460.5594 | 0.0060782 | 59.9951 | 0.53537 | 0.24924 | 89.1085 | 2.1617 | 0.29718 | 0.17568 | 4.9157 | 0.63653 | 0.25423 | 0 | 100 | 577.8 | 318 | 108.23 | 104.5 | 100.49 | 308.2 | 3 | 91.98 | 42.16 | 4 | 37.38 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 106.4 | 0 | 38.13 | 60 | 60 | 102.68 | 89.02 | 83.21 | 0 | 100.49 | 2.29 | 91.02 | 42.92 | 108.23 | 12.53 | 104.5 | 110 | 0 | 15693 | 80.58 | 114.76 | 220.22 | 214.17 | 219.68 | 0 | 33.01 | 50.65 | 13822 | 91.98 | 42.16 | 37.38 | 1.69 | 42.16 | 0 | 607 | 428 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 314.5 | 0 | 308.2 | 100.49 | 15693 | 15693 | 318
03/26/22 10:40:51.196 | 587.7092 | 1367.7316 | 54.1651 | 43.8818 | 10.2834 | 30.7394 | 51.0099 | 0 | 1789.3184 | 89.8202 | 80.7129 | 9.1073 | 25.5552 | 70.1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0001 | 461.9101 | 458.6601 | 462.4701 | 413.4001 | 443.2301 | 419.5701 | 315.4101 | 0.53668 | 0.12123 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7079527.4299 | 8145869.4989 | 8145869.4989 | 62.4281 | 62.1809 | 1.0018 | 0.99799 | 684617.3381 | 893001.4982 | 461.0134 | 0.51047 | 0 | 0 | 30.7394 | 25.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017905 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 588.3048 | 1368.0186 | 53.9849 | 43.694 | 31.0901 | 1786.863 | 80.0057 | 24.8558 | 460.5651 | 0.0060904 | 59.995 | 0.53548 | 0.24751 | 89.1205 | 2.1376 | 0.29197 | 0.17441 | 4.9171 | 0.62501 | 0.25291 | 0 | 100 | 577.7 | 316 | 108.35 | 104.58 | 100.47 | 306.4 | 3 | 92.04 | 42.13 | 4 | 37.34 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 106.5 | 0 | 38.1 | 60 | 60 | 102.75 | 89.06 | 83.32 | 0 | 100.5 | 2.3 | 91.07 | 42.89 | 108.35 | 12.54 | 104.58 | 110 | 0 | 15693 | 80.61 | 114.76 | 220.22 | 214.17 | 219.68 | 0 | 32.97 | 50.31 | 13828 | 92.04 | 42.13 | 37.34 | 1.57 | 42.13 | 0 | 606 | 430 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 312.3 | 0 | 306.1 | 100.49 | 15695 | 15693 | 316
03/26/22 10:40:56.195 | 588.6208 | 1371.7056 | 54.1547 | 43.8832 | 10.2714 | 30.7505 | 51.012 | 0 | 1790.5106 | 89.8277 | 80.7339 | 9.0938 | 25.245 | 70.1029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 461.92 | 458.64 | 462.47 | 413.18 | 443.06 | 419.33 | 315.24 | 0.53556 | 0.29106 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7090475.3435 | 8142384.603 | 8142384.603 | 62.4281 | 62.1808 | 1.0018 | 0.99799 | 686289.101 | 893638.1045 | 461.01 | 0.51409 | 0 | 0 | 30.7505 | 25.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017902 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 588.1686 | 1368.0317 | 53.9816 | 43.6931 | 31.0885 | 1786.9089 | 80.0196 | 24.8578 | 460.5704 | 0.0061019 | 59.9949 | 0.53558 | 0.2455 | 89.1324 | 2.153 | 0.28647 | 0.17306 | 4.9123 | 0.61314 | 0.25211 | 0 | 100 | 577.3 | 314 | 108.45 | 104.64 | 100.4 | 306 | 3 | 92.11 | 42.11 | 4 | 37.33 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 106.63 | 0 | 38.07 | 60 | 60 | 102.85 | 89.12 | 83.47 | 0 | 100.4 | 2.3 | 91.13 | 42.86 | 108.45 | 12.55 | 104.66 | 110 | 0 | 15693 | 80.61 | 114.74 | 220.22 | 214.27 | 219.68 | 0 | 32.72 | 49.9 | 13833 | 92.09 | 42.11 | 37.33 | 1.52 | 42.11 | 0 | 606 | 429 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.2 | 312.1 | 0 | 305.9 | 100.56 | 15694 | 15693 | 316
03/26/22 10:41:01.196 | 584.1768 | 1365.1511 | 54.1225 | 43.8817 | 10.2408 | 30.9498 | 51.0147 | 0 | 1792.095 | 89.8537 | 80.7968 | 9.0569 | 24.7268 | 70.1137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 461.92 | 458.63 | 462.48 | 412.63 | 442.62 | 418.75 | 314.82 | 0.53891 | 0.0056586 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7037272.8192 | 8112456.9237 | 8112456.9237 | 62.4282 | 62.1803 | 1.0018 | 0.99798 | 683327.5757 | 894375.7153 | 461.01 | 0.51626 | 0 | 0 | 30.9498 | 24.7268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017895 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 588.0294 | 1368.0434 | 53.9781 | 43.6922 | 31.0867 | 1786.9607 | 80.0335 | 24.8583 | 460.5758 | 0.0061134 | 59.9948 | 0.53568 | 0.24372 | 89.1443 | 2.1635 | 0.28068 | 0.17161 | 4.9119 | 0.60089 | 0.25119 | 0 | 100 | 577.4 | 317 | 108.58 | 104.68 | 100.42 | 304.2 | 3 | 92.16 | 42.1 | 4 | 37.31 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 106.7 | 0 | 38.06 | 60 | 60 | 103 | 89.2 | 83.58 | 0 | 100.43 | 2.3 | 91.17 | 42.85 | 108.55 | 12.53 | 104.68 | 110 | 0 | 15693 | 80.61 | 114.71 | 220.22 | 214.27 | 219.68 | 0 | 32.52 | 49.68 | 13838 | 92.14 | 42.1 | 37.31 | 1.52 | 42.1 | 0 | 606 | 429.2 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 314.1 | 0 | 307.9 | 100.37 | 15694 | 15693 | 317
03/26/22 10:41:06.195 | 582.9094 | 1363.7112 | 54.1087 | 43.8794 | 10.2293 | 30.6258 | 51.013 | 0 | 1792.2086 | 89.866 | 80.8236 | 9.0424 | 25.1269 | 70.0963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9971 | 461.9201 | 458.6301 | 462.4801 | 412.6301 | 442.6201 | 418.7501 | 314.8201 | 0.54008 | -0.055376 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7021751.0035 | 8100445.4381 | 8100445.4381 | 62.4282 | 62.1801 | 1.0018 | 0.99798 | 682607.4386 | 894428.6918 | 461.0101 | 0.51626 | 0 | 0 | 30.6258 | 25.1269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017895 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 587.856 | 1367.9998 | 53.9745 | 43.6913 | 31.0846 | 1787.0101 | 80.0479 | 24.8581 | 460.5803 | 0.0061232 | 59.9947 | 0.53581 | 0.23949 | 89.1564 | 2.1713 | 0.27452 | 0.17005 | 4.9198 | 0.58861 | 0.25165 | 0 | 100 | 576.6 | 317 | 108.65 | 104.7 | 100.28 | 307.9 | 3 | 92.2 | 42.08 | 4 | 37.29 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 106.8 | 0 | 38.05 | 60 | 60 | 103.05 | 89.23 | 83.62 | 0 | 100.28 | 2.3 | 91.23 | 42.84 | 108.68 | 12.51 | 104.72 | 110 | 0 | 15693 | 80.61 | 114.69 | 220.22 | 214.27 | 219.68 | 0 | 32.46 | 49.74 | 13842 | 92.21 | 42.08 | 37.29 | 1.5 | 42.08 | 0 | 606 | 431.5 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.9 | 312.3 | 0 | 306.1 | 100.33 | 15691 | 15693 | 316
03/26/22 10:41:11.195 | 582.6871 | 1366.8852 | 54.0715 | 43.8699 | 10.2016 | 31.5579 | 51.0103 | 0 | 1788.2552 | 89.9021 | 80.8959 | 9.0062 | 24.1941 | 70.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.995 | 461.91 | 458.62 | 462.52 | 411.84 | 442.02 | 418.12 | 314.3 | 0.5394 | 0.54649 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7019964.3066 | 8049144.4344 | 8049144.4344 | 62.4283 | 62.1795 | 1.0018 | 0.99798 | 684197.8384 | 892445.7904 | 461.0167 | 0.51987 | 0 | 0 | 31.5579 | 24.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017899 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 587.6898 | 1367.9838 | 53.9706 | 43.6902 | 31.0855 | 1787.0441 | 80.0624 | 24.8571 | 460.5845 | 0.0061323 | 59.9945 | 0.53594 | 0.2385 | 89.1686 | 2.1731 | 0.268 | 0.16834 | 4.9192 | 0.57612 | 0.25231 | 0 | 100 | 576.8 | 317 | 108.73 | 104.76 | 100.31 | 308.3 | 3 | 92.24 | 42.08 | 4 | 37.29 | 43.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 106.93 | 0 | 38.05 | 60 | 60 | 103.18 | 89.29 | 83.66 | 0 | 100.31 | 2.31 | 91.29 | 42.84 | 108.78 | 12.52 | 104.78 | 110 | 0 | 15693 | 80.63 | 114.69 | 220.22 | 214.27 | 219.68 | 0 | 32.44 | 49.79 | 13847 | 92.25 | 42.08 | 37.29 | 1.48 | 42.08 | 0 | 606 | 429.5 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 310.9 | 0 | 304.7 | 100.23 | 15692 | 15693 | 316
03/26/22 10:41:16.195 | 582.1833 | 1368.2529 | 54.0436 | 43.861 | 10.1826 | 30.5453 | 51.0256 | 0 | 1786.6089 | 89.9307 | 80.9493 | 8.9814 | 25.1008 | 70.1087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.995 | 461.91 | 458.62 | 462.52 | 411.84 | 442.02 | 418.12 | 314.3 | 0.53986 | 0.80565 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7013056.3933 | 8020612.498 | 8020612.498 | 62.4283 | 62.1791 | 1.0018 | 0.99798 | 684883.6748 | 891616.8434 | 461.0167 | 0.51987 | 0 | 0 | 30.5453 | 25.1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.0179 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 587.5224 | 1367.9835 | 53.9665 | 43.6891 | 31.0845 | 1787.0735 | 80.0774 | 24.8577 | 460.5886 | 0.006141 | 59.9944 | 0.53606 | 0.23989 | 89.181 | 2.1731 | 0.26105 | 0.16643 | 4.9006 | 0.5638 | 0.25339 | 0 | 100 | 577.3 | 317 | 108.9 | 104.84 | 100.4 | 306.7 | 3 | 92.33 | 42.09 | 4 | 37.3 | 43.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.05 | 0 | 38.05 | 60 | 60 | 103.28 | 89.35 | 83.75 | 0 | 100.4 | 2.31 | 91.36 | 42.84 | 108.88 | 12.52 | 104.84 | 110 | 0 | 15693 | 80.65 | 114.69 | 220.22 | 214.27 | 219.68 | 0 | 32.45 | 50.01 | 13852 | 92.31 | 42.09 | 37.3 | 1.47 | 42.09 | 0 | 606 | 429.7 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.5 | 312.5 | 0 | 306.3 | 100.26 | 15694 | 15693 | 317
03/26/22 10:41:21.195 | 580.9802 | 1370.1005 | 53.9897 | 43.842 | 10.1477 | 31.4655 | 51.0182 | 0 | 1786.2683 | 89.9888 | 81.051 | 8.9378 | 24.596 | 70.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9941 | 461.8901 | 458.6301 | 462.5401 | 411.4401 | 441.6701 | 417.8001 | 314.0301 | 0.54052 | 1.1382 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6999466.0034 | 7979635.1835 | 7979635.1835 | 62.4284 | 62.1782 | 1.0018 | 0.99798 | 685810.9353 | 891432.8742 | 461.0201 | 0.51842 | 0 | 0 | 31.4655 | 24.596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017905 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 587.3497 | 1367.9897 | 53.9622 | 43.6878 | 31.0837 | 1787.1088 | 80.0927 | 24.8609 | 460.5924 | 0.0061493 | 59.9944 | 0.53619 | 0.24187 | 89.1936 | 2.1744 | 0.25374 | 0.16437 | 4.882 | 0.55147 | 0.25477 | 0 | 100 | 576.9 | 317 | 108.93 | 104.85 | 100.33 | 307.5 | 3 | 92.34 | 42.08 | 4 | 37.29 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.03 | 0 | 38.05 | 60 | 60 | 103.25 | 89.33 | 83.88 | 0 | 100.33 | 2.31 | 91.35 | 42.84 | 108.88 | 12.54 | 104.85 | 110 | 0 | 15693 | 80.65 | 114.69 | 220.22 | 214.27 | 219.68 | 0 | 32.58 | 50.2 | 13857 | 92.31 | 42.08 | 37.29 | 1.52 | 42.08 | 0 | 606 | 430.1 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 312 | 0 | 305.8 | 100.4 | 15695 | 15693 | 313
03/26/22 10:41:26.195 | 579.0111 | 1368.0258 | 53.9576 | 43.829 | 10.1286 | 31.4821 | 51.0011 | 0 | 1784.6013 | 90.0273 | 81.1131 | 8.9142 | 24.0178 | 70.0657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9941 | 461.8901 | 458.6301 | 462.5401 | 411.4401 | 441.6701 | 417.8001 | 314.0301 | 0.54236 | 1.2108 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6975809.6483 | 7950471.9169 | 7950471.9169 | 62.4285 | 62.1777 | 1.0018 | 0.99798 | 684773.8498 | 890592.4402 | 461.0201 | 0.51842 | 0 | 0 | 31.4821 | 24.0178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017904 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 587.1632 | 1367.9831 | 53.9576 | 43.6864 | 31.0868 | 1787.1365 | 80.1084 | 24.8553 | 460.5961 | 0.0061573 | 59.9943 | 0.53633 | 0.24436 | 89.2065 | 2.1722 | 0.24599 | 0.16206 | 4.8557 | 0.5395 | 0.25612 | 0 | 100 | 577.5 | 314 | 108.9 | 104.87 | 100.43 | 304 | 3 | 92.33 | 42.1 | 4 | 37.31 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.1 | 0 | 38.07 | 60 | 60 | 103.25 | 89.35 | 84.03 | 0 | 100.43 | 2.31 | 91.38 | 42.86 | 108.95 | 12.53 | 104.87 | 110 | 0 | 15693 | 80.67 | 114.71 | 220.34 | 214.27 | 219.68 | 0 | 32.8 | 50.64 | 13862 | 92.34 | 42.1 | 37.31 | 1.52 | 42.1 | 0 | 606 | 427.5 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 313.9 | 0 | 307.6 | 100.43 | 15692 | 15693 | 317
03/26/22 10:41:31.195 | 577.6409 | 1366.3588 | 53.9271 | 43.8149 | 10.1122 | 30.8091 | 51.0075 | 0 | 1786.6141 | 90.0683 | 81.175 | 8.8933 | 24.8793 | 70.0814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9941 | 461.8701 | 458.6301 | 462.5301 | 411.4301 | 441.5601 | 417.8501 | 314.0201 | 0.54363 | 1.0991 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6958861.5816 | 7942597.3678 | 7942597.3678 | 62.4285 | 62.1773 | 1.0018 | 0.99798 | 684023.1317 | 891268.4174 | 461.0101 | 0.51626 | 0 | 0 | 30.8091 | 24.8793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017903 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 586.9795 | 1367.993 | 53.9528 | 43.6849 | 31.0889 | 1787.1445 | 80.1244 | 24.8476 | 460.5998 | 0.0061653 | 59.9943 | 0.53646 | 0.24944 | 89.2194 | 2.1614 | 0.23773 | 0.15953 | 4.8525 | 0.52769 | 0.25741 | 0 | 100 | 577.8 | 316 | 108.98 | 104.89 | 100.49 | 306.9 | 3 | 92.37 | 42.11 | 4 | 37.33 | 43.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.18 | 0 | 38.09 | 60 | 60 | 103.35 | 89.39 | 84.15 | 0 | 100.49 | 2.31 | 91.42 | 42.88 | 109.03 | 12.52 | 104.89 | 110 | 0 | 15693 | 80.67 | 114.76 | 220.34 | 214.27 | 219.68 | 0 | 33.04 | 50.91 | 13867 | 92.38 | 42.11 | 37.33 | 1.45 | 42.11 | 0 | 606 | 429 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.2 | 314.9 | 0 | 308.6 | 100.56 | 15693 | 15693 | 317
03/26/22 10:41:36.195 | 577.3998 | 1367.4787 | 53.9095 | 43.8052 | 10.1043 | 30.4406 | 51.0133 | 0 | 1786.707 | 90.0961 | 81.2136 | 8.8825 | 25.3873 | 70.0889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.994 | 461.87 | 458.63 | 462.53 | 411.43 | 441.56 | 417.85 | 314.02 | 0.54385 | 1.1776 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6955547.3769 | 7933055.3414 | 7933055.3414 | 62.4286 | 62.1768 | 1.0018 | 0.99798 | 684502.1451 | 891629.4031 | 461.01 | 0.51626 | 0 | 0 | 30.4406 | 25.3873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017903 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 586.7947 | 1368.0097 | 53.9478 | 43.6833 | 31.0884 | 1787.1309 | 80.1405 | 24.8466 | 460.6034 | 0.0061731 | 59.9942 | 0.5366 | 0.25638 | 89.2325 | 2.1456 | 0.22889 | 0.15675 | 4.8503 | 0.51602 | 0.25858 | 0 | 100 | 577.8 | 315 | 109.05 | 104.93 | 100.49 | 305.5 | 3 | 92.39 | 42.13 | 4 | 37.34 | 43.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.18 | 0 | 38.1 | 60 | 60 | 103.35 | 89.39 | 84.26 | 0 | 100.43 | 2.31 | 91.42 | 42.89 | 109.03 | 12.53 | 104.93 | 110 | 0 | 15693 | 80.69 | 114.79 | 220.34 | 214.27 | 219.68 | 0 | 33.2 | 50.98 | 13872 | 92.41 | 42.13 | 37.34 | 1.37 | 42.13 | 0 | 606 | 430.4 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.4 | 314.2 | 0 | 308 | 100.59 | 15691 | 15693 | 315
03/26/22 10:41:41.195 | 576.4478 | 1366.8904 | 53.8705 | 43.7787 | 10.0919 | 31.5373 | 51.0192 | 0 | 1786.8773 | 90.1719 | 81.3077 | 8.8642 | 23.6125 | 70.0591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9931 | 461.8801 | 458.6301 | 462.5301 | 411.5301 | 441.5801 | 417.9201 | 314.0701 | 0.54484 | 1.2722 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6945075.539 | 7915380.5323 | 7915380.5323 | 62.4287 | 62.1759 | 1.0018 | 0.99797 | 684209.3489 | 891701.4026 | 461.0134 | 0.51698 | 0 | 0 | 31.5373 | 23.6125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017904 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 586.6003 | 1368.0173 | 53.9425 | 43.6815 | 31.0915 | 1787.1258 | 80.1572 | 24.8399 | 460.6073 | 0.0061814 | 59.9942 | 0.53675 | 0.26284 | 89.246 | 2.1391 | 0.21945 | 0.15371 | 4.8501 | 0.50496 | 0.25952 | 0 | 100 | 578.5 | 317 | 109.1 | 104.95 | 100.61 | 308.7 | 3 | 92.43 | 42.15 | 4 | 37.36 | 43.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.25 | 0 | 38.11 | 60 | 60 | 103.38 | 89.4 | 84.37 | 0 | 100.61 | 2.31 | 91.46 | 42.9 | 109.1 | 12.52 | 104.95 | 110 | 0 | 15693 | 80.71 | 114.79 | 220.34 | 214.27 | 219.68 | 0 | 33.37 | 51.06 | 13877 | 92.43 | 42.15 | 37.36 | 1.29 | 42.15 | 0 | 606 | 431.6 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.8 | 312.6 | 0 | 306.4 | 100.66 | 15692 | 15693 | 315
03/26/22 10:41:46.195 | 576.9966 | 1368.4593 | 53.8537 | 43.7639 | 10.0899 | 31.6156 | 51.0197 | 0 | 1783.9046 | 90.216 | 81.3558 | 8.8602 | 23.9076 | 70.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.993 | 461.88 | 458.62 | 462.52 | 411.72 | 441.61 | 418.04 | 314.16 | 0.54447 | 1.568 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6951761.4169 | 7898882.608 | 7898882.608 | 62.4287 | 62.1755 | 1.0018 | 0.99797 | 684995.4526 | 890211.2765 | 461.0067 | 0.51771 | 0 | 0 | 31.6156 | 23.9076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017911 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 586.4168 | 1368.0432 | 53.9371 | 43.6795 | 31.0994 | 1787.1021 | 80.1739 | 24.8276 | 460.6112 | 0.0061898 | 59.9941 | 0.5369 | 0.27156 | 89.2596 | 2.1159 | 0.20945 | 0.15038 | 4.8554 | 0.49435 | 0.26019 | 0 | 100 | 578.3 | 318 | 109.2 | 104.95 | 100.59 | 309.4 | 3 | 92.48 | 42.16 | 4 | 37.38 | 43.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.4 | 0 | 38.13 | 60 | 60 | 103.5 | 89.47 | 84.45 | 0 | 100.59 | 2.31 | 91.54 | 42.91 | 109.23 | 12.47 | 104.95 | 110 | 0 | 15693 | 80.73 | 114.81 | 220.34 | 214.27 | 219.68 | 0 | 33.42 | 50.91 | 13883 | 92.48 | 42.18 | 37.38 | 1.24 | 42.18 | 0 | 606 | 430.4 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 314.9 | 0 | 308.6 | 100.57 | 15693 | 15693 | 316
03/26/22 10:41:51.194 | 575.5704 | 1365.0427 | 53.8354 | 43.7453 | 10.0901 | 30.6328 | 51.024 | 0 | 1782.4388 | 90.2805 | 81.4214 | 8.8591 | 25.4412 | 70.1425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9821 | 461.7901 | 458.4801 | 462.3701 | 412.2901 | 441.8201 | 418.3201 | 314.3701 | 0.54619 | 1.4209 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6933716.1333 | 7893129.615 | 7893129.615 | 62.4288 | 62.1748 | 1.0018 | 0.99797 | 683286.0552 | 889470.786 | 460.8801 | 0.52074 | 0 | 0 | 30.6328 | 25.4412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.01791 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 586.2266 | 1368.0443 | 53.9317 | 43.6775 | 31.1004 | 1787.0652 | 80.1907 | 24.8251 | 460.615 | 0.0061981 | 59.994 | 0.53705 | 0.27924 | 89.2734 | 2.1148 | 0.199 | 0.14685 | 4.8685 | 0.48389 | 0.26066 | 0 | 100 | 578.2 | 316 | 109.2 | 104.97 | 100.56 | 307.8 | 3 | 92.5 | 42.18 | 4 | 37.39 | 43.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.48 | 0 | 38.13 | 60 | 60 | 103.58 | 89.51 | 84.54 | 0 | 100.56 | 2.31 | 91.58 | 42.91 | 109.23 | 12.48 | 104.97 | 110 | 0 | 15693 | 80.73 | 114.81 | 220.34 | 214.27 | 219.68 | 0 | 33.43 | 50.83 | 13887 | 92.5 | 42.18 | 37.39 | 1.22 | 42.18 | 0 | 606 | 433.1 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 311.4 | 0 | 305.2 | 100.64 | 15694 | 15693 | 316
03/26/22 10:41:56.194 | 576.7155 | 1367.6026 | 53.8256 | 43.7344 | 10.0912 | 30.4062 | 50.9982 | 0 | 1787.8166 | 90.3302 | 81.4694 | 8.8608 | 25.6863 | 70.1095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.982 | 461.79 | 458.48 | 462.37 | 412.29 | 441.82 | 418.32 | 314.37 | 0.5451 | 1.272 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6947308.097 | 7918611.8886 | 7918611.8886 | 62.4288 | 62.1743 | 1.0018 | 0.99797 | 684567.8453 | 892147.7349 | 460.88 | 0.52074 | 0 | 0 | 30.4062 | 25.6863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017902 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 586.0476 | 1368.0541 | 53.9263 | 43.6753 | 31.0929 | 1787.0585 | 80.2078 | 24.8367 | 460.6182 | 0.0062051 | 59.9939 | 0.5372 | 0.28519 | 89.2875 | 2.1087 | 0.18834 | 0.14305 | 4.8666 | 0.47441 | 0.26033 | 0 | 100 | 578.5 | 316 | 109.15 | 104.99 | 100.57 | 307.4 | 3 | 92.46 | 42.16 | 4 | 37.38 | 43.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.45 | 0 | 38.13 | 60 | 60 | 103.53 | 89.48 | 84.62 | 0 | 100.57 | 2.31 | 91.57 | 42.91 | 109.18 | 12.52 | 104.99 | 110 | 0 | 15693 | 80.75 | 114.81 | 220.34 | 214.27 | 219.68 | 0 | 33.45 | 50.73 | 13892 | 92.47 | 42.18 | 37.39 | 1.2 | 42.18 | 0 | 605 | 430.3 | 458.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 312.8 | 0 | 306.6 | 100.61 | 15693 | 15693 | 315
03/26/22 10:42:01.194 | 576.8482 | 1367.6335 | 53.82 | 43.7267 | 10.0933 | 31.544 | 51.0147 | 0 | 1790.1906 | 90.3822 | 81.517 | 8.8651 | 24.4349 | 70.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.983 | 461.73 | 458.38 | 462.27 | 412.81 | 442.2 | 418.7 | 314.66 | 0.54548 | 1.1414 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6949900.6163 | 7931522.292 | 7931522.292 | 62.4288 | 62.1738 | 1.0018 | 0.99797 | 684583.5808 | 893325.7925 | 460.7933 | 0.52373 | 0 | 0 | 31.544 | 24.4349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017902 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.8869 | 1368.0624 | 53.9212 | 43.6731 | 31.0899 | 1787.0926 | 80.2245 | 24.8435 | 460.6215 | 0.006212 | 59.9938 | 0.53733 | 0.28889 | 89.3016 | 2.1085 | 0.17834 | 0.13902 | 4.8646 | 0.46632 | 0.25996 | 0 | 100 | 579.6 | 315 | 109.2 | 105.01 | 100.66 | 307 | 3 | 92.48 | 42.2 | 4 | 37.41 | 43.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.43 | 0 | 38.16 | 60 | 60 | 103.5 | 89.47 | 84.73 | 0 | 100.68 | 2.31 | 91.56 | 42.95 | 109.2 | 12.53 | 105.01 | 110 | 0 | 15693 | 80.78 | 114.81 | 220.34 | 214.27 | 219.68 | 0 | 33.56 | 50.9 | 13897 | 92.48 | 42.2 | 37.41 | 1.16 | 42.2 | 0 | 606 | 429.7 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.6 | 313.3 | 0 | 307 | 100.8 | 15690 | 15693 | 315
03/26/22 10:42:06.194 | 577.3063 | 1368.418 | 53.8196 | 43.7241 | 10.0955 | 31.572 | 51.0192 | 0 | 1787.2385 | 90.4162 | 81.5468 | 8.8695 | 24.1172 | 70.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9831 | 461.7001 | 458.3401 | 462.2301 | 413.0301 | 442.3801 | 418.8501 | 314.7901 | 0.54527 | 1.3442 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6955438.6499 | 7921893.9011 | 7921893.9011 | 62.4288 | 62.1734 | 1.0018 | 0.99797 | 684976.2732 | 891848.5315 | 460.7567 | 0.5245 | 0 | 0 | 31.572 | 24.1172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.01791 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.7379 | 1368.0632 | 53.9164 | 43.6709 | 31.0888 | 1787.1437 | 80.2411 | 24.8446 | 460.6237 | 0.0062169 | 59.9936 | 0.53747 | 0.29001 | 89.3158 | 2.1085 | 0.16888 | 0.1349 | 4.8345 | 0.45968 | 0.25966 | 0 | 100 | 579.7 | 317 | 109.28 | 105.01 | 100.82 | 307.2 | 3 | 92.52 | 42.21 | 4 | 37.43 | 43.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.55 | 0 | 38.18 | 60 | 60 | 103.63 | 89.54 | 84.84 | 0 | 100.82 | 2.31 | 91.62 | 42.96 | 109.3 | 12.48 | 105.01 | 110 | 0 | 15693 | 80.8 | 114.86 | 220.34 | 214.27 | 219.68 | 0 | 33.76 | 51.06 | 13902 | 92.54 | 42.21 | 37.43 | 1.11 | 42.21 | 0 | 606 | 432.3 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 312.7 | 0 | 306.4 | 100.82 | 15692 | 15693 | 315
03/26/22 10:42:11.194 | 577.9212 | 1369.5999 | 53.8209 | 43.7234 | 10.0975 | 30.8861 | 51.0242 | 0 | 1785.7625 | 90.4442 | 81.5712 | 8.8731 | 24.989 | 70.1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.983 | 461.7 | 458.34 | 462.23 | 413.03 | 442.38 | 418.85 | 314.79 | 0.54469 | 1.4645 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6962237.5481 | 7919509.933 | 7919509.933 | 62.4288 | 62.1731 | 1.0018 | 0.99797 | 685567.8229 | 891108.5894 | 460.7567 | 0.5245 | 0 | 0 | 30.8861 | 24.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017897 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.5998 | 1368.0644 | 53.9118 | 43.6687 | 31.0842 | 1787.1926 | 80.2576 | 24.8505 | 460.6257 | 0.0062211 | 59.9934 | 0.5376 | 0.29106 | 89.3301 | 2.1094 | 0.15971 | 0.13072 | 4.775 | 0.45386 | 0.25935 | 0 | 100 | 579.6 | 316 | 109.38 | 105.01 | 100.8 | 308.5 | 3 | 92.57 | 42.23 | 4 | 37.44 | 43.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.63 | 0 | 38.18 | 60 | 60 | 103.65 | 89.55 | 84.92 | 0 | 100.8 | 2.31 | 91.66 | 42.96 | 109.38 | 12.44 | 105.01 | 110 | 0 | 15693 | 80.8 | 114.88 | 220.34 | 214.27 | 219.68 | 0 | 33.81 | 50.79 | 13907 | 92.57 | 42.23 | 37.44 | 1.04 | 42.23 | 0 | 606 | 431.1 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.5 | 311.2 | 0 | 304.9 | 100.78 | 15693 | 15693 | 313
03/26/22 10:42:16.195 | 578.137 | 1369.698 | 53.8265 | 43.726 | 10.1006 | 31.3294 | 51.0248 | 0 | 1792.2499 | 90.5005 | 81.6217 | 8.8788 | 24.5804 | 70.1322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9821 | 461.6001 | 458.2201 | 462.1301 | 413.3001 | 442.7201 | 419.1601 | 314.9701 | 0.5448 | 1.0854 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6965219.9096 | 7952812.063 | 7952812.063 | 62.4288 | 62.1726 | 1.0018 | 0.99797 | 685616.6705 | 894338.8116 | 460.6501 | 0.52752 | 0 | 0 | 31.3294 | 24.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017896 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.4895 | 1368.0669 | 53.9078 | 43.6667 | 31.0831 | 1787.245 | 80.2735 | 24.8506 | 460.627 | 0.0062241 | 59.9932 | 0.53772 | 0.29131 | 89.3443 | 2.1113 | 0.15268 | 0.12692 | 4.7834 | 0.45105 | 0.25907 | 0 | 100 | 578.8 | 316 | 109.35 | 105.03 | 100.66 | 308.3 | 3 | 92.56 | 42.21 | 4 | 37.43 | 43.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.63 | 0 | 38.18 | 60 | 60 | 103.65 | 89.56 | 85.03 | 0 | 100.66 | 2.31 | 91.66 | 42.96 | 109.35 | 12.49 | 105.03 | 110 | 0 | 15693 | 80.82 | 114.88 | 220.34 | 214.27 | 219.68 | 0 | 33.58 | 50.28 | 13913 | 92.55 | 42.21 | 37.43 | 1.05 | 42.21 | 0 | 606 | 432.7 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579 | 314.8 | 0 | 308.5 | 100.7 | 15690 | 15693 | 317
03/26/22 10:42:21.195 | 576.3733 | 1365.4247 | 53.8311 | 43.7298 | 10.1013 | 31.5572 | 51.0137 | 0 | 1787.285 | 90.5271 | 81.6457 | 8.8814 | 24.3646 | 70.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9891 | 461.5501 | 458.1801 | 462.0901 | 413.4301 | 442.9101 | 419.3801 | 315.0901 | 0.54668 | 1.079 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6944169.3097 | 7932829.5967 | 7932829.5967 | 62.4288 | 62.1723 | 1.0018 | 0.99797 | 683477.4237 | 891857.9587 | 460.6067 | 0.52684 | 0 | 0 | 31.5572 | 24.3646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017913 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.3921 | 1368.0554 | 53.9043 | 43.6648 | 31.084 | 1787.2351 | 80.2889 | 24.8493 | 460.6279 | 0.0062259 | 59.993 | 0.53782 | 0.29377 | 89.3584 | 2.1201 | 0.14714 | 0.12351 | 4.7814 | 0.45013 | 0.25889 | 0 | 100 | 580.2 | 317 | 109.38 | 105.07 | 100.9 | 307.9 | 3 | 92.57 | 42.25 | 4 | 37.46 | 43.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.68 | 0 | 38.2 | 60 | 60 | 103.68 | 89.58 | 85.09 | 0 | 100.9 | 2.31 | 91.69 | 42.99 | 109.38 | 12.48 | 105.07 | 110 | 0 | 15693 | 80.84 | 114.9 | 220.34 | 214.27 | 219.68 | 0 | 33.39 | 50.11 | 13918 | 92.59 | 42.26 | 37.48 | 1.03 | 42.26 | 0 | 606 | 432.4 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.3 | 315.8 | 0 | 309.5 | 100.92 | 15692 | 15693 | 317
03/26/22 10:42:26.194 | 575.8473 | 1363.5203 | 53.8369 | 43.7348 | 10.1021 | 31.5688 | 51.0231 | 0 | 1780.297 | 90.5527 | 81.6683 | 8.8845 | 24.4425 | 70.1974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9891 | 461.5501 | 458.1801 | 462.0901 | 413.4301 | 442.9101 | 419.3801 | 315.0901 | 0.54718 | 1.3325 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6937940.1566 | 7907007.0934 | 7907007.0934 | 62.4288 | 62.1721 | 1.0018 | 0.99797 | 682815.8831 | 888729.1193 | 460.6067 | 0.52684 | 0 | 0 | 31.5688 | 24.4425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016241 | 0.017919 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.3084 | 1368.048 | 53.9013 | 43.6632 | 31.0836 | 1787.1792 | 80.304 | 24.8496 | 460.6283 | 0.0062268 | 59.9928 | 0.53792 | 0.29846 | 89.3723 | 2.1336 | 0.14291 | 0.12052 | 4.8035 | 0.45075 | 0.2588 | 0 | 100 | 580.3 | 316 | 109.5 | 105.07 | 100.92 | 309.3 | 3 | 92.64 | 42.28 | 4 | 37.49 | 43.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.73 | 0 | 38.23 | 60 | 60 | 103.8 | 89.63 | 85.18 | 0 | 100.92 | 2.31 | 91.71 | 43.01 | 109.5 | 12.43 | 105.07 | 110 | 0 | 15693 | 80.86 | 114.93 | 220.22 | 214.27 | 219.68 | 0 | 33.35 | 50.21 | 13922 | 92.64 | 42.28 | 37.5 | 1.02 | 42.28 | 0 | 606 | 431.1 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 313.9 | 0 | 307.7 | 100.82 | 15692 | 15693 | 316
03/26/22 10:42:31.194 | 576.1251 | 1365.6363 | 53.8456 | 43.7425 | 10.1031 | 31.2632 | 51.024 | 0 | 1779.7241 | 90.5845 | 81.6962 | 8.8883 | 24.6384 | 70.1838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9891 | 461.5501 | 458.1801 | 462.0901 | 413.4301 | 442.9101 | 419.3801 | 315.0901 | 0.54691 | 1.4195 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6940930.8355 | 7903074.6951 | 7903074.6951 | 62.4288 | 62.1718 | 1.0018 | 0.99797 | 683073.8397 | 887857.3158 | 460.6067 | 0.52684 | 0 | 0 | 31.2632 | 24.6384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017917 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.2582 | 1368.0491 | 53.8992 | 43.6619 | 31.0861 | 1787.1198 | 80.3181 | 24.8429 | 460.6287 | 0.0062277 | 59.9927 | 0.53799 | 0.30345 | 89.3857 | 2.1322 | 0.14092 | 0.11851 | 4.8293 | 0.45427 | 0.25871 | 0 | 100 | 579.8 | 315 | 109.48 | 105.07 | 100.83 | 306.8 | 3 | 92.63 | 42.3 | 4 | 37.51 | 43.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.75 | 0 | 38.23 | 60 | 60 | 103.8 | 89.63 | 85.24 | 0 | 100.83 | 2.31 | 91.73 | 43.01 | 109.5 | 12.45 | 105.07 | 110 | 0 | 15693 | 80.88 | 114.95 | 220.22 | 214.27 | 219.68 | 0 | 33.53 | 50.58 | 13927 | 92.63 | 42.3 | 37.51 | 1 | 42.3 | 0 | 606 | 431.3 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.9 | 316 | 0 | 309.7 | 100.85 | 15693 | 15693 | 318
03/26/22 10:42:36.194 | 578.2806 | 1369.5844 | 53.8566 | 43.7526 | 10.104 | 30.5932 | 51.018 | 0 | 1785.5767 | 90.6187 | 81.7265 | 8.8922 | 25.4079 | 70.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 461.58 | 458.22 | 462.11 | 413.67 | 443.15 | 419.69 | 315.31 | 0.54525 | 1.3297 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6966293.0389 | 7935940.7858 | 7935940.7858 | 62.4287 | 62.1714 | 1.0018 | 0.99797 | 685558.4912 | 890994.2743 | 460.6367 | 0.52464 | 0 | 0 | 30.5932 | 25.4079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017906 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.2236 | 1368.059 | 53.8975 | 43.6609 | 31.0829 | 1787.0853 | 80.332 | 24.8457 | 460.6291 | 0.0062285 | 59.9926 | 0.53804 | 0.30735 | 89.399 | 2.1352 | 0.13956 | 0.11692 | 4.8178 | 0.45888 | 0.25867 | 0 | 100 | 580.8 | 316 | 109.55 | 105.09 | 101.01 | 309.2 | 3 | 92.66 | 42.3 | 4 | 37.51 | 43.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.8 | 0 | 38.25 | 60 | 60 | 103.88 | 89.67 | 85.24 | 0 | 101.01 | 2.31 | 91.75 | 43.02 | 109.55 | 12.43 | 105.09 | 110 | 0 | 15693 | 80.88 | 114.98 | 220.22 | 214.27 | 219.68 | 0 | 33.8 | 51.1 | 13932 | 92.66 | 42.31 | 37.53 | 0.98 | 42.31 | 0 | 606 | 434.6 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.5 | 315.9 | 0 | 309.6 | 100.96 | 15693 | 15693 | 318
03/26/22 10:42:41.194 | 578.2786 | 1369.6876 | 53.8696 | 43.7646 | 10.105 | 30.5728 | 51.0217 | 0 | 1792.3582 | 90.6533 | 81.7566 | 8.8967 | 25.5924 | 70.1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0031 | 461.5901 | 458.2401 | 462.1101 | 413.8201 | 443.1801 | 419.8001 | 315.4001 | 0.54541 | 0.98328 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6965915.8046 | 7963415.9239 | 7963415.9239 | 62.4287 | 62.1711 | 1.0018 | 0.99796 | 685506.3822 | 893638.3196 | 460.6468 | 0.52245 | 0 | 0 | 30.5728 | 25.5924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017898 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.1934 | 1368.0584 | 53.8963 | 43.6602 | 31.0805 | 1787.1096 | 80.3456 | 24.8495 | 460.6296 | 0.0062296 | 59.9926 | 0.53809 | 0.30749 | 89.4121 | 2.1347 | 0.13884 | 0.11591 | 4.8334 | 0.46473 | 0.25861 | 0 | 100 | 580.3 | 317 | 109.5 | 105.11 | 100.92 | 307.8 | 3 | 92.64 | 42.33 | 4 | 37.54 | 43.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.78 | 0 | 38.26 | 60 | 60 | 103.77 | 89.62 | 85.33 | 0 | 100.92 | 2.31 | 91.74 | 43.05 | 109.5 | 12.47 | 105.11 | 110 | 0 | 15693 | 80.9 | 115.03 | 220.22 | 214.27 | 219.68 | 0 | 34.27 | 51.66 | 13937 | 92.64 | 42.33 | 37.54 | 0.97 | 42.33 | 0 | 606 | 433.6 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.5 | 312.9 | 0 | 306.7 | 100.96 | 15694 | 15693 | 315
03/26/22 10:42:46.194 | 578.5977 | 1370.1212 | 53.8743 | 43.7687 | 10.1056 | 30.6604 | 51.0141 | 0 | 1793.3388 | 90.664 | 81.7656 | 8.8984 | 25.5202 | 70.1347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0111 | 461.6001 | 458.2501 | 462.0901 | 413.9401 | 443.2201 | 419.9201 | 315.4601 | 0.54521 | 0.87722 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6970167.6344 | 7976081.1946 | 7976081.1946 | 62.4287 | 62.171 | 1.0018 | 0.99796 | 685826.3933 | 894862.0806 | 460.6467 | 0.52028 | 0 | 0 | 30.6604 | 25.5202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017897 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.1744 | 1368.0652 | 53.8956 | 43.6599 | 31.0772 | 1787.1134 | 80.3585 | 24.8518 | 460.6302 | 0.0062308 | 59.9927 | 0.53813 | 0.30889 | 89.4247 | 2.1394 | 0.13865 | 0.11557 | 4.8381 | 0.47165 | 0.25854 | 0 | 100 | 581 | 316 | 109.45 | 105.13 | 101.04 | 307.5 | 3 | 92.61 | 42.34 | 4 | 37.55 | 43.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.78 | 0 | 38.27 | 60 | 60 | 103.85 | 89.64 | 85.33 | 0 | 101.04 | 2.31 | 91.74 | 43.06 | 109.45 | 12.52 | 105.13 | 110 | 0 | 15693 | 80.95 | 115.07 | 220.22 | 214.27 | 219.68 | 0 | 34.55 | 51.72 | 13942 | 92.61 | 42.34 | 37.55 | 0.98 | 42.34 | 0 | 606 | 432.6 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.9 | 313.6 | 0 | 307.3 | 101.03 | 15692 | 15693 | 318
03/26/22 10:42:51.193 | 579.2432 | 1371.2669 | 53.8942 | 43.7857 | 10.1085 | 29.9843 | 51.0168 | 0 | 1793.7053 | 90.704 | 81.7991 | 8.9049 | 26.2331 | 70.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0181 | 461.6201 | 458.2701 | 462.0901 | 414.0801 | 443.2601 | 420.0401 | 315.5501 | 0.54476 | 0.8698 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6977340.4221 | 7984290.5172 | 7984290.5172 | 62.4286 | 62.1706 | 1.0018 | 0.99796 | 686399.0214 | 895040.2399 | 460.6601 | 0.51882 | 0 | 0 | 29.9843 | 26.2331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017886 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.1602 | 1368.0756 | 53.8954 | 43.66 | 31.0707 | 1787.127 | 80.3712 | 24.858 | 460.6306 | 0.0062318 | 59.9928 | 0.53817 | 0.30996 | 89.4371 | 2.1504 | 0.13862 | 0.11567 | 4.8532 | 0.47951 | 0.25852 | 0 | 100 | 580.9 | 318 | 109.55 | 105.13 | 101.03 | 309.1 | 3 | 92.66 | 42.35 | 4 | 37.56 | 43.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.83 | 0 | 38.29 | 60 | 60 | 103.85 | 89.66 | 85.39 | 0 | 101.03 | 2.31 | 91.77 | 43.07 | 109.55 | 12.47 | 105.13 | 110 | 0 | 15693 | 80.95 | 115.07 | 220.22 | 214.27 | 219.68 | 0 | 34.75 | 51.7 | 13947 | 92.66 | 42.35 | 37.56 | 0.98 | 42.35 | 0 | 606 | 434.3 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.9 | 314.4 | 0 | 308.1 | 101.03 | 15692 | 15693 | 316
03/26/22 10:42:56.194 | 578.7467 | 1369.8115 | 53.9049 | 43.7954 | 10.1096 | 30.1834 | 51.0291 | 0 | 1797.767 | 90.7234 | 81.8156 | 8.9078 | 26.346 | 70.1669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.021 | 461.64 | 458.29 | 462.09 | 414.26 | 443.33 | 420.25 | 315.66 | 0.54542 | 0.55356 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6971332.1325 | 8003978.8031 | 8003978.8031 | 62.4286 | 62.1704 | 1.0018 | 0.99796 | 685752.7881 | 896959.485 | 460.6734 | 0.51736 | 0 | 0 | 30.1834 | 26.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017878 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.1409 | 1368.0717 | 53.8954 | 43.6603 | 31.0655 | 1787.1774 | 80.3837 | 24.864 | 460.6311 | 0.0062327 | 59.9929 | 0.5382 | 0.30829 | 89.4493 | 2.1463 | 0.13862 | 0.11596 | 4.9141 | 0.48754 | 0.25852 | 0 | 100 | 581.1 | 317 | 109.6 | 105.13 | 101.06 | 308.8 | 3 | 92.69 | 42.34 | 4 | 37.55 | 43.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.78 | 0 | 38.29 | 60 | 60 | 103.83 | 89.64 | 85.43 | 0 | 101.06 | 2.31 | 91.74 | 43.07 | 109.6 | 12.44 | 105.13 | 110 | 0 | 15693 | 80.97 | 115.1 | 220.22 | 214.27 | 219.68 | 0 | 34.79 | 51.37 | 13952 | 92.69 | 42.34 | 37.55 | 1 | 42.34 | 0 | 606 | 434.3 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581 | 314.6 | 0 | 308.3 | 101.04 | 15695 | 15693 | 316
03/26/22 10:43:01.194 | 578.5519 | 1369.2232 | 53.9238 | 43.8122 | 10.1116 | 31.0341 | 51.0081 | 0 | 1793.504 | 90.7539 | 81.841 | 8.9129 | 25.1508 | 70.1888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.022 | 461.66 | 458.31 | 462.05 | 414.55 | 443.32 | 420.53 | 315.8 | 0.54585 | 0.72034 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6969928.5016 | 7989246.7427 | 7989246.7427 | 62.4285 | 62.1701 | 1.0018 | 0.99796 | 685374.6902 | 894933.9212 | 460.6734 | 0.51302 | 0 | 0 | 31.0341 | 25.1508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017883 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.1248 | 1368.076 | 53.8958 | 43.661 | 31.0697 | 1787.1972 | 80.3959 | 24.8597 | 460.6315 | 0.0062337 | 59.9931 | 0.53824 | 0.30966 | 89.4611 | 2.149 | 0.13857 | 0.11642 | 4.9422 | 0.49599 | 0.25853 | 0 | 100 | 581.1 | 316 | 109.6 | 105.13 | 101.06 | 308.5 | 3 | 92.69 | 42.36 | 4 | 37.58 | 43.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.83 | 0 | 38.31 | 60 | 60 | 103.9 | 89.68 | 85.41 | 0 | 101.06 | 2.31 | 91.77 | 43.1 | 109.6 | 12.44 | 105.13 | 110 | 0 | 15693 | 80.99 | 115.1 | 220.22 | 214.27 | 219.68 | 0 | 34.7 | 51.04 | 13957 | 92.69 | 42.36 | 37.58 | 0.97 | 42.36 | 0 | 606 | 431.2 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.1 | 313.2 | 0 | 307 | 101.06 | 15693 | 15693 | 317
03/26/22 10:43:06.194 | 578.3665 | 1368.5677 | 53.9346 | 43.8213 | 10.1132 | 31.77 | 51.0217 | 0 | 1792.3376 | 90.7691 | 81.8531 | 8.916 | 24.2792 | 70.1566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.022 | 461.66 | 458.31 | 462.05 | 414.55 | 443.32 | 420.53 | 315.8 | 0.54602 | 0.75037 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6968337.8015 | 7985743.5939 | 7985743.5939 | 62.4285 | 62.17 | 1.0018 | 0.99796 | 685046.1311 | 894350.2144 | 460.6734 | 0.51302 | 0 | 0 | 31.77 | 24.2792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017886 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.107 | 1368.0756 | 53.8965 | 43.662 | 31.077 | 1787.1799 | 80.4079 | 24.8525 | 460.6315 | 0.0062337 | 59.9932 | 0.53828 | 0.31299 | 89.4728 | 2.1489 | 0.13844 | 0.11702 | 4.9186 | 0.50486 | 0.25853 | 0 | 100 | 581.8 | 316 | 109.63 | 105.13 | 101.18 | 308 | 3 | 92.69 | 42.38 | 4 | 37.59 | 43.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.88 | 0 | 38.33 | 60 | 60 | 103.95 | 89.7 | 85.48 | 0 | 101.18 | 2.31 | 91.79 | 43.11 | 109.6 | 12.44 | 105.15 | 110 | 0 | 15693 | 81.01 | 115.12 | 220.22 | 214.27 | 219.68 | 0 | 34.59 | 50.73 | 13962 | 92.69 | 42.38 | 37.59 | 0.96 | 42.38 | 0 | 606 | 430.4 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.6 | 316.6 | 0 | 310.3 | 101.15 | 15691 | 15693 | 317
03/26/22 10:43:11.193 | 578.7468 | 1369.3832 | 53.9457 | 43.831 | 10.1147 | 31.5821 | 51.0196 | 0 | 1786.6141 | 90.784 | 81.8649 | 8.9191 | 24.0428 | 70.1165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.02 | 461.65 | 458.29 | 462.03 | 414.68 | 443.4 | 420.73 | 315.9 | 0.54583 | 1.0272 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6973001.0375 | 7968620.2052 | 7968620.2052 | 62.4285 | 62.1699 | 1.0018 | 0.99796 | 685428.152 | 892296.6932 | 460.6567 | 0.51376 | 0 | 0 | 31.5821 | 24.0428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017893 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.092 | 1368.0845 | 53.8973 | 43.6632 | 31.0821 | 1787.1272 | 80.4199 | 24.8454 | 460.6313 | 0.0062333 | 59.9934 | 0.53831 | 0.3188 | 89.4844 | 2.151 | 0.13827 | 0.11765 | 4.873 | 0.51364 | 0.25851 | 0 | 100 | 581.3 | 316 | 109.65 | 105.13 | 101.11 | 306.6 | 3 | 92.72 | 42.38 | 4 | 37.59 | 43.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.93 | 0 | 38.33 | 60 | 60 | 103.98 | 89.72 | 85.45 | 0 | 101.11 | 2.31 | 91.82 | 43.11 | 109.68 | 12.4 | 105.13 | 110 | 0 | 15692 | 81.03 | 115.14 | 220.22 | 214.27 | 219.68 | 0 | 34.5 | 50.61 | 13967 | 92.73 | 42.38 | 37.59 | 0.96 | 42.38 | 0 | 605 | 433.3 | 458.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.3 | 312.8 | 0 | 306.6 | 101.1 | 15692 | 15692 | 316
03/26/22 10:43:16.194 | 576.7197 | 1364.377 | 53.9638 | 43.8483 | 10.1155 | 30.4871 | 51.0219 | 0 | 1783.7858 | 90.808 | 81.8845 | 8.9235 | 25.4337 | 70.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.016 | 461.63 | 458.28 | 462.01 | 414.69 | 443.49 | 420.93 | 315.97 | 0.54787 | 0.8722 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6947366.6618 | 7955637.1612 | 7955637.1612 | 62.4284 | 62.1696 | 1.0018 | 0.99796 | 682947.1196 | 890078.6308 | 460.64 | 0.51233 | 0 | 0 | 30.4871 | 25.4337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.01789 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.0646 | 1368.069 | 53.8985 | 43.6647 | 31.0824 | 1787.0821 | 80.4317 | 24.8431 | 460.631 | 0.0062327 | 59.9936 | 0.53836 | 0.32356 | 89.4957 | 2.1514 | 0.13791 | 0.1182 | 4.8645 | 0.52257 | 0.25845 | 0 | 100 | 580.7 | 316 | 109.73 | 105.15 | 101.03 | 308.4 | 3 | 92.76 | 42.38 | 4 | 37.59 | 43.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108 | 0 | 38.31 | 60 | 60 | 104.05 | 89.76 | 85.5 | 0 | 101.03 | 2.31 | 91.86 | 43.1 | 109.7 | 12.43 | 105.17 | 110 | 0 | 15692 | 81.05 | 115.17 | 220.22 | 214.27 | 219.68 | 0 | 34.5 | 50.53 | 13972 | 92.74 | 42.38 | 37.59 | 0.94 | 42.38 | 0 | 606 | 431.9 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.6 | 314.7 | 0 | 308.4 | 100.99 | 15693 | 15692 | 316
03/26/22 10:43:21.194 | 576.5273 | 1363.897 | 53.9766 | 43.8609 | 10.1157 | 30.5735 | 51.0246 | 0 | 1789.9687 | 90.8245 | 81.8984 | 8.9261 | 25.162 | 70.1925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0191 | 461.6201 | 458.2601 | 462.0001 | 414.7801 | 443.6001 | 421.1001 | 316.0601 | 0.54821 | 0.47937 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6945123.7282 | 7985194.2294 | 7985194.2294 | 62.4284 | 62.1694 | 1.0018 | 0.99796 | 682706.3054 | 893161.8421 | 460.6268 | 0.51379 | 0 | 0 | 30.5735 | 25.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017878 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.0334 | 1368.0528 | 53.8998 | 43.6664 | 31.081 | 1787.0677 | 80.4435 | 24.8418 | 460.6304 | 0.0062312 | 59.9937 | 0.53841 | 0.32611 | 89.507 | 2.1734 | 0.13749 | 0.11879 | 4.8553 | 0.5315 | 0.25827 | 0 | 100 | 581.4 | 317 | 109.65 | 105.19 | 101.13 | 306.6 | 3 | 92.72 | 42.39 | 4 | 37.6 | 43.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.93 | 0 | 38.33 | 60 | 60 | 103.98 | 89.74 | 85.48 | 0 | 101.13 | 2.31 | 91.82 | 43.11 | 109.63 | 12.47 | 105.19 | 110 | 0 | 15692 | 81.08 | 115.17 | 220.22 | 214.27 | 219.68 | 0 | 34.39 | 50.35 | 13977 | 92.72 | 42.39 | 37.6 | 0.95 | 42.39 | 0 | 606 | 431.2 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.4 | 314.7 | 0 | 308.4 | 101.11 | 15691 | 15692 | 317
03/26/22 10:43:26.194 | 577.3985 | 1366.3536 | 53.9868 | 43.8701 | 10.1167 | 31.1203 | 51.0147 | 0 | 1790.6087 | 90.8365 | 81.9083 | 8.9282 | 24.3165 | 70.1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0191 | 461.6201 | 458.2601 | 462.0001 | 414.7801 | 443.6001 | 421.1001 | 316.0601 | 0.54739 | 0.54849 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6955972.3174 | 7990466.4474 | 7990466.4474 | 62.4284 | 62.1693 | 1.0018 | 0.99796 | 683697.9948 | 893683.5882 | 460.6267 | 0.51379 | 0 | 0 | 31.1203 | 24.3165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017881 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 585.0053 | 1368.0397 | 53.9013 | 43.6683 | 31.0783 | 1787.0646 | 80.4552 | 24.8406 | 460.6294 | 0.0062291 | 59.9938 | 0.53846 | 0.32923 | 89.5181 | 2.1794 | 0.13695 | 0.1193 | 4.8527 | 0.54032 | 0.25794 | 0 | 100 | 582.2 | 316 | 109.68 | 105.21 | 101.27 | 308.8 | 3 | 92.73 | 42.43 | 4 | 37.64 | 43.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.98 | 0 | 38.36 | 60 | 60 | 104 | 89.74 | 85.52 | 0 | 101.27 | 2.31 | 91.84 | 43.15 | 109.68 | 12.48 | 105.21 | 110 | 0 | 15692 | 81.08 | 115.19 | 220.22 | 214.27 | 219.68 | 0 | 34.36 | 50.45 | 13982 | 92.73 | 42.43 | 37.64 | 0.93 | 42.43 | 0 | 606 | 432.4 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.3 | 316.4 | 0 | 310.1 | 101.27 | 15691 | 15692 | 318
03/26/22 10:43:31.194 | 579.1451 | 1370.1057 | 54.0016 | 43.8824 | 10.1192 | 31.3573 | 51.0215 | 0 | 1784.5135 | 90.8524 | 81.9214 | 8.931 | 24.1376 | 70.1752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 461.6201 | 458.2601 | 461.9901 | 414.9701 | 443.7701 | 421.3401 | 316.2101 | 0.54599 | 1.0917 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6977293.6201 | 7968264.5216 | 7968264.5216 | 62.4283 | 62.1692 | 1.0018 | 0.99796 | 685609.0242 | 890959.7074 | 460.6234 | 0.51307 | 0 | 0 | 31.3573 | 24.1376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017894 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.9879 | 1368.0517 | 53.9029 | 43.6703 | 31.078 | 1787.0546 | 80.467 | 24.8397 | 460.6284 | 0.006227 | 59.9939 | 0.5385 | 0.33466 | 89.5292 | 2.1826 | 0.13636 | 0.1198 | 4.8539 | 0.54902 | 0.25761 | 0 | 100 | 582.3 | 317 | 109.9 | 105.23 | 101.3 | 310.5 | 3 | 92.85 | 42.44 | 4 | 37.65 | 43.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.13 | 0 | 38.38 | 60 | 60 | 104.17 | 89.83 | 85.5 | 0 | 101.3 | 2.31 | 91.92 | 43.16 | 109.88 | 12.4 | 105.23 | 110 | 0 | 15691 | 81.1 | 115.22 | 220.22 | 214.27 | 219.68 | 0 | 34.41 | 50.57 | 13987 | 92.83 | 42.44 | 37.65 | 0.91 | 42.44 | 0 | 606 | 434.1 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.3 | 316.8 | 0 | 310.5 | 101.27 | 15691 | 15691 | 317
03/26/22 10:43:36.193 | 578.6981 | 1368.1755 | 54.0186 | 43.8964 | 10.1222 | 31.5858 | 51.0335 | 0 | 1779.0687 | 90.8698 | 81.9372 | 8.9325 | 23.7831 | 70.1537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 461.6401 | 458.2901 | 462.0201 | 414.9701 | 443.7901 | 421.3501 | 316.2301 | 0.54645 | 1.3818 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6972147.008 | 7940614.0624 | 7940614.0624 | 62.4283 | 62.169 | 1.0018 | 0.99796 | 684846.0671 | 887717.5166 | 460.6501 | 0.51232 | 0 | 0 | 31.5858 | 23.7831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017907 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.9691 | 1368.0581 | 53.9046 | 43.6724 | 31.0764 | 1787.047 | 80.4787 | 24.841 | 460.6272 | 0.0062243 | 59.9941 | 0.53854 | 0.34016 | 89.5404 | 2.1873 | 0.13574 | 0.1203 | 4.8594 | 0.55756 | 0.25709 | 0 | 100 | 582 | 315 | 109.9 | 105.25 | 101.22 | 309.7 | 3 | 92.85 | 42.44 | 4 | 37.65 | 43.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.2 | 0 | 38.38 | 60 | 60 | 104.25 | 89.87 | 85.56 | 0 | 101.22 | 2.32 | 91.96 | 43.16 | 109.93 | 12.42 | 105.27 | 110 | 0 | 15690 | 81.12 | 115.24 | 220.34 | 214.27 | 219.68 | 0 | 34.46 | 50.6 | 13992 | 92.85 | 42.44 | 37.65 | 0.9 | 42.44 | 0 | 606 | 432.3 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.7 | 315.1 | 0 | 308.8 | 101.17 | 15690 | 15690 | 315
03/26/22 10:43:41.193 | 577.4803 | 1364.4338 | 54.0345 | 43.9098 | 10.1247 | 31.3356 | 51.0205 | 0 | 1776.9991 | 90.8868 | 81.9535 | 8.9333 | 24.1684 | 70.1739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 461.67 | 458.32 | 462.04 | 414.97 | 443.81 | 421.36 | 316.25 | 0.54764 | 1.3802 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6957499.8554 | 7926363.2076 | 7926363.2076 | 62.4283 | 62.1689 | 1.0018 | 0.99796 | 683274.8243 | 886080.4815 | 460.6767 | 0.51157 | 0 | 0 | 31.3356 | 24.1684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017902 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.9358 | 1368.0309 | 53.9065 | 43.6747 | 31.0745 | 1787.0125 | 80.4906 | 24.8415 | 460.626 | 0.0062217 | 59.9942 | 0.53859 | 0.34499 | 89.5516 | 2.1944 | 0.13515 | 0.1209 | 4.9171 | 0.56602 | 0.25647 | 0 | 100 | 581.7 | 318 | 109.98 | 105.29 | 101.17 | 309.7 | 3 | 92.88 | 42.45 | 4 | 37.66 | 43.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.25 | 0 | 38.39 | 60 | 60 | 104.3 | 89.9 | 85.54 | 0 | 101.17 | 2.32 | 91.99 | 43.17 | 110 | 12.39 | 105.29 | 110 | 0 | 15690 | 81.14 | 115.26 | 220.34 | 214.27 | 219.68 | 0 | 34.47 | 50.6 | 13997 | 92.9 | 42.45 | 37.66 | 0.92 | 42.45 | 0 | 606 | 432.8 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.7 | 316 | 0 | 309.7 | 101.17 | 15689 | 15690 | 318
03/26/22 10:43:46.194 | 576.8334 | 1363.3087 | 54.0399 | 43.9143 | 10.1256 | 31.2361 | 51.0101 | 0 | 1779.0842 | 90.8931 | 81.9596 | 8.9335 | 24.4944 | 70.1958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 461.67 | 458.32 | 462.04 | 414.97 | 443.81 | 421.36 | 316.25 | 0.54825 | 1.0784 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6949366.4602 | 7942342.3611 | 7942342.3611 | 62.4282 | 62.1687 | 1.0018 | 0.99796 | 682408.9992 | 887722.1335 | 460.6767 | 0.51157 | 0 | 0 | 31.2361 | 24.4944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017906 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.8948 | 1367.9867 | 53.9085 | 43.677 | 31.0737 | 1787.0182 | 80.5024 | 24.841 | 460.6248 | 0.0062193 | 59.9942 | 0.53865 | 0.3469 | 89.5627 | 2.2089 | 0.13449 | 0.12142 | 4.9074 | 0.57431 | 0.25581 | 0 | 100 | 581.8 | 317 | 110.1 | 105.35 | 101.18 | 309.5 | 3 | 92.95 | 42.49 | 4 | 37.7 | 43.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.33 | 0 | 38.43 | 60 | 60 | 104.35 | 89.92 | 85.63 | 0 | 101.18 | 2.32 | 92.03 | 43.21 | 110.1 | 12.4 | 105.35 | 110 | 0 | 15689 | 81.16 | 115.26 | 220.34 | 214.27 | 219.68 | 0 | 34.47 | 50.59 | 14002 | 92.95 | 42.49 | 37.7 | 0.98 | 42.49 | 0 | 606 | 433.6 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.8 | 315.8 | 0 | 309.5 | 101.18 | 15688 | 15689 | 317
03/26/22 10:43:51.193 | 579.7114 | 1369.507 | 54.0619 | 43.9318 | 10.1301 | 31.5028 | 51.0083 | 0 | 1782.093 | 90.9211 | 81.9864 | 8.9347 | 24.1151 | 70.1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 461.74 | 458.37 | 462.13 | 415.05 | 444 | 421.42 | 316.35 | 0.5457 | 1.3375 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6984260.8453 | 7956354.3006 | 7956354.3006 | 62.4282 | 62.1685 | 1.0018 | 0.99796 | 685510.6284 | 889219.74 | 460.7467 | 0.51583 | 0 | 0 | 31.5028 | 24.1151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.01791 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.8594 | 1367.955 | 53.9105 | 43.6794 | 31.0765 | 1787.0257 | 80.5143 | 24.8349 | 460.6238 | 0.006217 | 59.9943 | 0.5387 | 0.34981 | 89.5739 | 2.2156 | 0.13383 | 0.12195 | 4.8996 | 0.58245 | 0.25503 | 0 | 100 | 582 | 316 | 110.08 | 105.37 | 101.27 | 308.2 | 3 | 92.94 | 42.5 | 4 | 37.71 | 43.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.35 | 0 | 38.44 | 60 | 60 | 104.35 | 89.92 | 85.65 | 0 | 101.27 | 2.32 | 92.03 | 43.22 | 110.1 | 12.43 | 105.37 | 110 | 0 | 15688 | 81.18 | 115.29 | 220.34 | 214.27 | 219.79 | 0 | 34.42 | 50.55 | 14007 | 92.94 | 42.5 | 37.71 | 0.99 | 42.5 | 0 | 606 | 430.8 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 314.5 | 0 | 308.2 | 101.22 | 15687 | 15688 | 316
03/26/22 10:43:56.193 | 580.2599 | 1370.5547 | 54.0709 | 43.9388 | 10.132 | 31.0009 | 51.0155 | 0 | 1781.5718 | 90.934 | 81.9988 | 8.9352 | 24.5916 | 70.1425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 461.74 | 458.37 | 462.13 | 415.05 | 444 | 421.42 | 316.35 | 0.54519 | 1.4334 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6990422.8108 | 7955005.1171 | 7955005.1171 | 62.4282 | 62.1683 | 1.0018 | 0.99796 | 686034.6495 | 888957.9218 | 460.7467 | 0.51583 | 0 | 0 | 31.0009 | 24.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.01791 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.8409 | 1367.962 | 53.9127 | 43.682 | 31.0783 | 1786.9956 | 80.5263 | 24.8314 | 460.6228 | 0.0062149 | 59.9943 | 0.53874 | 0.3571 | 89.5852 | 2.2212 | 0.13323 | 0.12256 | 4.9146 | 0.59058 | 0.2542 | 0 | 100 | 582.4 | 316 | 110.18 | 105.39 | 101.3 | 309.1 | 3 | 92.99 | 42.51 | 4 | 37.73 | 43.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.43 | 0 | 38.45 | 60 | 60 | 104.43 | 89.96 | 85.65 | 0 | 101.3 | 2.32 | 92.08 | 43.23 | 110.18 | 12.38 | 105.39 | 110 | 0 | 15687 | 81.2 | 115.29 | 220.34 | 214.38 | 219.79 | 0 | 34.46 | 50.67 | 14012 | 93 | 42.51 | 37.73 | 0.98 | 42.51 | 0 | 606 | 431.1 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.4 | 316.8 | 0 | 310.6 | 101.29 | 15688 | 15687 | 316
03/26/22 10:44:01.193 | 579.741 | 1369.089 | 54.0798 | 43.946 | 10.1338 | 30.5435 | 51.0163 | 0 | 1785.876 | 90.9478 | 82.0127 | 8.9351 | 25.2819 | 70.1751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 461.74 | 458.37 | 462.13 | 415.05 | 444 | 421.42 | 316.35 | 0.54567 | 1.1007 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6983763.7018 | 7974926.4643 | 7974926.4643 | 62.4281 | 62.1682 | 1.0018 | 0.99796 | 685300.5639 | 891103.6845 | 460.7467 | 0.51583 | 0 | 0 | 30.5435 | 25.2819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017903 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.8186 | 1367.958 | 53.9149 | 43.6846 | 31.0731 | 1786.9952 | 80.5384 | 24.8378 | 460.6218 | 0.0062128 | 59.9943 | 0.53878 | 0.3623 | 89.5966 | 2.2184 | 0.13262 | 0.12318 | 4.9147 | 0.59863 | 0.25338 | 0 | 100 | 582.4 | 317 | 110.18 | 105.39 | 101.29 | 309.7 | 3 | 93 | 42.53 | 4 | 37.74 | 43.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.43 | 0 | 38.46 | 60 | 60 | 104.48 | 89.99 | 85.67 | 0 | 101.27 | 2.32 | 92.08 | 43.25 | 110.18 | 12.4 | 105.39 | 110 | 0 | 15686 | 81.2 | 115.31 | 220.34 | 214.38 | 219.79 | 0 | 34.51 | 50.73 | 14017 | 92.99 | 42.53 | 37.74 | 0.95 | 42.53 | 0 | 606 | 433 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.3 | 316.3 | 0 | 310 | 101.27 | 15686 | 15686 | 317
03/26/22 10:44:06.193 | 578.8714 | 1366.6117 | 54.0954 | 43.9584 | 10.137 | 30.3666 | 51.0066 | 0 | 1789.2771 | 90.9721 | 82.0373 | 8.9348 | 25.5881 | 70.1958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.004 | 461.82 | 458.46 | 462.19 | 415.03 | 443.91 | 421.44 | 316.37 | 0.54653 | 0.7781 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6973124.1601 | 7990140.7257 | 7990140.7257 | 62.4281 | 62.1679 | 1.0018 | 0.99796 | 684059.8538 | 892797.2681 | 460.8234 | 0.51285 | 0 | 0 | 30.3666 | 25.5881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017895 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.7937 | 1367.9454 | 53.9173 | 43.6872 | 31.0717 | 1787.026 | 80.5506 | 24.8403 | 460.6213 | 0.0062117 | 59.9944 | 0.53883 | 0.36541 | 89.608 | 2.2196 | 0.13207 | 0.12387 | 4.9114 | 0.60671 | 0.25291 | 0 | 100 | 581.5 | 316 | 110.15 | 105.41 | 101.13 | 310 | 3 | 92.98 | 42.54 | 4 | 37.75 | 43.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.4 | 0 | 38.48 | 60 | 60 | 104.48 | 89.99 | 85.75 | 0 | 101.13 | 2.31 | 92.07 | 43.26 | 110.13 | 12.44 | 105.41 | 110 | 0 | 15685 | 81.22 | 115.34 | 220.46 | 214.38 | 219.79 | 0 | 34.52 | 50.77 | 14022 | 92.96 | 42.54 | 37.75 | 0.94 | 42.54 | 0 | 606 | 430.4 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.5 | 314.2 | 0 | 307.9 | 101.13 | 15683 | 15685 | 316
03/26/22 10:44:11.193 | 581.3135 | 1372.3714 | 54.1183 | 43.9765 | 10.1418 | 30.0955 | 51.0266 | 0 | 1793.5143 | 91.0086 | 82.0729 | 8.9357 | 25.7716 | 70.1863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9981 | 461.8601 | 458.5401 | 462.2501 | 414.8901 | 443.7801 | 421.5401 | 316.3701 | 0.54423 | 0.9007 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7002372.1533 | 8009370.4108 | 8009370.4108 | 62.428 | 62.1676 | 1.0017 | 0.99796 | 686668.1713 | 894853.2408 | 460.8834 | 0.50844 | 0 | 0 | 30.0955 | 25.7716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017892 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.7822 | 1367.9611 | 53.9197 | 43.69 | 31.0694 | 1787.0438 | 80.5628 | 24.8435 | 460.6211 | 0.0062112 | 59.9944 | 0.53886 | 0.37138 | 89.6196 | 2.237 | 0.1316 | 0.12468 | 4.9288 | 0.61493 | 0.25266 | 0 | 100 | 582.7 | 317 | 110.18 | 105.43 | 101.34 | 308.2 | 3 | 92.99 | 42.56 | 4 | 37.78 | 43.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.4 | 0 | 38.5 | 60 | 60 | 104.4 | 89.95 | 85.8 | 0 | 101.3 | 2.31 | 92.07 | 43.28 | 110.2 | 12.44 | 105.43 | 110 | 0 | 15684 | 81.25 | 115.36 | 220.46 | 214.38 | 219.79 | 0 | 34.64 | 50.93 | 14027 | 92.99 | 42.56 | 37.78 | 0.93 | 42.56 | 0 | 606 | 434.6 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.5 | 313.6 | 0 | 307.3 | 101.3 | 15683 | 15684 | 317
03/26/22 10:44:16.193 | 580.3971 | 1369.3212 | 54.1313 | 43.9876 | 10.1437 | 31.2123 | 51.0221 | 0 | 1792.286 | 91.0297 | 82.094 | 8.9357 | 24.4211 | 70.1842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.998 | 461.86 | 458.54 | 462.25 | 414.89 | 443.78 | 421.54 | 316.37 | 0.54509 | 0.85555 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6992230.6026 | 8002966.3533 | 8002966.3533 | 62.428 | 62.1673 | 1.0017 | 0.99796 | 685414.5135 | 894290.6426 | 460.8834 | 0.50844 | 0 | 0 | 31.2123 | 24.4211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017896 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.7677 | 1367.9674 | 53.9223 | 43.6928 | 31.0725 | 1787.0536 | 80.5752 | 24.8396 | 460.6211 | 0.0062112 | 59.9945 | 0.5389 | 0.37747 | 89.6312 | 2.2393 | 0.13124 | 0.12561 | 4.9375 | 0.62319 | 0.25264 | 0 | 100 | 582.3 | 317 | 110.13 | 105.43 | 101.27 | 309.1 | 3 | 92.98 | 42.58 | 4 | 37.79 | 43.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.43 | 0 | 38.51 | 60 | 60 | 104.43 | 89.96 | 85.75 | 0 | 101.27 | 2.31 | 92.08 | 43.3 | 110.15 | 12.45 | 105.43 | 110 | 0 | 15683 | 81.27 | 115.38 | 220.46 | 214.38 | 219.79 | 0 | 34.68 | 51.06 | 14032 | 92.98 | 42.58 | 37.79 | 0.94 | 42.58 | 0 | 606 | 432.4 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.4 | 313.8 | 0 | 307.5 | 101.29 | 15682 | 15683 | 317
03/26/22 10:44:21.193 | 579.6538 | 1367.4529 | 54.1398 | 43.9952 | 10.1446 | 31.3121 | 51.0271 | 0 | 1789.9687 | 91.0436 | 82.1079 | 8.9358 | 24.3768 | 70.1747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 461.86 | 458.57 | 462.25 | 414.89 | 443.74 | 421.67 | 316.4 | 0.54584 | 0.87652 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6983360.3106 | 7992596.8369 | 7992596.8369 | 62.428 | 62.1672 | 1.0017 | 0.99796 | 684478.9531 | 893132.4485 | 460.8933 | 0.50409 | 0 | 0 | 31.3121 | 24.3768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01624 | 0.017892 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.7539 | 1367.9821 | 53.9249 | 43.6957 | 31.0718 | 1787.0707 | 80.5876 | 24.8384 | 460.6213 | 0.0062116 | 59.9947 | 0.53893 | 0.38365 | 89.6429 | 2.227 | 0.1309 | 0.12657 | 4.9422 | 0.63136 | 0.25286 | 0 | 100 | 582.3 | 317 | 110.23 | 105.43 | 101.25 | 308.7 | 3 | 93.01 | 42.58 | 4 | 37.79 | 43.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.45 | 0 | 38.53 | 60 | 60 | 104.53 | 90.02 | 85.75 | 0 | 101.25 | 2.31 | 92.09 | 43.31 | 110.28 | 12.4 | 105.43 | 110 | 0 | 15682 | 81.29 | 115.41 | 220.46 | 214.38 | 219.91 | 0 | 34.99 | 51.41 | 14037 | 93.03 | 42.59 | 37.8 | 0.92 | 42.59 | 0 | 606 | 432.6 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.3 | 313.9 | 0 | 307.6 | 101.27 | 15682 | 15682 | 314
03/26/22 10:44:26.193 | 577.9899 | 1363.319 | 54.1584 | 44.0122 | 10.1462 | 30.9478 | 51.0271 | 0 | 1788.2036 | 91.0725 | 82.1351 | 8.9374 | 24.5968 | 70.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.994 | 461.86 | 458.6 | 462.25 | 414.88 | 443.63 | 421.8 | 316.42 | 0.54745 | 0.70193 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6962990.9766 | 7986404.0716 | 7986404.0716 | 62.4279 | 62.1669 | 1.0017 | 0.99796 | 682408.8736 | 892247.9227 | 460.9034 | 0.49974 | 0 | 0 | 30.9478 | 24.5968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016241 | 0.017895 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.7314 | 1367.9688 | 53.9275 | 43.6987 | 31.0677 | 1787.1011 | 80.6001 | 24.8436 | 460.6218 | 0.0062127 | 59.9948 | 0.53897 | 0.38703 | 89.6547 | 2.2477 | 0.13072 | 0.1277 | 4.9322 | 0.63961 | 0.25332 | 0 | 100 | 582.4 | 316 | 110.25 | 105.45 | 101.29 | 308.7 | 3 | 93.03 | 42.6 | 4 | 37.81 | 43.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.48 | 0 | 38.54 | 60 | 60 | 104.53 | 90.02 | 85.78 | 0 | 101.29 | 2.31 | 92.11 | 43.32 | 110.25 | 12.42 | 105.45 | 110 | 0 | 15681 | 81.31 | 115.43 | 220.46 | 214.49 | 219.91 | 0 | 35.18 | 51.53 | 14042 | 93.03 | 42.59 | 37.8 | 0.98 | 42.59 | 0 | 606 | 433.5 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.7 | 313.6 | 0 | 307.3 | 101.34 | 15681 | 15681 | 317
03/26/22 10:44:31.193 | 579.555 | 1368.1651 | 54.175 | 44.0269 | 10.1481 | 31.2405 | 51.0306 | 0 | 1783.92 | 91.0959 | 82.1563 | 8.9396 | 24.4687 | 70.2045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9951 | 461.8601 | 458.6601 | 462.2301 | 414.8901 | 443.4501 | 422.1201 | 316.4701 | 0.54606 | 1.1197 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6982097.9323 | 7972005.2115 | 7972005.2115 | 62.4279 | 62.1667 | 1.0017 | 0.99796 | 684149.4116 | 890481.3797 | 460.9167 | 0.4896 | 0 | 0 | 31.2405 | 24.4687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017908 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.7215 | 1367.9854 | 53.9303 | 43.7017 | 31.0655 | 1787.121 | 80.6126 | 24.8455 | 460.6223 | 0.0062137 | 59.9949 | 0.539 | 0.39282 | 89.6665 | 2.2277 | 0.13067 | 0.12894 | 4.9149 | 0.64781 | 0.25377 | 0 | 100 | 582.5 | 317 | 110.33 | 105.47 | 101.34 | 310.2 | 3 | 93.07 | 42.61 | 4 | 37.82 | 43.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.53 | 0 | 38.56 | 60 | 60 | 104.58 | 90.05 | 85.82 | 0 | 101.34 | 2.31 | 92.13 | 43.35 | 110.33 | 12.4 | 105.47 | 110 | 0 | 15679 | 81.33 | 115.46 | 220.58 | 214.49 | 219.91 | 0 | 35.21 | 51.3 | 14047 | 93.07 | 42.61 | 37.84 | 0.96 | 42.61 | 0 | 606 | 432.3 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.7 | 316.1 | 0 | 309.8 | 101.34 | 15680 | 15679 | 317
03/26/22 10:44:36.193 | 582.1344 | 1372.4952 | 54.1982 | 44.0475 | 10.1507 | 30.6978 | 51.0151 | 0 | 1789.0655 | 91.1258 | 82.1828 | 8.9429 | 25.5447 | 70.2425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.998 | 461.87 | 458.7 | 462.23 | 414.9 | 443.37 | 422.2 | 316.48 | 0.54365 | 1.1978 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7012688.0633 | 7996175.4631 | 7996175.4631 | 62.4278 | 62.1663 | 1.0017 | 0.99796 | 687000.2617 | 892671.264 | 460.9334 | 0.48452 | 0 | 0 | 30.6978 | 25.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017886 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.7136 | 1368.0071 | 53.9331 | 43.7048 | 31.0583 | 1787.1415 | 80.6252 | 24.854 | 460.6228 | 0.006215 | 59.995 | 0.53903 | 0.39864 | 89.6784 | 2.2282 | 0.1307 | 0.13024 | 4.8888 | 0.65586 | 0.25432 | 0 | 100 | 583.4 | 316 | 110.35 | 105.47 | 101.46 | 309.4 | 3 | 93.08 | 42.65 | 4 | 37.86 | 43.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.58 | 0 | 38.59 | 60 | 60 | 104.58 | 90.05 | 85.86 | 0 | 101.46 | 2.31 | 92.16 | 43.37 | 110.38 | 12.37 | 105.47 | 110 | 0 | 15678 | 81.35 | 115.46 | 220.58 | 214.49 | 219.91 | 0 | 35.12 | 51.07 | 14052 | 93.09 | 42.65 | 37.86 | 0.92 | 42.65 | 0 | 606 | 431.2 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.9 | 315.9 | 0 | 309.6 | 101.37 | 15678 | 15678 | 317
03/26/22 10:44:41.192 | 581.8397 | 1371.6849 | 54.2108 | 44.0592 | 10.1516 | 31.5526 | 51.0304 | 0 | 1793.4988 | 91.1409 | 82.1959 | 8.945 | 24.47 | 70.1933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9981 | 461.8701 | 458.7001 | 462.2301 | 414.9001 | 443.3701 | 422.2001 | 316.4801 | 0.54393 | 0.90875 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7009888.5902 | 8016579.8423 | 8016579.8423 | 62.4278 | 62.1662 | 1.0017 | 0.99795 | 686594.1044 | 894881.4574 | 460.9334 | 0.48452 | 0 | 0 | 31.5526 | 24.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017891 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.7059 | 1368.0253 | 53.936 | 43.708 | 31.0548 | 1787.2176 | 80.6379 | 24.8588 | 460.6235 | 0.0062164 | 59.9952 | 0.53906 | 0.40123 | 89.6905 | 2.2448 | 0.13101 | 0.13183 | 4.8805 | 0.664 | 0.255 | 0 | 100 | 583 | 315 | 110.28 | 105.47 | 101.39 | 308.9 | 3 | 93.04 | 42.65 | 4 | 37.86 | 43.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.53 | 0 | 38.59 | 60 | 60 | 104.53 | 90.02 | 85.82 | 0 | 101.36 | 2.31 | 92.13 | 43.37 | 110.28 | 12.43 | 105.47 | 110 | 0 | 15677 | 81.35 | 115.46 | 220.58 | 214.49 | 219.91 | 0 | 35 | 50.74 | 14057 | 93.04 | 42.65 | 37.86 | 0.92 | 42.65 | 0 | 606 | 430.3 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 317 | 0 | 310.7 | 101.39 | 15675 | 15677 | 315
03/26/22 10:44:46.192 | 581.8596 | 1371.9275 | 54.2243 | 44.072 | 10.1523 | 31.324 | 51.0149 | 0 | 1788.792 | 91.1561 | 82.2084 | 8.9476 | 24.4552 | 70.2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.002 | 461.88 | 458.73 | 462.24 | 414.95 | 443.36 | 422.28 | 316.52 | 0.54398 | 1.0933 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 7010137.599 | 8002182.537 | 8002182.537 | 62.4278 | 62.1661 | 1.0017 | 0.99795 | 686585.9518 | 893139.4955 | 460.95 | 0.48161 | 0 | 0 | 31.324 | 24.4552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017895 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.6939 | 1368.0397 | 53.9389 | 43.7112 | 31.0544 | 1787.2731 | 80.6507 | 24.8598 | 460.6244 | 0.0062184 | 59.9954 | 0.53909 | 0.40404 | 89.7026 | 2.2614 | 0.13146 | 0.13354 | 4.8408 | 0.67199 | 0.25586 | 0 | 100 | 582.7 | 316 | 110.35 | 105.45 | 101.34 | 309.3 | 3 | 93.08 | 42.68 | 4 | 37.89 | 43.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.6 | 0 | 38.63 | 60 | 60 | 104.63 | 90.06 | 85.84 | 0 | 101.43 | 2.31 | 92.16 | 43.39 | 110.35 | 12.37 | 105.45 | 110 | 0 | 15675 | 81.37 | 115.46 | 220.58 | 214.49 | 220.03 | 0 | 34.84 | 50.55 | 14062 | 93.08 | 42.68 | 37.89 | 0.9 | 42.68 | 0 | 606 | 430.6 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.9 | 316 | 0 | 309.7 | 101.37 | 15675 | 15675 | 316
03/26/22 10:44:51.192 | 580.9035 | 1369.2954 | 54.2449 | 44.0919 | 10.153 | 30.9885 | 51.0331 | 0 | 1784.4981 | 91.177 | 82.2254 | 8.9516 | 24.891 | 70.2507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 461.91 | 458.75 | 462.24 | 414.97 | 443.1 | 422.11 | 316.43 | 0.54472 | 1.1873 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6998109.0672 | 7982636.3383 | 7982636.3383 | 62.4277 | 62.1658 | 1.0017 | 0.99795 | 685396.4876 | 890386.2961 | 460.9667 | 0.48087 | 0 | 0 | 30.9885 | 24.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017899 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.6818 | 1368.053 | 53.9419 | 43.7146 | 31.0523 | 1787.2948 | 80.6635 | 24.8601 | 460.6254 | 0.0062206 | 59.9956 | 0.53912 | 0.40889 | 89.7147 | 2.2688 | 0.13208 | 0.13539 | 4.8255 | 0.67984 | 0.25685 | 0 | 100 | 581.8 | 316 | 110.45 | 105.47 | 101.18 | 307.2 | 3 | 93.13 | 42.69 | 4 | 37.9 | 43.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.68 | 0 | 38.63 | 60 | 60 | 104.7 | 90.11 | 85.9 | 0 | 101.27 | 2.31 | 92.21 | 43.41 | 110.48 | 12.34 | 105.49 | 110 | 0 | 15674 | 81.4 | 115.46 | 220.71 | 214.6 | 220.03 | 0 | 34.7 | 50.39 | 14067 | 93.14 | 42.69 | 37.9 | 0.92 | 42.69 | 0 | 606 | 432.5 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.8 | 313.4 | 0 | 307.2 | 101.18 | 15672 | 15674 | 316
03/26/22 10:44:56.193 | 580.4892 | 1368.3716 | 54.2585 | 44.1058 | 10.1527 | 32.0102 | 51.0223 | 0 | 1784.0336 | 91.1898 | 82.2364 | 8.9535 | 23.9731 | 70.2561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 461.91 | 458.75 | 462.24 | 414.97 | 443.1 | 422.11 | 316.43 | 0.54511 | 1.1529 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6994017.2198 | 7981170.2657 | 7981170.2657 | 62.4276 | 62.1657 | 1.0017 | 0.99795 | 684933.4683 | 890152.9934 | 460.9667 | 0.48087 | 0 | 0 | 32.0102 | 23.9731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017898 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.6637 | 1368.0539 | 53.945 | 43.718 | 31.0547 | 1787.2864 | 80.6763 | 24.8569 | 460.6265 | 0.006223 | 59.9959 | 0.53916 | 0.41443 | 89.7269 | 2.2689 | 0.13289 | 0.13742 | 4.8304 | 0.68756 | 0.2579 | 0 | 100 | 582.2 | 314 | 110.38 | 105.5 | 101.27 | 308.3 | 3 | 93.09 | 42.68 | 4 | 37.89 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.68 | 0 | 38.63 | 60 | 60 | 104.7 | 90.11 | 85.9 | 0 | 101.27 | 2.31 | 92.21 | 43.41 | 110.4 | 12.4 | 105.5 | 110 | 0 | 15673 | 81.42 | 115.43 | 220.71 | 214.6 | 220.03 | 0 | 34.59 | 50.35 | 14072 | 93.1 | 42.69 | 37.9 | 0.98 | 42.69 | 0 | 606 | 433.8 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.3 | 314.1 | 0 | 307.9 | 101.27 | 15673 | 15673 | 315
03/26/22 10:45:01.192 | 580.4911 | 1368.4852 | 54.27 | 44.1182 | 10.1518 | 31.482 | 51.0155 | 0 | 1786.2889 | 91.2008 | 82.246 | 8.9548 | 24.7547 | 70.2313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0111 | 461.9101 | 458.7301 | 462.2301 | 415.0201 | 443.0501 | 421.9401 | 316.3901 | 0.54504 | 1.0382 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6993699.2893 | 7990018.1514 | 7990018.1514 | 62.4276 | 62.1656 | 1.0017 | 0.99795 | 684984.7169 | 890963.0464 | 460.9568 | 0.48305 | 0 | 0 | 31.482 | 24.7547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017895 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.6497 | 1368.0673 | 53.9482 | 43.7214 | 31.0619 | 1787.2605 | 80.6892 | 24.8475 | 460.6277 | 0.0062254 | 59.9961 | 0.53919 | 0.42158 | 89.7391 | 2.2641 | 0.13385 | 0.13956 | 4.8265 | 0.69512 | 0.25893 | 0 | 100 | 582.5 | 317 | 110.5 | 105.52 | 101.3 | 310.3 | 3 | 93.16 | 42.69 | 4 | 37.91 | 43.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.75 | 0 | 38.64 | 60 | 60 | 104.78 | 90.15 | 85.86 | 0 | 101.3 | 2.31 | 92.25 | 43.42 | 110.5 | 12.36 | 105.52 | 110 | 0 | 15672 | 81.44 | 115.43 | 220.71 | 214.6 | 220.03 | 0 | 34.55 | 50.46 | 14077 | 93.17 | 42.7 | 37.91 | 0.97 | 42.7 | 0 | 606 | 434.6 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.3 | 313.8 | 0 | 307.5 | 101.27 | 15671 | 15672 | 316
03/26/22 10:45:06.193 | 579.8883 | 1367.2052 | 54.2777 | 44.1268 | 10.1509 | 31.2425 | 51.0176 | 0 | 1787.3211 | 91.2084 | 82.253 | 8.9554 | 24.8005 | 70.2272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.011 | 461.91 | 458.73 | 462.23 | 415.02 | 443.05 | 421.94 | 316.39 | 0.54561 | 0.83628 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6986108.568 | 7998504.7832 | 7998504.7832 | 62.4276 | 62.1655 | 1.0017 | 0.99795 | 684348.7664 | 891790.9958 | 460.9567 | 0.48305 | 0 | 0 | 31.2425 | 24.8005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017896 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.63 | 1368.0692 | 53.9513 | 43.7249 | 31.0693 | 1787.2272 | 80.702 | 24.8378 | 460.6286 | 0.0062275 | 59.9964 | 0.53923 | 0.42815 | 89.7514 | 2.2633 | 0.13489 | 0.14177 | 4.8051 | 0.7025 | 0.25985 | 0 | 100 | 582.4 | 316 | 110.48 | 105.54 | 101.29 | 308.4 | 3 | 93.14 | 42.71 | 4 | 37.91 | 43.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.73 | 0 | 38.65 | 60 | 60 | 104.8 | 90.17 | 85.86 | 0 | 101.32 | 2.31 | 92.24 | 43.43 | 110.48 | 12.4 | 105.54 | 110 | 0 | 15671 | 81.44 | 115.43 | 220.83 | 214.6 | 220.15 | 0 | 34.61 | 50.69 | 14082 | 93.14 | 42.71 | 37.93 | 0.96 | 42.71 | 0 | 606 | 435.2 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.7 | 314.5 | 0 | 308.2 | 101.34 | 15670 | 15671 | 317
03/26/22 10:45:11.192 | 579.2952 | 1366.1988 | 54.2994 | 44.1514 | 10.1481 | 31.7396 | 51.019 | 0 | 1785.1483 | 91.2312 | 82.2748 | 8.9564 | 24.0439 | 70.2243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 461.95 | 458.74 | 462.24 | 415.01 | 442.96 | 421.74 | 316.34 | 0.54608 | 0.87238 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6979407.0647 | 7988805.3181 | 7988805.3181 | 62.4275 | 62.1653 | 1.0017 | 0.99795 | 683844.0247 | 890703.8222 | 460.9767 | 0.4852 | 0 | 0 | 31.7396 | 24.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017903 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.6098 | 1368.0755 | 53.9546 | 43.7285 | 31.0791 | 1787.1751 | 80.715 | 24.8259 | 460.63 | 0.0062304 | 59.9966 | 0.53926 | 0.43543 | 89.7638 | 2.2565 | 0.13619 | 0.14428 | 4.7763 | 0.70986 | 0.26103 | 0 | 100 | 582.3 | 315 | 110.5 | 105.54 | 101.22 | 308.9 | 3 | 93.16 | 42.73 | 4 | 37.94 | 43.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.78 | 0 | 38.66 | 60 | 60 | 104.83 | 90.18 | 85.88 | 0 | 101.22 | 2.31 | 92.26 | 43.44 | 110.5 | 12.39 | 105.54 | 110 | 0 | 15669 | 81.46 | 115.46 | 220.83 | 214.7 | 220.15 | 0 | 34.7 | 50.84 | 14086 | 93.16 | 42.73 | 37.94 | 0.95 | 42.73 | 0 | 606 | 433.5 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.2 | 314.7 | 0 | 308.4 | 101.25 | 15670 | 15669 | 314
03/26/22 10:45:16.193 | 579.7753 | 1367.52 | 54.3099 | 44.1632 | 10.1467 | 31.5783 | 51.0174 | 0 | 1783.7136 | 91.2434 | 82.2872 | 8.9562 | 24.4163 | 70.2094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 461.9801 | 458.7601 | 462.2601 | 414.9101 | 442.8401 | 421.5701 | 316.2601 | 0.54549 | 1.0164 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6985053.685 | 7982623.6426 | 7982623.6426 | 62.4275 | 62.1652 | 1.0017 | 0.99795 | 684504.8857 | 889986.2081 | 461.0001 | 0.4859 | 0 | 0 | 31.5783 | 24.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017908 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.5926 | 1368.0887 | 53.9578 | 43.7322 | 31.0812 | 1787.097 | 80.728 | 24.8243 | 460.6316 | 0.0062339 | 59.9969 | 0.5393 | 0.44441 | 89.7762 | 2.2462 | 0.13759 | 0.14688 | 4.7168 | 0.71712 | 0.26242 | 0 | 100 | 582.1 | 317 | 110.68 | 105.56 | 101.27 | 307.9 | 3 | 93.25 | 42.75 | 4 | 37.96 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.9 | 0 | 38.69 | 60 | 60 | 104.9 | 90.22 | 85.92 | 0 | 101.27 | 2.32 | 92.33 | 43.47 | 110.65 | 12.33 | 105.56 | 110 | 0 | 15669 | 81.48 | 115.46 | 220.83 | 214.7 | 220.15 | 0 | 34.75 | 50.91 | 14091 | 93.23 | 42.75 | 37.96 | 0.94 | 42.75 | 0 | 606 | 430.2 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.2 | 314.4 | 0 | 308.1 | 101.25 | 15669 | 15669 | 315
03/26/22 10:45:21.192 | 580.3634 | 1369.2645 | 54.3259 | 44.1818 | 10.1441 | 30.4736 | 51.0337 | 0 | 1783.5175 | 91.264 | 82.3098 | 8.9542 | 25.7336 | 70.2309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0171 | 461.9901 | 458.7501 | 462.2801 | 414.7701 | 442.8201 | 421.4201 | 316.1901 | 0.54481 | 1.1057 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6991174.3161 | 7981388.6738 | 7981388.6738 | 62.4274 | 62.1649 | 1.0017 | 0.99795 | 685377.3284 | 889885.1782 | 461.0067 | 0.48951 | 0 | 0 | 30.4736 | 25.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017904 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.5746 | 1368.1013 | 53.9612 | 43.7359 | 31.0811 | 1787.0252 | 80.741 | 24.8251 | 460.6334 | 0.0062377 | 59.9971 | 0.53933 | 0.45298 | 89.7886 | 2.2446 | 0.13907 | 0.14954 | 4.6867 | 0.72426 | 0.26382 | 0 | 100 | 583.1 | 316 | 110.65 | 105.6 | 101.41 | 309.8 | 3 | 93.23 | 42.76 | 4 | 37.98 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.88 | 0 | 38.7 | 60 | 60 | 104.88 | 90.21 | 85.99 | 0 | 101.41 | 2.31 | 92.31 | 43.48 | 110.65 | 12.37 | 105.6 | 110 | 0 | 15667 | 81.5 | 115.46 | 220.83 | 214.7 | 220.15 | 0 | 34.74 | 50.93 | 14096 | 93.23 | 42.76 | 37.98 | 0.99 | 42.76 | 0 | 606 | 431.7 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.5 | 316.3 | 0 | 310 | 101.3 | 15666 | 15667 | 316
03/26/22 10:45:26.192 | 579.8797 | 1368.3045 | 54.3337 | 44.1909 | 10.1428 | 30.6365 | 51.038 | 0 | 1787.2282 | 91.2748 | 82.3216 | 8.9532 | 25.4338 | 70.2276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0171 | 461.9901 | 458.7501 | 462.2801 | 414.7701 | 442.8201 | 421.4201 | 316.1901 | 0.54527 | 0.84191 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6985494.7934 | 7996769.021 | 7996769.021 | 62.4274 | 62.1648 | 1.0017 | 0.99795 | 684896.4778 | 891735.0023 | 461.0067 | 0.48951 | 0 | 0 | 30.6365 | 25.4338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017897 | 0.011584 | 0.004474 | 0.011584 | 0.0119 | 584.5484 | 1368.0992 | 53.9645 | 43.7397 | 31.0793 | 1786.9996 | 80.7541 | 24.8279 | 460.6352 | 0.0062417 | 59.9974 | 0.53937 | 0.45762 | 89.8012 | 2.2442 | 0.14071 | 0.15236 | 4.6728 | 0.73139 | 0.26527 | 0 | 100 | 583.4 | 315 | 110.7 | 105.6 | 101.46 | 307.6 | 3 | 93.26 | 42.79 | 4 | 38 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.88 | 0 | 38.73 | 60 | 60 | 104.85 | 90.19 | 86.07 | 0 | 101.46 | 2.31 | 92.31 | 43.51 | 110.7 | 12.34 | 105.6 | 110 | 0 | 15666 | 81.52 | 115.46 | 220.95 | 214.7 | 220.27 | 0 | 34.84 | 51.09 | 14102 | 93.26 | 42.79 | 38 | 0.96 | 42.79 | 0 | 606 | 435.3 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.4 | 315.2 | 0 | 309 | 101.46 | 15668 | 15666 | 317
03/26/22 10:45:31.192 | 579.604 | 1367.8297 | 54.3457 | 44.2042 | 10.1415 | 30.765 | 51.0279 | 0 | 1788.9623 | 91.2914 | 82.3389 | 8.9526 | 25.189 | 70.1937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0171 | 461.9901 | 458.7501 | 462.2801 | 414.7701 | 442.8201 | 421.4201 | 316.1901 | 0.54553 | 0.71596 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6982289.7071 | 8003665.2856 | 8003665.2856 | 62.4274 | 62.1646 | 1.0017 | 0.99795 | 684658.2731 | 892597.7789 | 461.0067 | 0.48951 | 0 | 0 | 30.765 | 25.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.01789 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.5217 | 1368.0969 | 53.9679 | 43.7436 | 31.0777 | 1786.9969 | 80.7673 | 24.829 | 460.6371 | 0.0062458 | 59.9976 | 0.53941 | 0.46077 | 89.8138 | 2.2443 | 0.14248 | 0.1553 | 4.6716 | 0.73846 | 0.2667 | 0 | 100 | 582.9 | 314 | 110.65 | 105.6 | 101.37 | 308.8 | 3 | 93.23 | 42.81 | 4 | 38.02 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.85 | 0 | 38.75 | 60 | 60 | 104.93 | 90.23 | 86.05 | 0 | 101.37 | 2.31 | 92.3 | 43.53 | 110.63 | 12.38 | 105.6 | 110 | 0 | 15665 | 81.52 | 115.46 | 220.95 | 214.7 | 220.27 | 0 | 34.96 | 51.29 | 14106 | 93.22 | 42.81 | 38.02 | 0.94 | 42.81 | 0 | 606 | 432.8 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.1 | 316.7 | 0 | 310.4 | 101.41 | 15665 | 15665 | 316
03/26/22 10:45:36.193 | 580.2589 | 1369.3677 | 54.3683 | 44.2269 | 10.1414 | 30.7706 | 51.0209 | 0 | 1794.7013 | 91.3209 | 82.3681 | 8.9528 | 25.4587 | 70.1979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.011 | 462.07 | 458.81 | 462.41 | 414.52 | 443.14 | 421.43 | 316.26 | 0.54503 | 0.52711 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6989941.9427 | 8026576.6507 | 8026576.6507 | 62.4273 | 62.1644 | 1.0017 | 0.99795 | 685453.0962 | 895071.5679 | 461.0967 | 0.49592 | 0 | 0 | 30.7706 | 25.4587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017883 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.4952 | 1368.0993 | 53.9714 | 43.7475 | 31.0766 | 1787.0106 | 80.7806 | 24.831 | 460.6392 | 0.0062503 | 59.9977 | 0.53945 | 0.46287 | 89.8265 | 2.2455 | 0.14448 | 0.15842 | 4.6883 | 0.74553 | 0.26841 | 0 | 100 | 583 | 316 | 110.58 | 105.6 | 101.39 | 309.9 | 3 | 93.19 | 42.84 | 4 | 38.05 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.83 | 0 | 38.76 | 60 | 60 | 104.85 | 90.19 | 86.03 | 0 | 101.39 | 2.31 | 92.29 | 43.54 | 110.58 | 12.39 | 105.6 | 110 | 0 | 15663 | 81.55 | 115.5 | 220.95 | 214.81 | 220.27 | 0 | 35.09 | 51.39 | 14111 | 93.19 | 42.84 | 38.05 | 0.91 | 42.84 | 0 | 606 | 431.9 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 316.2 | 0 | 309.9 | 101.39 | 15661 | 15663 | 316
03/26/22 10:45:41.192 | 580.6972 | 1370.276 | 54.3811 | 44.2385 | 10.1426 | 31.1085 | 51.0079 | 0 | 1792.3376 | 91.336 | 82.3817 | 8.9544 | 24.6311 | 70.2181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0111 | 462.0701 | 458.8101 | 462.4101 | 414.5201 | 443.1401 | 421.4301 | 316.2601 | 0.54462 | 0.6863 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6995758.8921 | 8019653.811 | 8019653.811 | 62.4273 | 62.1642 | 1.0017 | 0.99795 | 685881.1417 | 894275.8173 | 461.0967 | 0.49592 | 0 | 0 | 31.1085 | 24.6311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017888 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.4701 | 1368.1028 | 53.9749 | 43.7515 | 31.072 | 1787.0535 | 80.794 | 24.8342 | 460.6418 | 0.0062558 | 59.9979 | 0.53949 | 0.46351 | 89.8393 | 2.2484 | 0.14667 | 0.16169 | 4.7016 | 0.75253 | 0.27057 | 0 | 100 | 583.1 | 315 | 110.48 | 105.58 | 101.41 | 309 | 3 | 93.14 | 42.86 | 4 | 38.07 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.78 | 0 | 38.78 | 60 | 60 | 104.85 | 90.18 | 86.07 | 0 | 101.41 | 2.31 | 92.26 | 43.55 | 110.45 | 12.45 | 105.58 | 110 | 0 | 15662 | 81.57 | 115.53 | 220.95 | 214.81 | 220.27 | 0 | 35.13 | 51.31 | 14116 | 93.13 | 42.86 | 38.07 | 0.89 | 42.86 | 0 | 607 | 433.3 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.5 | 314.4 | 0 | 308.1 | 101.48 | 15662 | 15662 | 316
03/26/22 10:45:46.192 | 580.8567 | 1370.5444 | 54.3895 | 44.2461 | 10.1434 | 31.388 | 51.0112 | 0 | 1789.7984 | 91.3456 | 82.39 | 8.9556 | 23.7825 | 70.2049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0101 | 462.0801 | 458.8401 | 462.4401 | 414.4201 | 443.1801 | 421.4701 | 316.2701 | 0.54449 | 0.85398 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6997924.6022 | 8008398.7659 | 8008398.7659 | 62.4272 | 62.1641 | 1.0017 | 0.99795 | 686015.0854 | 893007.7261 | 461.1201 | 0.49445 | 0 | 0 | 31.388 | 23.7825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017887 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.4498 | 1368.1173 | 53.9785 | 43.7555 | 31.0684 | 1787.0915 | 80.8075 | 24.8332 | 460.6446 | 0.006262 | 59.998 | 0.53953 | 0.46518 | 89.8522 | 2.2557 | 0.14891 | 0.16494 | 4.6959 | 0.75932 | 0.27289 | 0 | 100 | 582.9 | 315 | 110.6 | 105.56 | 101.37 | 307.6 | 3 | 93.21 | 42.86 | 4 | 38.07 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 108.95 | 0 | 38.78 | 60 | 60 | 105 | 90.27 | 86.11 | 0 | 101.37 | 2.31 | 92.35 | 43.55 | 110.7 | 12.3 | 105.56 | 110 | 0 | 15660 | 81.57 | 115.53 | 221.07 | 214.81 | 220.39 | 0 | 35.1 | 51.15 | 14121 | 93.26 | 42.85 | 38.06 | 0.9 | 42.85 | 0 | 606 | 432.1 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 313.2 | 0 | 307 | 101.22 | 15661 | 15660 | 314
03/26/22 10:45:51.192 | 579.4602 | 1367.6542 | 54.4046 | 44.2641 | 10.1405 | 31.2388 | 51.031 | 0 | 1786.7689 | 91.3658 | 82.412 | 8.9539 | 24.5238 | 70.2041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.009 | 462.09 | 458.89 | 462.5 | 413.73 | 442.73 | 420.98 | 315.87 | 0.54511 | 0.81546 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6980977.1399 | 7994133.104 | 7994133.104 | 62.4272 | 62.1639 | 1.0017 | 0.99795 | 684567.7568 | 891493.0717 | 461.16 | 0.49224 | 0 | 0 | 31.2388 | 24.5238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017895 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.4209 | 1368.1129 | 53.9821 | 43.7596 | 31.0699 | 1787.1435 | 80.821 | 24.8293 | 460.6477 | 0.0062686 | 59.9982 | 0.53957 | 0.46514 | 89.8652 | 2.2558 | 0.15129 | 0.16835 | 4.6396 | 0.76607 | 0.27538 | 0 | 100 | 579.9 | 314 | 110.88 | 105.62 | 100.85 | 306.3 | 3 | 93.35 | 42.75 | 4 | 37.96 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.13 | 0 | 38.7 | 60 | 60 | 105.18 | 90.37 | 86.13 | 0 | 100.85 | 2.32 | 92.44 | 43.48 | 110.88 | 12.27 | 105.62 | 110 | 0 | 15659 | 81.59 | 115.53 | 221.07 | 214.81 | 220.39 | 0 | 34.98 | 50.79 | 14127 | 93.35 | 42.75 | 37.96 | 1 | 42.75 | 0 | 606 | 429.8 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 314.6 | 0 | 308.3 | 100.82 | 15659 | 15659 | 316
03/26/22 10:45:56.192 | 579.0367 | 1367.7523 | 54.4085 | 44.2762 | 10.1323 | 31.2414 | 51.025 | 0 | 1784.7922 | 91.3779 | 82.4303 | 8.9476 | 24.4194 | 70.1834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.009 | 462.09 | 458.89 | 462.5 | 413.73 | 442.73 | 420.98 | 315.87 | 0.54551 | 0.92416 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6975898.7485 | 7979605.4385 | 7979605.4385 | 62.4272 | 62.1637 | 1.0017 | 0.99795 | 684616.6603 | 890504.2459 | 461.16 | 0.49224 | 0 | 0 | 31.2414 | 24.4194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017901 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.3851 | 1368.0987 | 53.9857 | 43.7637 | 31.0717 | 1787.1424 | 80.8347 | 24.8255 | 460.651 | 0.0062758 | 59.9984 | 0.53961 | 0.46725 | 89.8783 | 2.2499 | 0.15364 | 0.17183 | 4.6401 | 0.77272 | 0.27793 | 0 | 100 | 578.6 | 315 | 110.98 | 105.7 | 100.63 | 305.7 | 3 | 93.4 | 42.69 | 4 | 37.9 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.28 | 0 | 38.63 | 60 | 60 | 105.25 | 90.41 | 86.17 | 0 | 100.7 | 2.32 | 92.52 | 43.41 | 111 | 12.29 | 105.7 | 110 | 0 | 15659 | 81.59 | 115.53 | 221.07 | 214.92 | 220.39 | 0 | 34.82 | 50.51 | 14132 | 93.41 | 42.69 | 37.9 | 1.06 | 42.69 | 0 | 607 | 429.4 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 314.4 | 0 | 308.2 | 100.68 | 15658 | 15659 | 316
03/26/22 10:46:01.192 | 578.9868 | 1371.0863 | 54.4045 | 44.2977 | 10.1068 | 31.7542 | 51.0178 | 0 | 1784.3226 | 91.4015 | 82.4737 | 8.9278 | 23.6921 | 70.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.013 | 462.1 | 458.92 | 462.53 | 412.92 | 441.98 | 420.25 | 315.32 | 0.54461 | 1.1585 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6975819.4436 | 7958992.3101 | 7958992.3101 | 62.4272 | 62.1633 | 1.0017 | 0.99795 | 686285.6511 | 890263.7921 | 461.1834 | 0.49077 | 0 | 0 | 31.7542 | 23.6921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017899 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.353 | 1368.1098 | 53.9893 | 43.7679 | 31.0742 | 1787.1105 | 80.8485 | 24.8193 | 460.6544 | 0.006283 | 59.9985 | 0.53965 | 0.47279 | 89.8914 | 2.2621 | 0.15583 | 0.1755 | 4.6385 | 0.77956 | 0.28041 | 0 | 100 | 578.9 | 314 | 111.18 | 105.76 | 100.7 | 306.5 | 3 | 93.5 | 42.68 | 4 | 37.9 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.4 | 0 | 38.61 | 60 | 60 | 105.43 | 90.5 | 86.19 | 0 | 100.7 | 2.33 | 92.59 | 43.39 | 111.18 | 12.26 | 105.76 | 110 | 0 | 15659 | 81.61 | 115.5 | 221.07 | 214.92 | 220.39 | 0 | 34.73 | 50.45 | 14136 | 93.5 | 42.68 | 37.89 | 1.07 | 42.68 | 0 | 607 | 428.4 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 312.7 | 0 | 306.5 | 100.68 | 15660 | 15659 | 314
03/26/22 10:46:06.192 | 575.9304 | 1366.1782 | 54.3963 | 44.3067 | 10.0896 | 31.708 | 51.0318 | 0 | 1782.1549 | 91.4161 | 82.5014 | 8.9147 | 23.8176 | 70.1772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.007 | 462.06 | 458.9 | 462.51 | 412.5 | 441.5 | 419.85 | 314.98 | 0.54691 | 0.96705 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6939001.7106 | 7937782.3568 | 7937782.3568 | 62.4271 | 62.1631 | 1.0017 | 0.99795 | 683829.3145 | 889178.3789 | 461.1567 | 0.48935 | 0 | 0 | 31.708 | 23.8176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017905 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.3111 | 1368.1099 | 53.9929 | 43.7722 | 31.0747 | 1787.083 | 80.8625 | 24.8164 | 460.6583 | 0.0062916 | 59.9987 | 0.5397 | 0.47726 | 89.9046 | 2.2621 | 0.15783 | 0.17916 | 4.6516 | 0.7864 | 0.28282 | 0 | 100 | 578.3 | 316 | 111.23 | 105.82 | 100.57 | 306.7 | 3 | 93.53 | 42.65 | 4 | 37.86 | 43.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.48 | 0 | 38.58 | 60 | 60 | 105.48 | 90.53 | 86.36 | 0 | 100.57 | 2.33 | 92.63 | 43.36 | 111.23 | 12.29 | 105.82 | 110 | 0 | 15659 | 81.63 | 115.5 | 221.07 | 214.92 | 220.39 | 0 | 34.67 | 50.45 | 14141 | 93.53 | 42.65 | 37.86 | 1.06 | 42.65 | 0 | 607 | 431 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 313 | 0 | 306.7 | 100.57 | 15659 | 15659 | 316
03/26/22 10:46:11.192 | 574.4753 | 1365.1356 | 54.3846 | 44.3135 | 10.071 | 31.3395 | 51.0359 | 0 | 1780.7718 | 91.4328 | 82.5319 | 8.9009 | 24.2011 | 70.1974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.007 | 462.06 | 458.9 | 462.51 | 412.5 | 441.5 | 419.85 | 314.98 | 0.54829 | 0.94577 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6921213.0844 | 7920701.4352 | 7920701.4352 | 62.4272 | 62.1629 | 1.0017 | 0.99795 | 683039.209 | 888240.4754 | 461.1567 | 0.48935 | 0 | 0 | 31.3395 | 24.2011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017907 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.2585 | 1368.0983 | 53.9964 | 43.7765 | 31.0729 | 1787.0611 | 80.8767 | 24.8161 | 460.6625 | 0.0063005 | 59.999 | 0.53975 | 0.48049 | 89.918 | 2.272 | 0.15953 | 0.1828 | 4.672 | 0.79337 | 0.28466 | 0 | 100 | 578 | 315 | 111.25 | 105.84 | 100.52 | 306.5 | 3 | 93.54 | 42.63 | 4 | 37.84 | 43.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.53 | 0 | 38.55 | 60 | 60 | 105.53 | 90.55 | 86.44 | 0 | 100.52 | 2.33 | 92.65 | 43.33 | 111.25 | 12.3 | 105.84 | 110 | 0 | 15659 | 81.65 | 115.5 | 221.19 | 214.92 | 220.39 | 0 | 34.75 | 50.67 | 14146 | 93.54 | 42.63 | 37.84 | 1.07 | 42.63 | 0 | 606 | 430.6 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 312.4 | 0 | 306.1 | 100.49 | 15658 | 15659 | 313
03/26/22 10:46:16.192 | 573.8877 | 1369.0993 | 54.3527 | 44.3204 | 10.0323 | 30.4763 | 51.0213 | 0 | 1787.6308 | 91.4699 | 82.5991 | 8.8707 | 25.7547 | 70.1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.008 | 461.99 | 458.83 | 462.45 | 411.76 | 440.7 | 419.02 | 314.35 | 0.54776 | 0.77936 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6913464.9274 | 7925155.9278 | 7925155.9278 | 62.4272 | 62.1623 | 1.0017 | 0.99795 | 685293.4453 | 891896.6317 | 461.09 | 0.49014 | 0 | 0 | 30.4763 | 25.7547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017895 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.1919 | 1368.0618 | 53.9998 | 43.7808 | 31.074 | 1787.0526 | 80.891 | 24.8127 | 460.6666 | 0.0063095 | 59.9992 | 0.53981 | 0.48165 | 89.9313 | 2.2466 | 0.16103 | 0.18636 | 4.6794 | 0.80036 | 0.28602 | 0 | 100 | 578.3 | 316 | 111.28 | 105.88 | 100.57 | 306 | 3 | 93.55 | 42.64 | 4 | 37.85 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.58 | 0 | 38.55 | 60 | 60 | 105.55 | 90.57 | 86.66 | 0 | 100.57 | 2.33 | 92.68 | 43.33 | 111.28 | 12.32 | 105.88 | 110 | 0 | 15659 | 81.65 | 115.53 | 221.19 | 214.92 | 220.51 | 0 | 34.78 | 50.67 | 14152 | 93.55 | 42.64 | 37.85 | 1.02 | 42.64 | 0 | 606 | 427.9 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 313.5 | 0 | 307.2 | 100.57 | 15659 | 15659 | 317
03/26/22 10:46:21.192 | 573.2057 | 1369.249 | 54.34 | 44.3207 | 10.0193 | 30.6851 | 51.0287 | 0 | 1791.9196 | 91.4831 | 82.6231 | 8.86 | 25.5519 | 70.1979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.008 | 461.99 | 458.83 | 462.45 | 411.76 | 440.7 | 419.02 | 314.35 | 0.54841 | 0.54979 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6905467.2776 | 7934330.9 | 7934330.9 | 62.4272 | 62.1621 | 1.0017 | 0.99795 | 685368.9469 | 894033.0195 | 461.09 | 0.49014 | 0 | 0 | 30.6851 | 25.5519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017887 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.1195 | 1368.0406 | 54.003 | 43.7851 | 31.0684 | 1787.0556 | 80.9055 | 24.8215 | 460.6707 | 0.0063182 | 59.9994 | 0.53987 | 0.48268 | 89.9448 | 2.2169 | 0.16204 | 0.18985 | 4.6823 | 0.80789 | 0.28685 | 0 | 100 | 578.3 | 313 | 111.23 | 105.9 | 100.57 | 305 | 3 | 93.53 | 42.64 | 4 | 37.85 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.53 | 0 | 38.56 | 60 | 60 | 105.5 | 90.54 | 86.74 | 0 | 100.57 | 2.33 | 92.65 | 43.35 | 111.18 | 12.39 | 105.9 | 110 | 0 | 15659 | 81.67 | 115.53 | 221.19 | 215.03 | 220.51 | 0 | 34.82 | 50.83 | 14157 | 93.5 | 42.64 | 37.85 | 1 | 42.64 | 0 | 606 | 427.4 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 311.8 | 0 | 305.5 | 100.64 | 15658 | 15659 | 316
03/26/22 10:46:26.191 | 570.9305 | 1368.5316 | 54.3013 | 44.3166 | 9.9847 | 30.8148 | 51.0335 | 0 | 1794.2988 | 91.5216 | 82.69 | 8.8316 | 25.071 | 70.2264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 461.9601 | 458.7901 | 462.4301 | 411.4201 | 440.3601 | 418.5401 | 314.0401 | 0.55005 | 0.38986 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6878266.0171 | 7918881.9182 | 7918881.9182 | 62.4273 | 62.1615 | 1.0017 | 0.99795 | 685011.6135 | 895210.5606 | 461.0601 | 0.49234 | 0 | 0 | 30.8148 | 25.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017883 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 584.0425 | 1368.0231 | 54.006 | 43.7893 | 31.0643 | 1787.0776 | 80.9203 | 24.8289 | 460.6746 | 0.0063266 | 59.9996 | 0.53994 | 0.48306 | 89.9584 | 2.2014 | 0.16271 | 0.19315 | 4.7133 | 0.81565 | 0.28733 | 0 | 100 | 578.3 | 316 | 111.3 | 105.9 | 100.57 | 308.2 | 3 | 93.57 | 42.64 | 4 | 37.85 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.55 | 0 | 38.56 | 60 | 60 | 105.53 | 90.55 | 86.94 | 0 | 100.47 | 2.33 | 92.66 | 43.33 | 111.28 | 12.34 | 105.9 | 110 | 0 | 15659 | 81.69 | 115.58 | 221.19 | 215.03 | 220.51 | 0 | 34.97 | 51.08 | 14162 | 93.55 | 42.64 | 37.85 | 1 | 42.64 | 0 | 606 | 429.8 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 312.6 | 0 | 306.3 | 100.61 | 15659 | 15659 | 315
03/26/22 10:46:31.193 | 570.6595 | 1368.6967 | 54.2899 | 44.3146 | 9.9753 | 30.8524 | 51.0331 | 0 | 1793.4318 | 91.5327 | 82.7088 | 8.8239 | 24.7925 | 70.2173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 461.9601 | 458.7901 | 462.4301 | 411.4201 | 440.3601 | 418.5401 | 314.0401 | 0.55031 | 0.42519 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6875032.112 | 7912864.2006 | 7912864.2006 | 62.4273 | 62.1615 | 1.0017 | 0.99795 | 685053.2337 | 894992.7476 | 461.0601 | 0.49234 | 0 | 0 | 30.8524 | 24.7925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.01789 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 583.9655 | 1368.0185 | 54.0089 | 43.7935 | 31.0646 | 1787.1151 | 80.9352 | 24.8252 | 460.6785 | 0.006335 | 59.9997 | 0.54 | 0.48335 | 89.972 | 2.199 | 0.1631 | 0.19628 | 4.7369 | 0.8237 | 0.28777 | 0 | 100 | 578.5 | 314 | 111.33 | 105.9 | 100.61 | 304.7 | 3 | 93.57 | 42.64 | 4 | 37.85 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.58 | 0 | 38.56 | 60 | 60 | 105.53 | 90.55 | 87.1 | 0 | 100.61 | 2.33 | 92.68 | 43.35 | 111.3 | 12.33 | 105.9 | 110 | 0 | 15659 | 81.72 | 115.6 | 221.19 | 215.03 | 220.51 | 0 | 35.17 | 51.3 | 14166 | 93.57 | 42.65 | 37.86 | 0.99 | 42.65 | 0 | 606 | 430.5 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 312.3 | 0 | 306 | 100.61 | 15658 | 15659 | 315
03/26/22 10:46:36.191 | 569.0099 | 1371.1018 | 54.2318 | 44.2996 | 9.9323 | 30.9495 | 51.037 | 0 | 1789.3855 | 91.5907 | 82.8035 | 8.7872 | 24.4727 | 70.2358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.013 | 461.92 | 458.72 | 462.39 | 411.39 | 440.16 | 418.17 | 313.88 | 0.55162 | 0.88339 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6855388.5075 | 7856779.4721 | 7856779.4721 | 62.4274 | 62.1606 | 1.0017 | 0.99794 | 686301.2463 | 892743.0952 | 461.01 | 0.49674 | 0 | 0 | 30.9495 | 24.4727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.01788 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 583.8883 | 1368.0403 | 54.0116 | 43.7977 | 31.0641 | 1787.1172 | 80.9504 | 24.8196 | 460.682 | 0.0063426 | 59.9999 | 0.54007 | 0.48773 | 89.9858 | 2.2105 | 0.16311 | 0.19915 | 4.7378 | 0.8323 | 0.28818 | 0 | 100 | 578.9 | 315 | 111.33 | 105.92 | 100.68 | 306.8 | 3 | 93.58 | 42.65 | 4 | 37.88 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.65 | 0 | 38.59 | 60 | 60 | 105.55 | 90.57 | 87.2 | 0 | 100.68 | 2.33 | 92.72 | 43.37 | 111.38 | 12.31 | 105.92 | 110 | 0 | 15659 | 81.74 | 115.65 | 221.19 | 215.03 | 220.51 | 0 | 35.37 | 51.46 | 14171 | 93.61 | 42.66 | 37.88 | 0.97 | 42.66 | 0 | 606 | 429.4 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 311.9 | 0 | 305.6 | 100.64 | 15660 | 15659 | 314
03/26/22 10:46:41.192 | 566.2685 | 1366.8852 | 54.2016 | 44.2868 | 9.9148 | 30.6926 | 51.0318 | 0 | 1789.7932 | 91.6281 | 82.8559 | 8.7722 | 25.0332 | 70.2276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.015 | 461.91 | 458.69 | 462.37 | 411.47 | 440.23 | 418.17 | 313.91 | 0.55435 | 0.60256 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6822181.8942 | 7845766.109 | 7845766.109 | 62.4275 | 62.1601 | 1.0017 | 0.99794 | 684192.0272 | 892939.049 | 460.99 | 0.49893 | 0 | 0 | 30.6926 | 25.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017882 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 583.8017 | 1368.0471 | 54.0141 | 43.8018 | 31.0637 | 1787.1228 | 80.9658 | 24.8138 | 460.6852 | 0.0063496 | 60 | 0.54014 | 0.49112 | 89.9997 | 2.2133 | 0.16289 | 0.20178 | 4.7406 | 0.8411 | 0.28857 | 0 | 100 | 578.7 | 316 | 111.33 | 105.92 | 100.64 | 304.9 | 3 | 93.58 | 42.66 | 4 | 37.88 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.68 | 0 | 38.59 | 60 | 60 | 105.55 | 90.57 | 87.26 | 0 | 100.64 | 2.33 | 92.73 | 43.37 | 111.33 | 12.32 | 105.92 | 110 | 0 | 15659 | 81.76 | 115.67 | 221.19 | 215.03 | 220.51 | 0 | 35.5 | 51.5 | 14176 | 93.59 | 42.66 | 37.88 | 0.96 | 42.66 | 0 | 606 | 427.9 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.4 | 312.4 | 0 | 306.1 | 100.59 | 15659 | 15659 | 315
03/26/22 10:46:46.191 | 564.8806 | 1364.9602 | 54.1783 | 44.2739 | 9.9044 | 30.1971 | 51.0267 | 0 | 1789.0242 | 91.6625 | 82.8989 | 8.7635 | 25.7033 | 70.2218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0181 | 461.9501 | 458.7101 | 462.3901 | 411.5501 | 440.2901 | 418.1701 | 313.9601 | 0.5558 | 0.51897 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6805053.9775 | 7835389.9716 | 7835389.9716 | 62.4275 | 62.1597 | 1.0017 | 0.99794 | 683229.4878 | 892549.2651 | 461.0167 | 0.50034 | 0 | 0 | 30.1971 | 25.7033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.01788 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 583.6993 | 1368.0344 | 54.0163 | 43.8058 | 31.062 | 1787.1167 | 80.9814 | 24.8154 | 460.6882 | 0.006356 | 60.0002 | 0.54023 | 0.49392 | 90.0137 | 2.2205 | 0.16251 | 0.20413 | 4.736 | 0.85028 | 0.28895 | 0 | 100 | 578.8 | 314 | 111.3 | 105.94 | 100.66 | 305.8 | 3 | 93.57 | 42.66 | 4 | 37.88 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.65 | 0 | 38.59 | 60 | 60 | 105.53 | 90.55 | 87.44 | 0 | 100.66 | 2.33 | 92.72 | 43.37 | 111.3 | 12.37 | 105.94 | 110 | 0 | 15659 | 81.78 | 115.72 | 221.19 | 215.03 | 220.51 | 0 | 35.58 | 51.4 | 14181 | 93.57 | 42.66 | 37.88 | 0.96 | 42.66 | 0 | 606 | 430.2 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.4 | 313.3 | 0 | 307 | 100.77 | 15658 | 15659 | 315
03/26/22 10:46:51.191 | 564.8422 | 1365.466 | 54.1633 | 44.2633 | 9.9001 | 30.0016 | 51.0296 | 0 | 1790.2061 | 91.6889 | 82.9286 | 8.7603 | 25.9445 | 70.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.018 | 461.95 | 458.71 | 462.39 | 411.55 | 440.29 | 418.17 | 313.96 | 0.55584 | 0.48149 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6804432.1847 | 7837878.2869 | 7837878.2869 | 62.4276 | 62.1594 | 1.0017 | 0.99794 | 683483.3305 | 893134.673 | 461.0167 | 0.50034 | 0 | 0 | 30.0016 | 25.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017872 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 583.5895 | 1368.0186 | 54.0184 | 43.8096 | 31.0571 | 1787.1375 | 80.9973 | 24.8228 | 460.6911 | 0.0063622 | 60.0003 | 0.54033 | 0.49466 | 90.0279 | 2.2286 | 0.16198 | 0.20616 | 4.7414 | 0.85981 | 0.28963 | 0 | 100 | 578.7 | 316 | 111.28 | 105.94 | 100.68 | 306.3 | 3 | 93.55 | 42.68 | 4 | 37.89 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.65 | 0 | 38.59 | 60 | 60 | 105.53 | 90.55 | 87.48 | 0 | 100.68 | 2.33 | 92.72 | 43.37 | 111.3 | 12.37 | 105.94 | 110 | 0 | 15659 | 81.8 | 115.74 | 221.19 | 215.03 | 220.51 | 0 | 35.7 | 51.57 | 14186 | 93.57 | 42.68 | 37.89 | 0.94 | 42.68 | 0 | 607 | 430.7 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 314.1 | 0 | 307.8 | 100.68 | 15656 | 15659 | 315
03/26/22 10:46:56.191 | 564.7671 | 1366.1472 | 54.1408 | 44.244 | 9.8969 | 31.6626 | 51.0186 | 0 | 1793.4575 | 91.7365 | 82.9775 | 8.7591 | 23.9375 | 70.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.02 | 462 | 458.75 | 462.42 | 411.58 | 440.29 | 418.18 | 313.99 | 0.55596 | 0.37708 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6804756.3352 | 7846491.0867 | 7846491.0867 | 62.4276 | 62.1589 | 1.0017 | 0.99794 | 683600.4772 | 894462.1556 | 461.0567 | 0.5003 | 0 | 0 | 31.6626 | 23.9375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.01787 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 583.4823 | 1368.0128 | 54.0203 | 43.8134 | 31.0584 | 1787.1911 | 81.0134 | 24.8222 | 460.694 | 0.0063686 | 60.0005 | 0.54042 | 0.49438 | 90.0423 | 2.2333 | 0.16136 | 0.2079 | 4.7515 | 0.86951 | 0.29065 | 0 | 100 | 579 | 317 | 111.35 | 105.94 | 100.7 | 307.7 | 3 | 93.59 | 42.68 | 4 | 37.89 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.65 | 0 | 38.59 | 60 | 60 | 105.55 | 90.57 | 87.59 | 0 | 100.7 | 2.33 | 92.72 | 43.37 | 111.35 | 12.34 | 105.94 | 110 | 0 | 15659 | 81.82 | 115.77 | 221.19 | 215.03 | 220.51 | 0 | 36 | 51.91 | 14191 | 93.59 | 42.68 | 37.89 | 0.96 | 42.68 | 0 | 607 | 429.2 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 312.4 | 0 | 306.2 | 100.68 | 15658 | 15659 | 313
03/26/22 10:47:01.191 | 566.1064 | 1368.8825 | 54.1283 | 44.2309 | 9.8974 | 31.2238 | 51.0316 | 0 | 1788.4359 | 91.7716 | 83.0105 | 8.7611 | 24.0739 | 70.2986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.017 | 462.08 | 458.79 | 462.46 | 411.72 | 440.33 | 418.19 | 314.06 | 0.55477 | 0.80758 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6820743.2131 | 7828641.9942 | 7828641.9942 | 62.4277 | 62.1585 | 1.0017 | 0.99794 | 685195.0643 | 892239.823 | 461.11 | 0.50313 | 0 | 0 | 31.2238 | 24.0739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017877 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 583.384 | 1368.0332 | 54.0222 | 43.8171 | 31.0624 | 1787.236 | 81.0296 | 24.8167 | 460.697 | 0.0063749 | 60.0007 | 0.54051 | 0.49587 | 90.0569 | 2.2199 | 0.16071 | 0.20946 | 4.7445 | 0.87915 | 0.29162 | 0 | 100 | 579.2 | 315 | 111.4 | 105.96 | 100.73 | 305.4 | 3 | 93.62 | 42.69 | 4 | 37.9 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.73 | 0 | 38.6 | 60 | 60 | 105.63 | 90.6 | 87.65 | 0 | 100.73 | 2.33 | 92.76 | 43.38 | 111.4 | 12.34 | 105.96 | 110 | 0 | 15659 | 81.82 | 115.79 | 221.19 | 215.03 | 220.51 | 0 | 36.31 | 52.06 | 14196 | 93.62 | 42.69 | 37.9 | 0.95 | 42.69 | 0 | 607 | 430 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 311.6 | 0 | 305.4 | 100.73 | 15658 | 15659 | 315
03/26/22 10:47:06.191 | 565.7055 | 1367.7058 | 54.1194 | 44.2207 | 9.8986 | 31.6016 | 51.0399 | 0 | 1786.6089 | 91.8028 | 83.0378 | 8.7651 | 23.741 | 70.2615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.012 | 462.11 | 458.78 | 462.47 | 411.77 | 440.38 | 418.17 | 314.07 | 0.55518 | 0.83216 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6816036.3526 | 7822287.6662 | 7822287.6662 | 62.4277 | 62.1582 | 1.0017 | 0.99794 | 684637.401 | 891253.0839 | 461.12 | 0.50746 | 0 | 0 | 31.6016 | 23.741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017877 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 583.2759 | 1368.0296 | 54.024 | 43.8207 | 31.0705 | 1787.2191 | 81.0459 | 24.8029 | 460.7 | 0.0063814 | 60.0008 | 0.5406 | 0.49973 | 90.0715 | 2.2198 | 0.16005 | 0.21082 | 4.7417 | 0.88888 | 0.29308 | 0 | 100 | 578.6 | 317 | 111.43 | 105.96 | 100.63 | 306.6 | 3 | 93.63 | 42.69 | 4 | 37.9 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.73 | 0 | 38.6 | 60 | 60 | 105.6 | 90.59 | 87.73 | 0 | 100.63 | 2.33 | 92.76 | 43.38 | 111.4 | 12.34 | 105.96 | 110 | 0 | 15659 | 81.84 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.55 | 52.12 | 14201 | 93.62 | 42.69 | 37.9 | 0.95 | 42.69 | 0 | 607 | 427.3 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 312.2 | 0 | 305.9 | 100.64 | 15658 | 15659 | 316
03/26/22 10:47:11.191 | 566.084 | 1368.5987 | 54.1172 | 44.2182 | 9.899 | 31.8724 | 51.044 | 0 | 1786.6966 | 91.812 | 83.0454 | 8.7666 | 23.5573 | 70.2561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 462.1101 | 458.7801 | 462.4701 | 411.7701 | 440.3801 | 418.1701 | 314.0701 | 0.55481 | 0.8577 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6821039.5049 | 7825284.0016 | 7825284.0016 | 62.4277 | 62.1581 | 1.0017 | 0.99794 | 685053.4803 | 891367.1434 | 461.1201 | 0.50746 | 0 | 0 | 31.8724 | 23.5573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.01789 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 583.1699 | 1368.0316 | 54.0257 | 43.8243 | 31.0767 | 1787.1989 | 81.0623 | 24.7932 | 460.7032 | 0.0063882 | 60.0009 | 0.5407 | 0.50395 | 90.0863 | 2.2202 | 0.15938 | 0.21207 | 4.7361 | 0.89839 | 0.29452 | 0 | 100 | 578.6 | 315 | 111.45 | 105.96 | 100.63 | 307.9 | 3 | 93.64 | 42.69 | 4 | 37.9 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.8 | 0 | 38.6 | 60 | 60 | 105.65 | 90.62 | 87.79 | 0 | 100.63 | 2.34 | 92.79 | 43.38 | 111.48 | 12.3 | 105.96 | 110 | 0 | 15659 | 81.87 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.73 | 52.03 | 14206 | 93.66 | 42.69 | 37.9 | 0.93 | 42.69 | 0 | 606 | 429.1 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 311.6 | 0 | 305.4 | 100.68 | 15659 | 15659 | 316
03/26/22 10:47:16.191 | 566.3006 | 1369.0322 | 54.1116 | 44.2119 | 9.8996 | 30.9468 | 51.0351 | 0 | 1778.1758 | 91.8455 | 83.0744 | 8.7711 | 24.7656 | 70.2606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 462.16 | 458.8 | 462.51 | 411.84 | 440.54 | 418.11 | 314.13 | 0.55471 | 1.2909 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6822832.4433 | 7793259.3061 | 7793259.3061 | 62.4277 | 62.1578 | 1.0017 | 0.99794 | 685270.7433 | 887112.0734 | 461.1567 | 0.51103 | 0 | 0 | 30.9468 | 24.7656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017897 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 583.0653 | 1368.0382 | 54.0273 | 43.8279 | 31.08 | 1787.1394 | 81.0788 | 24.7865 | 460.7065 | 0.0063954 | 60.0011 | 0.54079 | 0.51049 | 90.1011 | 2.2197 | 0.1587 | 0.21322 | 4.7398 | 0.90772 | 0.29603 | 0 | 100 | 579.4 | 314 | 111.58 | 106 | 100.77 | 305.9 | 3 | 93.71 | 42.69 | 4 | 37.9 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.9 | 0 | 38.61 | 60 | 60 | 105.73 | 90.66 | 87.79 | 0 | 100.77 | 2.34 | 92.85 | 43.39 | 111.6 | 12.29 | 106.01 | 110 | 0 | 15659 | 81.89 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.79 | 51.75 | 14211 | 93.72 | 42.7 | 37.91 | 0.92 | 42.7 | 0 | 607 | 431.1 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579 | 311.1 | 0 | 304.9 | 100.7 | 15658 | 15659 | 317
03/26/22 10:47:21.191 | 566.7075 | 1369.8425 | 54.1106 | 44.2109 | 9.8997 | 30.6447 | 51.0413 | 0 | 1782.444 | 91.8575 | 83.0858 | 8.7717 | 25.2958 | 70.2705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 462.16 | 458.8 | 462.51 | 411.84 | 440.54 | 418.11 | 314.13 | 0.55431 | 1.1788 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6827524.6515 | 7806805.8577 | 7806805.8577 | 62.4277 | 62.1577 | 1.0017 | 0.99794 | 685756.4425 | 888550.1085 | 461.1567 | 0.51103 | 0 | 0 | 30.6447 | 25.2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017891 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 582.9633 | 1368.0519 | 54.029 | 43.8314 | 31.075 | 1787.1083 | 81.0954 | 24.7933 | 460.7099 | 0.0064029 | 60.0012 | 0.54088 | 0.51617 | 90.1159 | 2.2232 | 0.15803 | 0.21429 | 4.7521 | 0.91699 | 0.29764 | 0 | 100 | 579.3 | 316 | 111.65 | 106.05 | 100.75 | 304 | 3 | 93.75 | 42.71 | 4 | 37.93 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.9 | 0 | 38.63 | 60 | 60 | 105.73 | 90.66 | 87.85 | 0 | 100.73 | 2.34 | 92.85 | 43.41 | 111.65 | 12.31 | 106.05 | 110 | 0 | 15659 | 81.89 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.65 | 51.32 | 14216 | 93.75 | 42.71 | 37.93 | 0.91 | 42.71 | 0 | 606 | 429.7 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.4 | 313.4 | 0 | 307.1 | 100.77 | 15658 | 15659 | 316
03/26/22 10:47:26.191 | 566.0078 | 1368.1703 | 54.1114 | 44.2107 | 9.9007 | 30.5906 | 51.0219 | 0 | 1785.9844 | 91.8828 | 83.1092 | 8.7736 | 25.2954 | 70.2635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.007 | 462.16 | 458.8 | 462.53 | 411.89 | 440.63 | 418.13 | 314.17 | 0.55506 | 0.77233 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6818989.1968 | 7830271.4031 | 7830271.4031 | 62.4277 | 62.1574 | 1.0017 | 0.99794 | 684839.3247 | 891002.7175 | 461.1634 | 0.51247 | 0 | 0 | 30.5906 | 25.2954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017892 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 582.8588 | 1368.0611 | 54.0306 | 43.8349 | 31.0709 | 1787.0855 | 81.112 | 24.7988 | 460.7135 | 0.0064105 | 60.0013 | 0.54098 | 0.52068 | 90.1309 | 2.2271 | 0.15734 | 0.21529 | 4.75 | 0.92606 | 0.29922 | 0 | 100 | 579.8 | 316 | 111.6 | 106.07 | 100.85 | 307.8 | 3 | 93.72 | 42.74 | 4 | 37.95 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.85 | 0 | 38.65 | 60 | 60 | 105.7 | 90.64 | 87.92 | 0 | 100.82 | 2.33 | 92.82 | 43.43 | 111.58 | 12.35 | 106.07 | 110 | 0 | 15659 | 81.91 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.56 | 51.15 | 14221 | 93.72 | 42.74 | 37.95 | 0.9 | 42.74 | 0 | 607 | 432.5 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.8 | 314.1 | 0 | 307.8 | 100.83 | 15658 | 15659 | 315
03/26/22 10:47:31.191 | 566.0207 | 1368.0155 | 54.114 | 44.2119 | 9.9021 | 31.005 | 51.0409 | 0 | 1787.5017 | 91.9006 | 83.1257 | 8.7749 | 24.9698 | 70.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 462.0901 | 458.7501 | 462.5101 | 412.0201 | 440.9801 | 418.2801 | 314.3001 | 0.55528 | 0.68451 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6819504.8987 | 7837663.0161 | 7837663.0161 | 62.4277 | 62.1572 | 1.0017 | 0.99794 | 684761.7129 | 891757.3317 | 461.1167 | 0.51325 | 0 | 0 | 31.005 | 24.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017889 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 582.7538 | 1368.069 | 54.0323 | 43.8384 | 31.0729 | 1787.0825 | 81.1288 | 24.7966 | 460.717 | 0.0064181 | 60.0015 | 0.54107 | 0.52377 | 90.146 | 2.2242 | 0.15666 | 0.21625 | 4.7492 | 0.93502 | 0.30076 | 0 | 100 | 579.7 | 312 | 111.63 | 106.07 | 100.82 | 307.5 | 3 | 93.73 | 42.75 | 4 | 37.96 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.9 | 0 | 38.66 | 60 | 60 | 105.78 | 90.68 | 87.98 | 0 | 100.85 | 2.33 | 92.85 | 43.44 | 111.6 | 12.35 | 106.07 | 110 | 0 | 15659 | 81.93 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.59 | 51.15 | 14226 | 93.72 | 42.75 | 37.95 | 0.89 | 42.75 | 0 | 606 | 430.2 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.7 | 313.8 | 0 | 307.5 | 100.82 | 15657 | 15659 | 316
03/26/22 10:47:36.191 | 566.7927 | 1370.1366 | 54.117 | 44.2137 | 9.9032 | 31.5286 | 51.0376 | 0 | 1786.4437 | 91.9148 | 83.1396 | 8.7753 | 24.0359 | 70.2478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.018 | 462.09 | 458.75 | 462.53 | 412.07 | 441.15 | 418.35 | 314.37 | 0.55465 | 0.85595 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6829202.9492 | 7834293.1845 | 7834293.1845 | 62.4277 | 62.1571 | 1.0017 | 0.99794 | 685637.3663 | 891441.7162 | 461.1234 | 0.51469 | 0 | 0 | 31.5286 | 24.0359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.01789 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 582.6561 | 1368.0974 | 54.0339 | 43.8419 | 31.081 | 1787.055 | 81.1456 | 24.7833 | 460.7205 | 0.0064257 | 60.0017 | 0.54116 | 0.52971 | 90.1611 | 2.213 | 0.15598 | 0.21716 | 4.7359 | 0.94376 | 0.30172 | 0 | 100 | 580.3 | 317 | 111.63 | 106.07 | 100.92 | 306.5 | 3 | 93.75 | 42.75 | 4 | 37.96 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.9 | 0 | 38.66 | 60 | 60 | 105.78 | 90.68 | 88.08 | 0 | 100.92 | 2.33 | 92.85 | 43.44 | 111.63 | 12.34 | 106.07 | 110 | 0 | 15659 | 81.95 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.62 | 51.13 | 14231 | 93.73 | 42.75 | 37.96 | 0.9 | 42.75 | 0 | 606 | 432 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.3 | 315 | 0 | 308.7 | 100.92 | 15658 | 15659 | 315
03/26/22 10:47:41.191 | 567.7731 | 1371.8759 | 54.1228 | 44.218 | 9.9048 | 31.47 | 51.0234 | 0 | 1780.9318 | 91.935 | 83.1593 | 8.7757 | 23.9667 | 70.2548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.022 | 462.08 | 458.77 | 462.55 | 412.15 | 441.31 | 418.45 | 314.47 | 0.55387 | 1.3439 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6841020.7062 | 7808393.359 | 7808393.359 | 62.4277 | 62.1568 | 1.0017 | 0.99794 | 686693.6447 | 888474.9073 | 461.1334 | 0.51251 | 0 | 0 | 31.47 | 23.9667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016213 | 0.0179 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 582.5643 | 1368.1368 | 54.0356 | 43.8455 | 31.0855 | 1786.9836 | 81.1625 | 24.7754 | 460.7243 | 0.0064338 | 60.0019 | 0.54125 | 0.5394 | 90.1763 | 2.2124 | 0.15532 | 0.21804 | 4.7154 | 0.95239 | 0.30252 | 0 | 100 | 580 | 316 | 111.7 | 106.07 | 100.87 | 307.8 | 3 | 93.76 | 42.78 | 4 | 37.99 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.98 | 0 | 38.69 | 60 | 60 | 105.85 | 90.72 | 88.2 | 0 | 100.87 | 2.34 | 92.88 | 43.47 | 111.7 | 12.31 | 106.07 | 110 | 0 | 15659 | 81.95 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.65 | 51.13 | 14236 | 93.76 | 42.78 | 37.99 | 0.88 | 42.78 | 0 | 607 | 429.3 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 313.2 | 0 | 307 | 100.89 | 15658 | 15659 | 316
03/26/22 10:47:46.191 | 567.4912 | 1370.5856 | 54.1276 | 44.2217 | 9.9058 | 31.539 | 51.0285 | 0 | 1779.8067 | 91.9481 | 83.1724 | 8.7756 | 23.867 | 70.2602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.025 | 462.09 | 458.8 | 462.58 | 412.17 | 441.45 | 418.57 | 314.55 | 0.55428 | 1.3768 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6837554.9621 | 7802399.4894 | 7802399.4894 | 62.4277 | 62.1567 | 1.0017 | 0.99794 | 686295.6366 | 887788.5232 | 461.1567 | 0.51103 | 0 | 0 | 31.539 | 23.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016215 | 0.017903 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 582.4628 | 1368.1553 | 54.0372 | 43.8491 | 31.0853 | 1786.9198 | 81.1794 | 24.7751 | 460.7282 | 0.0064422 | 60.0022 | 0.54134 | 0.54719 | 90.1915 | 2.223 | 0.15467 | 0.2189 | 4.7378 | 0.96081 | 0.30326 | 0 | 100 | 580.3 | 316 | 111.83 | 106.09 | 100.92 | 307.9 | 3 | 93.84 | 42.79 | 4 | 38 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.08 | 0 | 38.7 | 60 | 60 | 105.9 | 90.75 | 88.22 | 0 | 100.96 | 2.34 | 92.92 | 43.48 | 111.83 | 12.26 | 106.09 | 110 | 0 | 15659 | 81.97 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.69 | 51.15 | 14241 | 93.84 | 42.79 | 38 | 0.87 | 42.79 | 0 | 607 | 427.4 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.3 | 314.2 | 0 | 307.9 | 100.92 | 15659 | 15659 | 316
03/26/22 10:47:51.191 | 565.8909 | 1366.7923 | 54.1348 | 44.2277 | 9.9071 | 31.0591 | 51.0219 | 0 | 1781.4892 | 91.9655 | 83.1906 | 8.7748 | 24.75 | 70.2829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0261 | 462.0701 | 458.8301 | 462.5901 | 412.1401 | 441.5801 | 418.7401 | 314.6201 | 0.55597 | 1.0161 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6818008.806 | 7811517.7751 | 7811517.7751 | 62.4277 | 62.1565 | 1.0017 | 0.99794 | 684277.7455 | 888808.2354 | 461.1634 | 0.50597 | 0 | 0 | 31.0591 | 24.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017907 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 582.3499 | 1368.1475 | 54.0389 | 43.8527 | 31.0858 | 1786.8798 | 81.1965 | 24.7747 | 460.7322 | 0.0064509 | 60.0025 | 0.54144 | 0.55213 | 90.2069 | 2.2244 | 0.15404 | 0.21975 | 4.7522 | 0.96905 | 0.3041 | 0 | 100 | 580.4 | 315 | 111.85 | 106.09 | 100.94 | 308.1 | 3 | 93.85 | 42.79 | 4 | 38 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.1 | 0 | 38.7 | 60 | 60 | 105.93 | 90.76 | 88.18 | 0 | 100.87 | 2.34 | 92.95 | 43.48 | 111.85 | 12.24 | 106.09 | 110 | 0 | 15659 | 81.99 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.72 | 51.13 | 14246 | 93.85 | 42.79 | 38 | 0.87 | 42.79 | 0 | 607 | 430.9 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.1 | 312.2 | 0 | 305.9 | 100.89 | 15659 | 15659 | 314
03/26/22 10:47:56.191 | 564.5874 | 1363.6854 | 54.1439 | 44.2355 | 9.9084 | 30.9757 | 51.0351 | 0 | 1782.3511 | 91.9857 | 83.2128 | 8.7729 | 24.6293 | 70.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0261 | 462.0701 | 458.8301 | 462.5901 | 412.1401 | 441.5801 | 418.7401 | 314.6201 | 0.55726 | 0.80235 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6802192.8827 | 7812781.9771 | 7812781.9771 | 62.4276 | 62.1563 | 1.0017 | 0.99794 | 682592.9611 | 889175.3198 | 461.1634 | 0.50597 | 0 | 0 | 30.9757 | 24.6293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017905 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 582.2338 | 1368.1334 | 54.0406 | 43.8563 | 31.0846 | 1786.8521 | 81.2137 | 24.7792 | 460.7364 | 0.0064599 | 60.0028 | 0.54155 | 0.55609 | 90.2223 | 2.2384 | 0.15345 | 0.22058 | 4.7699 | 0.97711 | 0.30483 | 0 | 100 | 580.3 | 314 | 111.88 | 106.11 | 100.92 | 307 | 3 | 93.86 | 42.79 | 4 | 38 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.18 | 0 | 38.7 | 60 | 60 | 105.95 | 90.78 | 88.28 | 0 | 100.92 | 2.34 | 92.99 | 43.48 | 111.9 | 12.25 | 106.11 | 110 | 0 | 15659 | 81.99 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.77 | 51.19 | 14251 | 93.86 | 42.79 | 38 | 0.87 | 42.79 | 0 | 607 | 431.4 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.9 | 314.6 | 0 | 308.4 | 100.85 | 15658 | 15659 | 316
03/26/22 10:48:01.190 | 565.0881 | 1364.697 | 54.1534 | 44.2435 | 9.9099 | 31.5574 | 51.0168 | 0 | 1787.0166 | 92.005 | 83.2345 | 8.7706 | 24.0361 | 70.1838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0191 | 462.0401 | 458.8601 | 462.6001 | 412.1701 | 441.8001 | 419.0501 | 314.7601 | 0.55701 | 0.66513 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6808731.7821 | 7830480.855 | 7830480.855 | 62.4276 | 62.156 | 1.0017 | 0.99794 | 683098.8661 | 891499.7627 | 461.1668 | 0.50018 | 0 | 0 | 31.5574 | 24.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017901 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 582.1154 | 1368.1158 | 54.0424 | 43.86 | 31.0877 | 1786.8607 | 81.231 | 24.7779 | 460.7406 | 0.0064689 | 60.0031 | 0.54166 | 0.55809 | 90.2378 | 2.2556 | 0.1529 | 0.22145 | 4.768 | 0.98511 | 0.30549 | 0 | 100 | 580.4 | 316 | 111.93 | 106.15 | 100.94 | 308.5 | 3 | 93.89 | 42.8 | 4 | 38.01 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.18 | 0 | 38.7 | 60 | 60 | 105.98 | 90.79 | 88.32 | 0 | 100.94 | 2.34 | 92.99 | 43.48 | 111.88 | 12.28 | 106.15 | 110 | 0 | 15659 | 82.01 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.83 | 51.19 | 14256 | 93.86 | 42.8 | 38.01 | 0.89 | 42.8 | 0 | 607 | 431.5 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.7 | 311.6 | 0 | 305.3 | 100.99 | 15659 | 15659 | 316
03/26/22 10:48:06.190 | 566.2814 | 1367.551 | 54.1628 | 44.2514 | 9.9114 | 31.2222 | 51.0225 | 0 | 1786.8154 | 92.0233 | 83.2529 | 8.7703 | 24.4079 | 70.1987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.012 | 462.03 | 458.88 | 462.59 | 412.19 | 441.84 | 419.14 | 314.8 | 0.55591 | 0.83175 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6822814.1322 | 7831409.5863 | 7831409.5863 | 62.4276 | 62.1559 | 1.0017 | 0.99794 | 684457.3484 | 891587.6295 | 461.1667 | 0.49584 | 0 | 0 | 31.2222 | 24.4079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017905 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 582.0061 | 1368.1202 | 54.0442 | 43.8637 | 31.089 | 1786.8853 | 81.2484 | 24.7777 | 460.7449 | 0.0064782 | 60.0033 | 0.54177 | 0.56071 | 90.2534 | 2.2534 | 0.15239 | 0.22233 | 4.7582 | 0.99293 | 0.306 | 0 | 100 | 580.8 | 315 | 111.93 | 106.17 | 101.1 | 308 | 3 | 93.89 | 42.81 | 4 | 38.02 | 43.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.2 | 0 | 38.73 | 60 | 60 | 106.03 | 90.82 | 88.3 | 0 | 101.1 | 2.34 | 93 | 43.51 | 111.93 | 12.28 | 106.17 | 110 | 0 | 15659 | 82.03 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 36.86 | 51.25 | 14261 | 93.89 | 42.81 | 38.02 | 0.9 | 42.81 | 0 | 606 | 431.4 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581 | 315.4 | 0 | 309.1 | 101.04 | 15660 | 15659 | 316
03/26/22 10:48:11.190 | 566.2309 | 1367.1639 | 54.1679 | 44.2558 | 9.9121 | 31.2745 | 51.0374 | 0 | 1785.3909 | 92.0329 | 83.2622 | 8.7707 | 24.358 | 70.2169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 462.0301 | 458.8801 | 462.5901 | 412.1901 | 441.8401 | 419.1401 | 314.8001 | 0.55596 | 0.9233 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6822247.4068 | 7823817.2611 | 7823817.2611 | 62.4276 | 62.1557 | 1.0017 | 0.99794 | 684333.0411 | 890684.765 | 461.1667 | 0.49584 | 0 | 0 | 31.2745 | 24.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017907 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 581.8929 | 1368.1161 | 54.046 | 43.8675 | 31.0905 | 1786.9023 | 81.2659 | 24.7747 | 460.7493 | 0.0064876 | 60.0036 | 0.54187 | 0.5632 | 90.2691 | 2.2545 | 0.1519 | 0.22322 | 4.7472 | 1.0005 | 0.30638 | 0 | 100 | 580.7 | 316 | 111.95 | 106.17 | 100.99 | 305.9 | 3 | 93.9 | 42.83 | 4 | 38.04 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.23 | 0 | 38.74 | 60 | 60 | 106.03 | 90.82 | 88.32 | 0 | 101.03 | 2.34 | 93.01 | 43.52 | 111.95 | 12.27 | 106.17 | 110 | 0 | 15659 | 82.03 | 115.84 | 221.19 | 215.03 | 220.51 | 0 | 37.01 | 51.37 | 14266 | 93.9 | 42.83 | 38.04 | 0.91 | 42.83 | 0 | 606 | 429.6 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.7 | 312.1 | 0 | 305.9 | 100.99 | 15659 | 15659 | 316
03/26/22 10:48:16.190 | 566.4036 | 1367.4942 | 54.1839 | 44.2712 | 9.9127 | 30.9021 | 51.0364 | 0 | 1786.3302 | 92.0636 | 83.2919 | 8.7717 | 25.0984 | 70.2235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.008 | 462.04 | 458.93 | 462.61 | 412.17 | 441.92 | 419.32 | 314.88 | 0.55593 | 0.87304 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6823999.0074 | 7829622.0994 | 7829622.0994 | 62.4275 | 62.1554 | 1.0017 | 0.99794 | 684497.6556 | 891149.0936 | 461.1934 | 0.49076 | 0 | 0 | 30.9021 | 25.0984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017902 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 581.7843 | 1368.122 | 54.0479 | 43.8713 | 31.0874 | 1786.9347 | 81.2835 | 24.7801 | 460.7536 | 0.0064971 | 60.0037 | 0.54198 | 0.56546 | 90.2849 | 2.2482 | 0.15146 | 0.22415 | 4.7124 | 1.008 | 0.30672 | 0 | 100 | 580.9 | 316 | 111.95 | 106.19 | 101.03 | 308.2 | 3 | 93.9 | 42.83 | 4 | 38.04 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.25 | 0 | 38.74 | 60 | 60 | 106.13 | 90.87 | 88.34 | 0 | 101.03 | 2.34 | 93.03 | 43.52 | 111.95 | 12.29 | 106.19 | 110 | 0 | 15659 | 82.06 | 115.86 | 221.19 | 215.03 | 220.51 | 0 | 37.1 | 51.41 | 14271 | 93.9 | 42.83 | 38.04 | 0.91 | 42.83 | 0 | 606 | 428.5 | 459.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581 | 313.2 | 0 | 306.9 | 101.04 | 15661 | 15659 | 314
03/26/22 10:48:21.190 | 567.2127 | 1369.5225 | 54.1913 | 44.2791 | 9.9122 | 31.6336 | 51.0378 | 0 | 1790.2938 | 92.0776 | 83.3062 | 8.7714 | 23.9999 | 70.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.008 | 462.04 | 458.93 | 462.61 | 412.17 | 441.92 | 419.32 | 314.88 | 0.55514 | 0.80436 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6834391.9307 | 7845446.2452 | 7845446.2452 | 62.4275 | 62.1553 | 1.0017 | 0.99794 | 685512.5719 | 893124.384 | 461.1933 | 0.49076 | 0 | 0 | 31.6336 | 23.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017894 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 581.6836 | 1368.1461 | 54.0498 | 43.8752 | 31.0878 | 1787.0043 | 81.3012 | 24.7803 | 460.7581 | 0.0065068 | 60.0039 | 0.54207 | 0.56689 | 90.3009 | 2.2397 | 0.15105 | 0.22514 | 4.6684 | 1.0154 | 0.3072 | 0 | 100 | 580.9 | 317 | 111.95 | 106.21 | 101.03 | 309.3 | 3 | 93.9 | 42.84 | 4 | 38.05 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.25 | 0 | 38.75 | 60 | 60 | 106.1 | 90.86 | 88.4 | 0 | 101.03 | 2.34 | 93.03 | 43.53 | 112 | 12.29 | 106.21 | 110 | 0 | 15659 | 82.08 | 115.86 | 221.19 | 215.14 | 220.51 | 0 | 37.11 | 51.33 | 14276 | 93.93 | 42.84 | 38.05 | 0.91 | 42.84 | 0 | 607 | 432.2 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.9 | 314.9 | 0 | 308.6 | 101.03 | 15655 | 15659 | 315
03/26/22 10:48:26.190 | 568.3025 | 1372.2114 | 54.2039 | 44.2921 | 9.9118 | 31.4626 | 51.0314 | 0 | 1789.2926 | 92.1008 | 83.3296 | 8.7712 | 24.1935 | 70.2342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.012 | 462.03 | 458.94 | 462.63 | 412.15 | 442.04 | 419.45 | 314.94 | 0.55418 | 1.0269 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6847373.3096 | 7841055.1492 | 7841055.1492 | 62.4275 | 62.155 | 1.0017 | 0.99794 | 686857.9189 | 892621.5387 | 461.2 | 0.49003 | 0 | 0 | 31.4626 | 24.1935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01621 | 0.017896 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 581.5806 | 1368.1659 | 54.0518 | 43.8791 | 31.091 | 1787.0434 | 81.319 | 24.7743 | 460.7626 | 0.0065165 | 60.0041 | 0.54217 | 0.56962 | 90.3169 | 2.2551 | 0.1507 | 0.2262 | 4.6576 | 1.0227 | 0.30771 | 0 | 100 | 581.6 | 316 | 112.05 | 106.23 | 101.15 | 307.2 | 3 | 93.95 | 42.86 | 4 | 38.07 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.33 | 0 | 38.79 | 60 | 60 | 106.13 | 90.87 | 88.47 | 0 | 101.15 | 2.34 | 93.07 | 43.57 | 112.03 | 12.29 | 106.23 | 110 | 0 | 15659 | 82.08 | 115.86 | 221.19 | 215.14 | 220.51 | 0 | 37.13 | 51.23 | 14281 | 93.94 | 42.86 | 38.07 | 0.91 | 42.86 | 0 | 607 | 432.5 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.5 | 312.5 | 0 | 306.3 | 101.13 | 15659 | 15659 | 316
03/26/22 10:48:31.191 | 568.3778 | 1372.3662 | 54.2109 | 44.2988 | 9.9121 | 31.6444 | 51.0357 | 0 | 1790.299 | 92.1134 | 83.3424 | 8.771 | 23.8031 | 70.2354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.017 | 462.08 | 458.98 | 462.69 | 412.27 | 442.25 | 419.66 | 315.11 | 0.5544 | 0.99236 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6848440.8189 | 7844823.1824 | 7844823.1824 | 62.4274 | 62.1549 | 1.0017 | 0.99794 | 686935.0985 | 893121.7515 | 461.25 | 0.49214 | 0 | 0 | 31.6444 | 23.8031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016212 | 0.017895 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 581.4784 | 1368.1868 | 54.0538 | 43.8831 | 31.0949 | 1787.0787 | 81.3369 | 24.766 | 460.7674 | 0.0065268 | 60.0043 | 0.54227 | 0.57271 | 90.333 | 2.2765 | 0.15036 | 0.22727 | 4.658 | 1.0299 | 0.30856 | 0 | 100 | 581.6 | 316 | 111.98 | 106.25 | 101.15 | 307.4 | 3 | 93.91 | 42.89 | 4 | 38.1 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.33 | 0 | 38.8 | 60 | 60 | 106.15 | 90.88 | 88.53 | 0 | 101.15 | 2.34 | 93.07 | 43.58 | 112 | 12.32 | 106.25 | 110 | 0 | 15658 | 82.1 | 115.86 | 221.19 | 215.14 | 220.51 | 0 | 37.11 | 51.16 | 14286 | 93.93 | 42.89 | 38.1 | 0.88 | 42.89 | 0 | 607 | 433.3 | 459.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.2 | 314.8 | 0 | 308.5 | 101.25 | 15659 | 15658 | 316
03/26/22 10:48:36.190 | 568.0982 | 1371.174 | 54.2196 | 44.307 | 9.9126 | 31.2704 | 51.0425 | 0 | 1790.2113 | 92.1288 | 83.3572 | 8.7717 | 24.2498 | 70.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.017 | 462.08 | 458.98 | 462.69 | 412.27 | 442.25 | 419.66 | 315.11 | 0.55468 | 0.94044 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6844795.1329 | 7845860.8366 | 7845860.8366 | 62.4274 | 62.1548 | 1.0017 | 0.99793 | 686573.1246 | 893156.1568 | 461.25 | 0.49214 | 0 | 0 | 31.2704 | 24.2498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016212 | 0.017892 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 581.3683 | 1368.1838 | 54.0559 | 43.8871 | 31.1022 | 1787.0993 | 81.3547 | 24.7533 | 460.7721 | 0.006537 | 60.0045 | 0.54238 | 0.57547 | 90.3491 | 2.2722 | 0.15003 | 0.22837 | 4.6637 | 1.0369 | 0.30941 | 0 | 100 | 581.5 | 314 | 112.03 | 106.25 | 101.13 | 307.9 | 3 | 93.94 | 42.9 | 4 | 38.11 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.33 | 0 | 38.8 | 60 | 60 | 106.1 | 90.86 | 88.51 | 0 | 101.13 | 2.34 | 93.07 | 43.58 | 112.03 | 12.31 | 106.25 | 110 | 0 | 15658 | 82.12 | 115.86 | 221.19 | 215.14 | 220.51 | 0 | 37.08 | 51.16 | 14291 | 93.94 | 42.9 | 38.11 | 0.87 | 42.9 | 0 | 607 | 434 | 459.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.3 | 313.7 | 0 | 307.5 | 101.1 | 15657 | 15658 | 314
03/26/22 10:48:41.190 | 567.652 | 1370.3379 | 54.2307 | 44.3173 | 9.9134 | 30.5089 | 51.0578 | 0 | 1788.312 | 92.148 | 83.3738 | 8.7741 | 25.2116 | 70.2561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.017 | 462.1 | 459.01 | 462.71 | 412.34 | 442.32 | 419.74 | 315.17 | 0.55522 | 0.92308 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6838871.396 | 7841556.4912 | 7841556.4912 | 62.4274 | 62.1546 | 1.0017 | 0.99793 | 685981.0517 | 892337.5579 | 461.2734 | 0.49067 | 0 | 0 | 30.5089 | 25.2116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016213 | 0.017891 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 581.2614 | 1368.1927 | 54.0581 | 43.8911 | 31.1039 | 1787.0858 | 81.3727 | 24.7478 | 460.7771 | 0.0065477 | 60.0046 | 0.54248 | 0.58011 | 90.3652 | 2.2775 | 0.14975 | 0.22951 | 4.6566 | 1.0437 | 0.31025 | 0 | 100 | 581.5 | 315 | 112 | 106.25 | 101.13 | 306.7 | 3 | 93.93 | 42.9 | 4 | 38.11 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.3 | 0 | 38.81 | 60 | 60 | 106.13 | 90.87 | 88.47 | 0 | 101.13 | 2.34 | 93.05 | 43.59 | 112 | 12.32 | 106.25 | 110 | 0 | 15657 | 82.14 | 115.86 | 221.19 | 215.14 | 220.63 | 0 | 37.18 | 51.33 | 14296 | 93.93 | 42.9 | 38.11 | 0.89 | 42.9 | 0 | 607 | 433.3 | 459.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.5 | 312.9 | 0 | 306.7 | 101.13 | 15653 | 15657 | 315
03/26/22 10:48:46.190 | 566.5577 | 1367.5613 | 54.2443 | 44.3292 | 9.9151 | 30.2974 | 51.0543 | 0 | 1789.272 | 92.1687 | 83.3903 | 8.7784 | 25.5584 | 70.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.02 | 462.13 | 459.04 | 462.73 | 412.4 | 442.36 | 419.86 | 315.24 | 0.55641 | 0.66189 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6825318.2409 | 7848838.2661 | 7848838.2661 | 62.4273 | 62.1543 | 1.0017 | 0.99793 | 684528.5183 | 892602.524 | 461.3 | 0.48992 | 0 | 0 | 30.2974 | 25.5584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017888 | 0.011268 | 0.004474 | 0.011584 | 0.0119 | 581.1549 | 1368.195 | 54.0603 | 43.8952 | 31.0967 | 1787.0536 | 81.3906 | 24.7552 | 460.7822 | 0.0065588 | 60.0048 | 0.54258 | 0.58558 | 90.3815 | 2.2766 | 0.14953 | 0.23073 | 4.6209 | 1.0505 | 0.31123 | 0 | 100 | 582 | 314 | 112.05 | 106.25 | 101.13 | 307 | 3 | 93.95 | 42.91 | 4 | 38.13 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.3 | 0 | 38.83 | 60 | 60 | 106.2 | 90.9 | 88.47 | 0 | 101.13 | 2.34 | 93.05 | 43.6 | 112.05 | 12.33 | 106.27 | 110 | 0 | 15656 | 82.16 | 115.89 | 221.31 | 215.14 | 220.63 | 0 | 37.3 | 51.4 | 14301 | 93.94 | 42.91 | 38.13 | 0.9 | 42.91 | 0 | 607 | 430.2 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.2 | 312.5 | 0 | 306.2 | 101.25 | 15658 | 15656 | 316
03/26/22 10:48:51.190 | 566.4215 | 1366.8955 | 54.2595 | 44.3419 | 9.9176 | 30.6179 | 51.0382 | 0 | 1791.5944 | 92.1882 | 83.4043 | 8.7838 | 25.4173 | 70.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 462.1701 | 459.1101 | 462.8001 | 412.3701 | 442.4801 | 420.1201 | 315.3501 | 0.55674 | 0.45808 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6823952.0325 | 7863695.2333 | 7863695.2333 | 62.4273 | 62.1541 | 1.0017 | 0.99793 | 684194.5834 | 893759.0923 | 461.3601 | 0.48769 | 0 | 0 | 30.6179 | 25.4173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.01788 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 581.0427 | 1368.1823 | 54.0626 | 43.8994 | 31.0921 | 1787.0347 | 81.4086 | 24.7617 | 460.7874 | 0.0065699 | 60.0049 | 0.54269 | 0.58927 | 90.3978 | 2.2768 | 0.1494 | 0.23199 | 4.598 | 1.0571 | 0.31259 | 0 | 100 | 581.7 | 317 | 112.05 | 106.27 | 101.17 | 308.5 | 3 | 93.95 | 42.91 | 4 | 38.13 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.3 | 0 | 38.83 | 60 | 60 | 106.13 | 90.87 | 88.53 | 0 | 101.17 | 2.34 | 93.05 | 43.6 | 112.03 | 12.33 | 106.27 | 110 | 0 | 15656 | 82.18 | 115.91 | 221.31 | 215.14 | 220.63 | 0 | 37.38 | 51.42 | 14306 | 93.94 | 42.91 | 38.13 | 0.92 | 42.91 | 0 | 607 | 430.3 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.6 | 314.6 | 0 | 308.3 | 101.15 | 15658 | 15656 | 316
03/26/22 10:48:56.190 | 566.1784 | 1365.9098 | 54.2687 | 44.3498 | 9.9189 | 30.3826 | 51.032 | 0 | 1794.0201 | 92.1983 | 83.4117 | 8.7866 | 25.5422 | 70.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 462.1701 | 459.1101 | 462.8001 | 412.3701 | 442.4801 | 420.1201 | 315.3501 | 0.55698 | 0.28162 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6820802.3467 | 7874613.3323 | 7874613.3323 | 62.4273 | 62.1541 | 1.0017 | 0.99793 | 683830.0001 | 894746.8929 | 461.3601 | 0.48769 | 0 | 0 | 30.3826 | 25.5422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017873 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 580.9324 | 1368.1715 | 54.0649 | 43.9035 | 31.0889 | 1787.0597 | 81.4267 | 24.7676 | 460.7926 | 0.0065812 | 60.005 | 0.5428 | 0.59086 | 90.4141 | 2.283 | 0.14932 | 0.23329 | 4.6237 | 1.0634 | 0.31422 | 0 | 100 | 582 | 315 | 112 | 106.27 | 101.22 | 308.8 | 3 | 93.93 | 42.91 | 4 | 38.13 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.3 | 0 | 38.83 | 60 | 60 | 106.13 | 90.87 | 88.55 | 0 | 101.15 | 2.34 | 93.05 | 43.6 | 112 | 12.34 | 106.27 | 110 | 0 | 15655 | 82.21 | 115.91 | 221.31 | 215.14 | 220.63 | 0 | 37.43 | 51.4 | 14311 | 93.93 | 42.91 | 38.13 | 0.92 | 42.91 | 0 | 607 | 433.2 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.5 | 315.1 | 0 | 308.8 | 101.13 | 15655 | 15655 | 315
03/26/22 10:49:01.190 | 565.6353 | 1364.5628 | 54.2864 | 44.3656 | 9.9208 | 30.2947 | 51.0296 | 0 | 1796.0587 | 92.2154 | 83.4243 | 8.7911 | 25.3137 | 70.2833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.017 | 462.15 | 459.12 | 462.77 | 412.32 | 442.37 | 420.3 | 315.33 | 0.55748 | 0.0067305 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6814188.4071 | 7889675.7442 | 7889675.7442 | 62.4272 | 62.1539 | 1.0017 | 0.99793 | 683025.7088 | 895983.272 | 461.3467 | 0.48264 | 0 | 0 | 30.2947 | 25.3137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017865 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 580.823 | 1368.1626 | 54.0672 | 43.9077 | 31.0824 | 1787.1335 | 81.4447 | 24.774 | 460.7979 | 0.0065925 | 60.0051 | 0.54291 | 0.58965 | 90.4304 | 2.2942 | 0.14927 | 0.23459 | 4.6435 | 1.0695 | 0.31575 | 0 | 100 | 581.5 | 316 | 111.93 | 106.25 | 101.13 | 309 | 3 | 93.89 | 42.91 | 4 | 38.13 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.28 | 0 | 38.83 | 60 | 60 | 106.15 | 90.88 | 88.49 | 0 | 101.13 | 2.33 | 93.04 | 43.6 | 111.93 | 12.36 | 106.25 | 110 | 0 | 15654 | 82.23 | 115.94 | 221.31 | 215.14 | 220.63 | 0 | 37.46 | 51.3 | 14316 | 93.89 | 42.91 | 38.13 | 0.92 | 42.91 | 0 | 607 | 429 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.4 | 314.5 | 0 | 308.2 | 101.11 | 15653 | 15654 | 316
03/26/22 10:49:06.189 | 566.0857 | 1365.6569 | 54.2935 | 44.3727 | 9.9208 | 31.1671 | 51.0271 | 0 | 1795.8884 | 92.2219 | 83.4294 | 8.7925 | 24.4281 | 70.2809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.017 | 462.15 | 459.12 | 462.77 | 412.32 | 442.37 | 420.3 | 315.33 | 0.55704 | 0.091684 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6820380.4174 | 7889094.2311 | 7889094.2311 | 62.4272 | 62.1538 | 1.0017 | 0.99793 | 683573.0373 | 895897.5608 | 461.3467 | 0.48264 | 0 | 0 | 31.1671 | 24.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017862 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 580.7166 | 1368.1601 | 54.0697 | 43.912 | 31.0801 | 1787.2058 | 81.4628 | 24.7755 | 460.8031 | 0.0066037 | 60.0052 | 0.54301 | 0.58893 | 90.4468 | 2.2967 | 0.14935 | 0.23601 | 4.6781 | 1.0754 | 0.31706 | 0 | 100 | 580.8 | 317 | 112.05 | 106.23 | 101.01 | 305.9 | 3 | 93.94 | 42.91 | 4 | 38.13 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.4 | 0 | 38.81 | 60 | 60 | 106.23 | 90.92 | 88.45 | 0 | 101.01 | 2.34 | 93.1 | 43.59 | 112.08 | 12.27 | 106.23 | 110 | 0 | 15654 | 82.25 | 115.94 | 221.31 | 215.25 | 220.63 | 0 | 37.4 | 51.18 | 14321 | 93.96 | 42.9 | 38.11 | 0.93 | 42.9 | 0 | 607 | 430.4 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.3 | 313.8 | 0 | 307.5 | 100.92 | 15654 | 15654 | 316
03/26/22 10:49:11.190 | 565.4734 | 1364.6763 | 54.2996 | 44.3824 | 9.9172 | 31.9305 | 51.0254 | 0 | 1792.544 | 92.2297 | 83.4381 | 8.7916 | 23.6416 | 70.2817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 462.11 | 459.09 | 462.73 | 412.07 | 442.05 | 420.17 | 315.13 | 0.55729 | 0.21442 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6813682.0615 | 7872733.0044 | 7872733.0044 | 62.4272 | 62.1537 | 1.0017 | 0.99793 | 683081.9513 | 894227.9481 | 461.31 | 0.48124 | 0 | 0 | 31.9305 | 23.6416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017873 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 580.6085 | 1368.1559 | 54.0721 | 43.9163 | 31.0797 | 1787.2647 | 81.4809 | 24.7745 | 460.8081 | 0.0066145 | 60.0052 | 0.54312 | 0.58886 | 90.4632 | 2.3024 | 0.14948 | 0.23748 | 4.6782 | 1.0811 | 0.3179 | 0 | 100 | 578.2 | 316 | 112.23 | 106.29 | 100.56 | 306.8 | 3 | 94.03 | 42.83 | 4 | 38.04 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.58 | 0 | 38.71 | 60 | 60 | 106.4 | 91.02 | 88.49 | 0 | 100.56 | 2.35 | 93.19 | 43.49 | 112.23 | 12.25 | 106.29 | 110 | 0 | 15654 | 82.25 | 115.94 | 221.31 | 215.25 | 220.63 | 0 | 37.45 | 51.12 | 14326 | 94.04 | 42.8 | 38.01 | 1.03 | 42.8 | 0 | 607 | 431 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.9 | 314.6 | 0 | 308.4 | 100.5 | 15653 | 15654 | 316
03/26/22 10:49:16.190 | 565.1043 | 1365.8943 | 54.2976 | 44.3957 | 9.9019 | 31.5529 | 51.0461 | 0 | 1783.213 | 92.2395 | 83.4579 | 8.7816 | 24.1377 | 70.2846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.013 | 462.03 | 459.07 | 462.68 | 411.31 | 441.35 | 419.74 | 314.6 | 0.55671 | 0.7628 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6808946.614 | 7823421.3438 | 7823421.3438 | 62.4272 | 62.1536 | 1.0017 | 0.99793 | 683691.7066 | 889570.2074 | 461.26 | 0.47479 | 0 | 0 | 31.5529 | 24.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017881 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 580.4955 | 1368.1434 | 54.0746 | 43.9207 | 31.0804 | 1787.2608 | 81.4991 | 24.7733 | 460.8129 | 0.0066248 | 60.0053 | 0.54322 | 0.59183 | 90.4796 | 2.3086 | 0.14957 | 0.23903 | 4.6813 | 1.0867 | 0.31847 | 0 | 100 | 577.6 | 316 | 112.45 | 106.37 | 100.45 | 305.7 | 3 | 94.16 | 42.75 | 4 | 37.96 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.75 | 0 | 38.66 | 60 | 60 | 106.58 | 91.11 | 88.55 | 0 | 100.45 | 2.35 | 93.27 | 43.44 | 112.48 | 12.2 | 106.37 | 110 | 0 | 15654 | 82.27 | 115.91 | 221.31 | 215.25 | 220.75 | 0 | 37.46 | 50.98 | 14331 | 94.17 | 42.75 | 37.96 | 1.04 | 42.75 | 0 | 607 | 426.8 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.6 | 311.9 | 0 | 305.7 | 100.45 | 15656 | 15654 | 317
03/26/22 10:49:21.190 | 564.9958 | 1367.422 | 54.2922 | 44.4012 | 9.8909 | 31.6369 | 51.0475 | 0 | 1781.6285 | 92.2445 | 83.4707 | 8.7738 | 23.8529 | 70.2817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.013 | 462.03 | 459.07 | 462.68 | 411.31 | 441.35 | 419.74 | 314.6 | 0.55682 | 0.8714 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6807726.5708 | 7812806.924 | 7812806.924 | 62.4272 | 62.1535 | 1.0017 | 0.99793 | 684115.5461 | 888974.1334 | 461.26 | 0.47479 | 0 | 0 | 31.6369 | 23.8529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017889 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 580.3734 | 1368.1278 | 54.0769 | 43.9251 | 31.0845 | 1787.262 | 81.5173 | 24.7667 | 460.8175 | 0.0066348 | 60.0053 | 0.54334 | 0.5936 | 90.496 | 2.3039 | 0.14961 | 0.24058 | 4.6797 | 1.0921 | 0.31886 | 0 | 100 | 577.2 | 314 | 112.58 | 106.43 | 100.38 | 306.3 | 3 | 94.22 | 42.74 | 4 | 37.95 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.85 | 0 | 38.64 | 60 | 60 | 106.65 | 91.15 | 88.67 | 0 | 100.38 | 2.35 | 93.34 | 43.42 | 112.6 | 12.2 | 106.43 | 110 | 0 | 15654 | 82.29 | 115.91 | 221.31 | 215.25 | 220.75 | 0 | 37.39 | 50.82 | 14335 | 94.23 | 42.73 | 37.94 | 1.03 | 42.73 | 0 | 607 | 430.3 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 312.6 | 0 | 306.3 | 100.37 | 15653 | 15654 | 316
03/26/22 10:49:26.189 | 564.0533 | 1368.289 | 54.2754 | 44.4092 | 9.8662 | 30.8975 | 51.0434 | 0 | 1780.0493 | 92.2566 | 83.5017 | 8.7549 | 24.8206 | 70.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.011 | 462.02 | 459.08 | 462.67 | 410.87 | 440.92 | 419.4 | 314.28 | 0.55718 | 1.0423 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6795807.0323 | 7786592.8076 | 7786592.8076 | 62.4272 | 62.1533 | 1.0017 | 0.99793 | 684891.3636 | 887985.703 | 461.2567 | 0.4719 | 0 | 0 | 30.8975 | 24.8206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017889 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 580.2369 | 1368.0957 | 54.0792 | 43.9295 | 31.0842 | 1787.2434 | 81.5356 | 24.7657 | 460.8222 | 0.0066449 | 60.0053 | 0.54346 | 0.59549 | 90.5125 | 2.2604 | 0.14951 | 0.24215 | 4.7018 | 1.0976 | 0.31909 | 0 | 100 | 577 | 317 | 112.65 | 106.47 | 100.35 | 303.9 | 3 | 94.26 | 42.73 | 4 | 37.94 | 43.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.98 | 0 | 38.63 | 60 | 60 | 106.78 | 91.21 | 88.79 | 0 | 100.35 | 2.36 | 93.4 | 43.41 | 112.68 | 12.22 | 106.49 | 110 | 0 | 15654 | 82.29 | 115.89 | 221.44 | 215.25 | 220.75 | 0 | 37.32 | 50.75 | 14340 | 94.27 | 42.71 | 37.94 | 0.98 | 42.71 | 0 | 607 | 428.7 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 311.8 | 0 | 305.5 | 100.35 | 15653 | 15654 | 316
03/26/22 10:49:31.189 | 561.8645 | 1365.9923 | 54.2496 | 44.4119 | 9.8376 | 30.8672 | 51.0419 | 0 | 1783.1097 | 92.274 | 83.5427 | 8.7313 | 25.0227 | 70.2837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.011 | 462.02 | 459.08 | 462.67 | 410.87 | 440.92 | 419.4 | 314.28 | 0.55935 | 0.81482 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6769487.4377 | 7778217.0806 | 7778217.0806 | 62.4272 | 62.153 | 1.0017 | 0.99793 | 683791.7617 | 888897.679 | 461.2567 | 0.4719 | 0 | 0 | 30.8672 | 25.0227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017888 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 580.0912 | 1368.0593 | 54.0813 | 43.9339 | 31.0822 | 1787.222 | 81.5542 | 24.7658 | 460.8269 | 0.006655 | 60.0054 | 0.54359 | 0.59731 | 90.529 | 2.2412 | 0.14922 | 0.24367 | 4.7118 | 1.1032 | 0.31924 | 0 | 100 | 576.6 | 317 | 112.73 | 106.51 | 100.28 | 305.4 | 3 | 94.3 | 42.71 | 4 | 37.93 | 43.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111 | 0 | 38.61 | 60 | 60 | 106.78 | 91.21 | 88.89 | 0 | 100.28 | 2.36 | 93.41 | 43.39 | 112.73 | 12.23 | 106.53 | 110 | 0 | 15654 | 82.29 | 115.86 | 221.44 | 215.25 | 220.75 | 0 | 37.37 | 50.87 | 14346 | 94.3 | 42.7 | 37.91 | 0.98 | 42.7 | 0 | 607 | 429.8 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.8 | 313.5 | 0 | 307.3 | 100.31 | 15653 | 15654 | 317
03/26/22 10:49:36.189 | 560.2325 | 1367.6645 | 54.2109 | 44.4072 | 9.8037 | 31.1735 | 51.0477 | 0 | 1787.0063 | 92.3013 | 83.5984 | 8.7029 | 24.7722 | 70.3035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 462 | 459.07 | 462.63 | 409.84 | 439.62 | 418.28 | 313.36 | 0.55934 | 0.63899 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6750188.1209 | 7770559.5106 | 7770559.5106 | 62.4273 | 62.1525 | 1.0017 | 0.99793 | 684581.6847 | 891442.3123 | 461.2334 | 0.46903 | 0 | 0 | 31.1735 | 24.7722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.01788 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 579.957 | 1368.0615 | 54.0833 | 43.9383 | 31.079 | 1787.2042 | 81.5727 | 24.7695 | 460.8317 | 0.0066653 | 60.0054 | 0.54371 | 0.60096 | 90.5455 | 2.2401 | 0.14885 | 0.24513 | 4.7157 | 1.1087 | 0.31915 | 0 | 100 | 577 | 314 | 112.73 | 106.55 | 100.35 | 304.1 | 3 | 94.3 | 42.71 | 4 | 37.93 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.98 | 0 | 38.61 | 60 | 60 | 106.7 | 91.16 | 89.03 | 0 | 100.38 | 2.36 | 93.4 | 43.39 | 112.68 | 12.26 | 106.55 | 110 | 0 | 15654 | 82.31 | 115.86 | 221.44 | 215.25 | 220.75 | 0 | 37.47 | 51.01 | 14351 | 94.28 | 42.71 | 37.93 | 0.94 | 42.71 | 0 | 607 | 426.4 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.9 | 311.7 | 0 | 305.5 | 100.33 | 15653 | 15654 | 317
03/26/22 10:49:41.189 | 559.4437 | 1368.5883 | 54.1846 | 44.4014 | 9.7833 | 31.0319 | 51.0539 | 0 | 1787.7959 | 92.3208 | 83.635 | 8.6857 | 24.7948 | 70.2875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 462 | 459.07 | 462.63 | 409.84 | 439.62 | 418.28 | 313.36 | 0.56013 | 0.65711 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6740615.5747 | 7758692.8085 | 7758692.8085 | 62.4273 | 62.1522 | 1.0017 | 0.99793 | 685045.2826 | 891830.9491 | 461.2334 | 0.46903 | 0 | 0 | 31.0319 | 24.7948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.01788 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 579.8061 | 1368.0568 | 54.0851 | 43.9426 | 31.0822 | 1787.2095 | 81.5916 | 24.7648 | 460.8363 | 0.0066754 | 60.0055 | 0.54383 | 0.60298 | 90.5622 | 2.2381 | 0.14822 | 0.24641 | 4.7158 | 1.1147 | 0.31882 | 0 | 100 | 577.1 | 316 | 112.65 | 106.57 | 100.37 | 304.9 | 3 | 94.26 | 42.71 | 4 | 37.93 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.05 | 0 | 38.61 | 60 | 60 | 106.78 | 91.21 | 89.12 | 0 | 100.37 | 2.36 | 93.44 | 43.39 | 112.75 | 12.27 | 106.57 | 110 | 0 | 15654 | 82.31 | 115.86 | 221.44 | 215.25 | 220.75 | 0 | 37.56 | 51.12 | 14356 | 94.3 | 42.7 | 37.91 | 0.96 | 42.7 | 0 | 607 | 426 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 310 | 0 | 303.8 | 100.28 | 15655 | 15654 | 317
03/26/22 10:49:46.190 | 558.909 | 1369.0941 | 54.1579 | 44.3939 | 9.764 | 31.0065 | 51.0463 | 0 | 1787.5637 | 92.3409 | 83.6714 | 8.6695 | 24.7413 | 70.2668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.019 | 461.98 | 459.04 | 462.61 | 409.58 | 439.29 | 417.93 | 313.1 | 0.5602 | 0.69961 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6734150.1344 | 7748094.9398 | 7748094.9398 | 62.4274 | 62.1519 | 1.0017 | 0.99793 | 685555.2391 | 892052.9789 | 461.21 | 0.4705 | 0 | 0 | 31.0065 | 24.7413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017887 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 579.6513 | 1368.0525 | 54.0866 | 43.9468 | 31.0849 | 1787.1879 | 81.6107 | 24.7585 | 460.8409 | 0.0066852 | 60.0056 | 0.54396 | 0.6064 | 90.5789 | 2.2353 | 0.1475 | 0.24756 | 4.7052 | 1.1208 | 0.31827 | 0 | 100 | 577 | 315 | 112.78 | 106.58 | 100.43 | 305.4 | 3 | 94.32 | 42.7 | 4 | 37.91 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.08 | 0 | 38.6 | 60 | 60 | 106.8 | 91.23 | 89.28 | 0 | 100.43 | 2.36 | 93.45 | 43.38 | 112.78 | 12.26 | 106.58 | 110 | 0 | 15654 | 82.33 | 115.89 | 221.44 | 215.25 | 220.75 | 0 | 37.69 | 51.29 | 14361 | 94.32 | 42.7 | 37.91 | 0.92 | 42.7 | 0 | 607 | 427.5 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.5 | 311.6 | 0 | 305.4 | 100.26 | 15653 | 15654 | 316
03/26/22 10:49:51.189 | 555.3586 | 1366.5136 | 54.1011 | 44.3747 | 9.7264 | 31.3816 | 51.0308 | 0 | 1783.5845 | 92.385 | 83.7467 | 8.6383 | 24.1152 | 70.2966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0241 | 461.9901 | 459.0401 | 462.5801 | 409.5301 | 438.9601 | 417.5101 | 312.8801 | 0.56338 | 0.80712 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6691860.9215 | 7697379.8273 | 7697379.8273 | 62.4275 | 62.1512 | 1.0017 | 0.99793 | 684010.5408 | 889714.0428 | 461.2034 | 0.46906 | 0 | 0 | 31.3816 | 24.1152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017891 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 579.4929 | 1368.0588 | 54.088 | 43.951 | 31.0885 | 1787.1503 | 81.6298 | 24.7511 | 460.8454 | 0.006695 | 60.0057 | 0.54409 | 0.61115 | 90.5957 | 2.2353 | 0.14676 | 0.24859 | 4.6783 | 1.1269 | 0.31767 | 0 | 100 | 576.8 | 317 | 112.78 | 106.58 | 100.28 | 305.2 | 3 | 94.32 | 42.69 | 4 | 37.9 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.15 | 0 | 38.59 | 60 | 60 | 106.85 | 91.25 | 89.5 | 0 | 100.28 | 2.36 | 93.48 | 43.37 | 112.8 | 12.25 | 106.58 | 110 | 0 | 15654 | 82.33 | 115.91 | 221.44 | 215.25 | 220.75 | 0 | 37.84 | 51.36 | 14366 | 94.33 | 42.69 | 37.9 | 0.93 | 42.69 | 0 | 607 | 427.9 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.8 | 311.6 | 0 | 305.4 | 100.31 | 15653 | 15654 | 317
03/26/22 10:49:56.189 | 554.2014 | 1366.4053 | 54.069 | 44.3622 | 9.7068 | 31.1568 | 51.0312 | 0 | 1783.7084 | 92.4119 | 83.7898 | 8.6221 | 24.6573 | 70.3407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0241 | 461.9901 | 459.0401 | 462.5801 | 409.5301 | 438.9601 | 417.5101 | 312.8801 | 0.56456 | 0.79422 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6677774.9563 | 7684093.7059 | 7684093.7059 | 62.4275 | 62.1509 | 1.0017 | 0.99793 | 683957.7185 | 889769.6206 | 461.2034 | 0.46906 | 0 | 0 | 31.1568 | 24.6573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017886 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 579.3176 | 1368.0559 | 54.089 | 43.9551 | 31.0924 | 1787.0808 | 81.6493 | 24.7461 | 460.85 | 0.0067047 | 60.0058 | 0.54424 | 0.61746 | 90.6126 | 2.2371 | 0.14603 | 0.24935 | 4.6355 | 1.1337 | 0.31694 | 0 | 100 | 576.6 | 312 | 112.83 | 106.6 | 100.28 | 304.4 | 3 | 94.35 | 42.69 | 4 | 37.9 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.18 | 0 | 38.59 | 60 | 60 | 106.9 | 91.28 | 89.63 | 0 | 100.28 | 2.36 | 93.5 | 43.37 | 112.85 | 12.26 | 106.6 | 110 | 0 | 15654 | 82.36 | 115.96 | 221.44 | 215.25 | 220.75 | 0 | 37.97 | 51.42 | 14370 | 94.35 | 42.69 | 37.9 | 0.91 | 42.69 | 0 | 607 | 427.4 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 310.9 | 0 | 304.6 | 100.23 | 15653 | 15654 | 314
03/26/22 10:50:01.190 | 553.9303 | 1367.6749 | 54.0394 | 44.3485 | 9.6908 | 31.1571 | 51.0407 | 0 | 1787.5172 | 92.4407 | 83.8317 | 8.6091 | 24.5191 | 70.3288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0241 | 461.9901 | 459.0401 | 462.5801 | 409.5301 | 438.9601 | 417.5101 | 312.8801 | 0.56484 | 0.68265 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6674450.5606 | 7689369.6784 | 7689369.6784 | 62.4276 | 62.1506 | 1.0017 | 0.99793 | 684418.4782 | 891328.139 | 461.2034 | 0.46906 | 0 | 0 | 31.1571 | 24.5191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017881 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 579.1392 | 1368.0574 | 54.0898 | 43.959 | 31.0925 | 1787.0401 | 81.669 | 24.7465 | 460.8545 | 0.0067145 | 60.0059 | 0.54439 | 0.62243 | 90.6297 | 2.2368 | 0.14536 | 0.24994 | 4.599 | 1.1407 | 0.31615 | 0 | 100 | 577 | 314 | 112.83 | 106.6 | 100.35 | 306 | 3 | 94.36 | 42.69 | 4 | 37.9 | 43.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.15 | 0 | 38.59 | 60 | 60 | 106.85 | 91.25 | 89.67 | 0 | 100.35 | 2.36 | 93.49 | 43.37 | 112.83 | 12.26 | 106.6 | 110 | 0 | 15654 | 82.36 | 115.98 | 221.44 | 215.25 | 220.75 | 0 | 38.1 | 51.48 | 14376 | 94.35 | 42.69 | 37.9 | 0.89 | 42.69 | 0 | 607 | 427.2 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.9 | 311.6 | 0 | 305.4 | 100.33 | 15654 | 15654 | 314
03/26/22 10:50:06.189 | 551.4937 | 1364.4234 | 53.9946 | 44.3213 | 9.6733 | 31.703 | 51.0593 | 0 | 1787.5017 | 92.4964 | 83.9006 | 8.5958 | 24.1361 | 70.3585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.024 | 462.02 | 459.03 | 462.61 | 409.54 | 438.99 | 417.36 | 312.87 | 0.56731 | 0.48015 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6645721.6329 | 7676263.4429 | 7676263.4429 | 62.4277 | 62.1498 | 1.0017 | 0.99793 | 682969.003 | 891645.7898 | 461.22 | 0.47483 | 0 | 0 | 31.703 | 24.1361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017883 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 578.9498 | 1368.0471 | 54.0904 | 43.9628 | 31.0952 | 1787.0222 | 81.689 | 24.7454 | 460.8592 | 0.0067247 | 60.0061 | 0.54455 | 0.62543 | 90.647 | 2.2466 | 0.14484 | 0.2503 | 4.5929 | 1.1479 | 0.31544 | 0 | 100 | 577.1 | 312 | 112.88 | 106.62 | 100.37 | 305 | 3 | 94.37 | 42.7 | 4 | 37.91 | 43.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.2 | 0 | 38.6 | 60 | 60 | 106.88 | 91.27 | 89.88 | 0 | 100.37 | 2.36 | 93.52 | 43.38 | 112.9 | 12.24 | 106.62 | 110 | 0 | 15654 | 82.38 | 116.01 | 221.44 | 215.25 | 220.75 | 0 | 38.21 | 51.5 | 14381 | 94.38 | 42.7 | 37.91 | 0.88 | 42.7 | 0 | 607 | 428.8 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 312.1 | 0 | 305.9 | 100.35 | 15652 | 15654 | 316
03/26/22 10:50:11.189 | 551.6808 | 1365.564 | 53.9736 | 44.3052 | 9.6684 | 31.3244 | 51.0587 | 0 | 1787.5843 | 92.5283 | 83.936 | 8.5923 | 24.7057 | 70.3663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.019 | 462.03 | 459.05 | 462.63 | 409.45 | 439.01 | 417.33 | 312.87 | 0.56712 | 0.53386 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6647657.8893 | 7674135.4278 | 7674135.4278 | 62.4278 | 62.1494 | 1.0017 | 0.99793 | 683540.8624 | 891681.8691 | 461.2367 | 0.47409 | 0 | 0 | 31.3244 | 24.7057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017883 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 578.7563 | 1368.0334 | 54.0907 | 43.9664 | 31.0962 | 1787.0312 | 81.7092 | 24.7454 | 460.8639 | 0.0067349 | 60.0063 | 0.54471 | 0.62673 | 90.6644 | 2.2566 | 0.14446 | 0.25051 | 4.5917 | 1.1552 | 0.31444 | 0 | 100 | 577.1 | 315 | 112.98 | 106.62 | 100.33 | 305.6 | 3 | 94.45 | 42.71 | 4 | 37.93 | 43.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.25 | 0 | 38.61 | 60 | 60 | 106.98 | 91.32 | 89.94 | 0 | 100.33 | 2.36 | 93.54 | 43.39 | 112.98 | 12.2 | 106.62 | 110 | 0 | 15654 | 82.38 | 116.03 | 221.44 | 215.25 | 220.75 | 0 | 38.32 | 51.46 | 14386 | 94.42 | 42.71 | 37.93 | 0.87 | 42.71 | 0 | 607 | 429.5 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 311.8 | 0 | 305.6 | 100.35 | 15654 | 15654 | 315
03/26/22 10:50:16.189 | 553.2721 | 1370.5702 | 53.9562 | 44.291 | 9.6652 | 30.647 | 51.0558 | 0 | 1789.1739 | 92.5567 | 83.9662 | 8.5905 | 25.3901 | 70.3312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0151 | 462.0801 | 459.1001 | 462.6901 | 409.3701 | 439.0001 | 417.3101 | 312.8701 | 0.56549 | 0.73338 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6666455.5769 | 7677499.3306 | 7677499.3306 | 62.4278 | 62.1492 | 1.0017 | 0.99793 | 685688.2387 | 892170.2523 | 461.2901 | 0.47476 | 0 | 0 | 30.647 | 25.3901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017877 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 578.5695 | 1368.0398 | 54.091 | 43.97 | 31.0921 | 1787.0525 | 81.7296 | 24.7502 | 460.869 | 0.0067458 | 60.0064 | 0.54486 | 0.62853 | 90.6819 | 2.2602 | 0.1442 | 0.2506 | 4.5899 | 1.1625 | 0.31303 | 0 | 100 | 576.8 | 316 | 112.95 | 106.62 | 100.28 | 305.3 | 3 | 94.41 | 42.7 | 4 | 37.91 | 43.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.23 | 0 | 38.6 | 60 | 60 | 106.9 | 91.28 | 89.98 | 0 | 100.28 | 2.36 | 93.53 | 43.38 | 112.98 | 12.2 | 106.62 | 110 | 0 | 15654 | 82.4 | 116.03 | 221.44 | 215.25 | 220.75 | 0 | 38.41 | 51.54 | 14391 | 94.42 | 42.7 | 37.91 | 0.88 | 42.7 | 0 | 607 | 428.6 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 311.5 | 0 | 305.3 | 100.28 | 15656 | 15654 | 317
03/26/22 10:50:21.189 | 554.0557 | 1372.3869 | 53.9355 | 44.2738 | 9.6617 | 30.0797 | 51.0587 | 0 | 1792.6524 | 92.5938 | 84.0034 | 8.5904 | 26.2424 | 70.3783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.015 | 462.1 | 459.14 | 462.74 | 409.3 | 439 | 417.35 | 312.88 | 0.56471 | 0.60726 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6675196.3702 | 7695876.2866 | 7695876.2866 | 62.4279 | 62.1487 | 1.0017 | 0.99793 | 686957.7875 | 894200.1315 | 461.3267 | 0.474 | 0 | 0 | 30.0797 | 26.2424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017866 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 578.3861 | 1368.0585 | 54.0911 | 43.9734 | 31.0868 | 1787.083 | 81.7501 | 24.7573 | 460.8746 | 0.0067578 | 60.0066 | 0.54502 | 0.63053 | 90.6996 | 2.2822 | 0.14411 | 0.25053 | 4.6088 | 1.1698 | 0.31154 | 0 | 100 | 576.8 | 316 | 112.85 | 106.64 | 100.31 | 306.3 | 3 | 94.36 | 42.71 | 4 | 37.94 | 43.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.2 | 0 | 38.61 | 60 | 60 | 106.88 | 91.27 | 90.13 | 0 | 100.31 | 2.36 | 93.52 | 43.39 | 112.85 | 12.27 | 106.64 | 110 | 0 | 15654 | 82.42 | 116.03 | 221.44 | 215.25 | 220.75 | 0 | 38.63 | 51.69 | 14396 | 94.37 | 42.73 | 37.94 | 0.85 | 42.73 | 0 | 607 | 424.1 | 459.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.8 | 312.5 | 0 | 306.3 | 100.31 | 15654 | 15654 | 316
03/26/22 10:50:26.189 | 553.7731 | 1371.4166 | 53.9238 | 44.264 | 9.6598 | 30.2627 | 51.045 | 0 | 1796.9774 | 92.6171 | 84.0258 | 8.5913 | 25.8049 | 70.3667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0151 | 462.1001 | 459.1401 | 462.7401 | 409.3001 | 439.0001 | 417.3501 | 312.8801 | 0.565 | 0.38811 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6672005.0077 | 7709615.5871 | 7709615.5871 | 62.4279 | 62.1485 | 1.0017 | 0.99793 | 686720.5555 | 895788.3938 | 461.3267 | 0.474 | 0 | 0 | 30.2627 | 25.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017858 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 578.2001 | 1368.0706 | 54.091 | 43.9767 | 31.0822 | 1787.1266 | 81.7708 | 24.7627 | 460.8806 | 0.0067708 | 60.0068 | 0.54517 | 0.63195 | 90.7175 | 2.2942 | 0.14415 | 0.2504 | 4.6651 | 1.177 | 0.30973 | 0 | 100 | 577.5 | 316 | 112.8 | 106.64 | 100.43 | 307 | 4 | 94.33 | 42.73 | 4 | 37.94 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.15 | 0 | 38.63 | 60 | 60 | 106.85 | 91.25 | 90.27 | 0 | 100.43 | 2.36 | 93.49 | 43.41 | 112.8 | 12.31 | 106.64 | 110 | 0 | 15654 | 82.44 | 116.05 | 221.44 | 215.25 | 220.75 | 0 | 38.77 | 51.71 | 14401 | 94.33 | 42.73 | 37.94 | 0.87 | 42.73 | 0 | 607 | 429.1 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.6 | 313.4 | 0 | 307.1 | 100.45 | 15653 | 15654 | 316
03/26/22 10:50:31.189 | 552.9366 | 1369.7857 | 53.9118 | 44.2538 | 9.658 | 30.8808 | 51.05 | 0 | 1794.2833 | 92.644 | 84.0507 | 8.5933 | 24.9058 | 70.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0151 | 462.1001 | 459.1401 | 462.7401 | 409.3001 | 439.0001 | 417.3501 | 312.8801 | 0.56585 | 0.29833 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6662480.8377 | 7707044.8066 | 7707044.8066 | 62.4279 | 62.1482 | 1.0017 | 0.99793 | 685803.9637 | 895434.7304 | 461.3268 | 0.474 | 0 | 0 | 30.8808 | 24.9058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017864 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 578.0182 | 1368.0951 | 54.0909 | 43.98 | 31.0812 | 1787.153 | 81.7916 | 24.7638 | 460.8866 | 0.0067838 | 60.0069 | 0.54532 | 0.63443 | 90.7354 | 2.2888 | 0.1443 | 0.25019 | 4.6921 | 1.184 | 0.3078 | 0 | 100 | 577.5 | 316 | 112.83 | 106.64 | 100.47 | 306.5 | 4 | 94.35 | 42.73 | 4 | 37.94 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.18 | 0 | 38.63 | 60 | 60 | 106.85 | 91.25 | 90.31 | 0 | 100.47 | 2.36 | 93.5 | 43.41 | 112.85 | 12.29 | 106.64 | 110 | 0 | 15654 | 82.46 | 116.05 | 221.44 | 215.25 | 220.75 | 0 | 38.91 | 51.71 | 14406 | 94.36 | 42.73 | 37.94 | 0.89 | 42.73 | 0 | 607 | 429.1 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 312.7 | 0 | 306.5 | 100.43 | 15653 | 15654 | 316
03/26/22 10:50:36.189 | 552.9919 | 1370.4205 | 53.9021 | 44.2452 | 9.6569 | 30.9766 | 51.0465 | 0 | 1789.7055 | 92.6702 | 84.0738 | 8.5964 | 24.8728 | 70.3812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.016 | 462.19 | 459.25 | 462.83 | 409.28 | 439.07 | 417.53 | 313 | 0.56601 | 0.57474 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6663182.7748 | 7686875.718 | 7686875.718 | 62.428 | 62.1479 | 1.0017 | 0.99792 | 685974.9893 | 892719.923 | 461.4233 | 0.47101 | 0 | 0 | 30.9766 | 24.8728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017865 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 577.8423 | 1368.1375 | 54.0907 | 43.9831 | 31.079 | 1787.1775 | 81.8125 | 24.7678 | 460.8935 | 0.0067987 | 60.007 | 0.54547 | 0.63806 | 90.7535 | 2.2604 | 0.14454 | 0.2499 | 4.6939 | 1.1909 | 0.30576 | 0 | 100 | 577.5 | 317 | 112.85 | 106.64 | 100.43 | 306 | 4 | 94.36 | 42.73 | 4 | 37.94 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.18 | 0 | 38.63 | 60 | 60 | 106.85 | 91.25 | 90.29 | 0 | 100.43 | 2.36 | 93.5 | 43.41 | 112.9 | 12.26 | 106.64 | 110 | 0 | 15654 | 82.46 | 116.08 | 221.44 | 215.25 | 220.75 | 0 | 39.03 | 51.67 | 14410 | 94.38 | 42.71 | 37.93 | 0.9 | 42.71 | 0 | 607 | 424.7 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.4 | 313.6 | 0 | 307.4 | 100.42 | 15654 | 15654 | 316
03/26/22 10:50:41.188 | 552.6653 | 1369.2541 | 53.8957 | 44.2393 | 9.6565 | 31.1617 | 51.0543 | 0 | 1788.2914 | 92.6921 | 84.0914 | 8.6007 | 24.2664 | 70.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0181 | 462.2301 | 459.2801 | 462.8701 | 409.2601 | 439.1201 | 417.5301 | 313.0301 | 0.5664 | 0.56807 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6659443.8456 | 7683772.4552 | 7683772.4552 | 62.428 | 62.1477 | 1.0017 | 0.99792 | 685598.0652 | 892099.9763 | 461.4601 | 0.47241 | 0 | 0 | 31.1617 | 24.2664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017865 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 577.657 | 1368.1572 | 54.0904 | 43.9863 | 31.0773 | 1787.2209 | 81.8335 | 24.7656 | 460.9008 | 0.0068144 | 60.0072 | 0.54563 | 0.63918 | 90.7717 | 2.2545 | 0.14487 | 0.24957 | 4.6677 | 1.1976 | 0.30354 | 0 | 100 | 577.3 | 316 | 112.83 | 106.62 | 100.4 | 305.6 | 4 | 94.35 | 42.73 | 4 | 37.94 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.18 | 0 | 38.63 | 60 | 60 | 106.83 | 91.24 | 90.29 | 0 | 100.4 | 2.36 | 93.5 | 43.41 | 112.83 | 12.28 | 106.62 | 110 | 0 | 15654 | 82.48 | 116.1 | 221.44 | 215.25 | 220.75 | 0 | 39.13 | 51.66 | 14415 | 94.35 | 42.73 | 37.94 | 0.87 | 42.73 | 0 | 607 | 428.8 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.6 | 311.2 | 0 | 305 | 100.45 | 15653 | 15654 | 316
03/26/22 10:50:46.189 | 551.7715 | 1367.422 | 53.8946 | 44.2379 | 9.6567 | 31.1204 | 51.0572 | 0 | 1787.8217 | 92.6984 | 84.0958 | 8.6026 | 24.1176 | 70.3721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.02 | 462.28 | 459.33 | 462.92 | 409.29 | 439.14 | 417.53 | 313.06 | 0.56737 | 0.4321 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6648604.4404 | 7683435.1243 | 7683435.1243 | 62.428 | 62.1476 | 1.0017 | 0.99792 | 684474.3864 | 891777.0864 | 461.51 | 0.47236 | 0 | 0 | 31.1204 | 24.1176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017872 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 577.4666 | 1368.1652 | 54.0901 | 43.9894 | 31.0756 | 1787.2589 | 81.8546 | 24.7619 | 460.9085 | 0.0068308 | 60.0073 | 0.54579 | 0.63968 | 90.7899 | 2.2494 | 0.14521 | 0.2492 | 4.6444 | 1.2039 | 0.30148 | 0 | 100 | 577.3 | 316 | 112.88 | 106.62 | 100.4 | 304.1 | 4 | 94.37 | 42.74 | 4 | 37.95 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.28 | 0 | 38.64 | 60 | 60 | 106.93 | 91.29 | 90.35 | 0 | 100.4 | 2.36 | 93.55 | 43.42 | 112.9 | 12.24 | 106.62 | 110 | 0 | 15654 | 82.5 | 116.1 | 221.44 | 215.25 | 220.75 | 0 | 39.25 | 51.61 | 14420 | 94.38 | 42.74 | 37.95 | 0.86 | 42.74 | 0 | 608 | 426.2 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 312.6 | 0 | 306.3 | 100.47 | 15652 | 15654 | 316
03/26/22 10:50:51.188 | 551.1159 | 1365.693 | 53.8918 | 44.2344 | 9.6574 | 31.3874 | 51.0638 | 0 | 1781.4685 | 92.72 | 84.1103 | 8.6097 | 24.0945 | 70.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 462.44 | 459.48 | 463.06 | 409.28 | 439.17 | 417.43 | 313.11 | 0.56814 | 0.60979 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6640937.2371 | 7662343.3119 | 7662343.3119 | 62.428 | 62.1474 | 1.0017 | 0.99792 | 683609.0796 | 888605.9612 | 461.66 | 0.47221 | 0 | 0 | 31.3874 | 24.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017883 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 577.2691 | 1368.1586 | 54.0898 | 43.9924 | 31.0759 | 1787.2459 | 81.8757 | 24.7589 | 460.9167 | 0.0068485 | 60.0075 | 0.54596 | 0.64186 | 90.8082 | 2.2537 | 0.14559 | 0.2488 | 4.6482 | 1.2099 | 0.30009 | 0 | 100 | 576.8 | 314 | 113.08 | 106.62 | 100.4 | 306.3 | 4 | 94.46 | 42.73 | 4 | 37.94 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.35 | 0 | 38.63 | 60 | 60 | 107 | 91.33 | 90.37 | 0 | 100.4 | 2.36 | 93.59 | 43.41 | 113.08 | 12.15 | 106.62 | 110 | 0 | 15654 | 82.5 | 116.1 | 221.44 | 215.25 | 220.75 | 0 | 39.3 | 51.54 | 14425 | 94.47 | 42.73 | 37.94 | 0.87 | 42.73 | 0 | 608 | 425.6 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 312.3 | 0 | 306 | 100.37 | 15653 | 15654 | 316
03/26/22 10:50:56.188 | 551.7885 | 1367.6181 | 53.8909 | 44.234 | 9.657 | 31.7465 | 51.071 | 0 | 1778.0881 | 92.7272 | 84.1158 | 8.6115 | 23.8195 | 70.3564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0141 | 462.4401 | 459.4801 | 463.0601 | 409.2801 | 439.1701 | 417.4301 | 313.1101 | 0.56745 | 0.86668 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6649321.9007 | 7651097.7562 | 7651097.7562 | 62.428 | 62.1474 | 1.0017 | 0.99792 | 684464.2076 | 887186.8861 | 461.6601 | 0.47221 | 0 | 0 | 31.7465 | 23.8195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017888 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 577.0777 | 1368.1683 | 54.0894 | 43.9955 | 31.0797 | 1787.1811 | 81.8968 | 24.7527 | 460.9252 | 0.0068668 | 60.0076 | 0.54612 | 0.64758 | 90.8266 | 2.2475 | 0.146 | 0.24836 | 4.6941 | 1.2156 | 0.2993 | 0 | 100 | 577.3 | 315 | 113 | 106.64 | 100.4 | 304.2 | 4 | 94.44 | 42.74 | 4 | 37.95 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.38 | 0 | 38.64 | 60 | 60 | 107.03 | 91.35 | 90.35 | 0 | 100.4 | 2.36 | 93.61 | 43.42 | 113.03 | 12.22 | 106.66 | 110 | 0 | 15654 | 82.53 | 116.1 | 221.44 | 215.25 | 220.75 | 0 | 39.4 | 51.5 | 14430 | 94.45 | 42.74 | 37.95 | 0.88 | 42.74 | 0 | 608 | 426.8 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.2 | 312.2 | 0 | 306 | 100.38 | 15653 | 15654 | 314
03/26/22 10:51:01.189 | 552.7128 | 1369.9457 | 53.8902 | 44.2349 | 9.6553 | 31.4184 | 51.0657 | 0 | 1779.6158 | 92.7416 | 84.1269 | 8.6146 | 23.7801 | 70.4283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.018 | 462.57 | 459.58 | 463.15 | 409.3 | 439.17 | 417.29 | 313.13 | 0.56653 | 0.91241 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6660212.481 | 7658391.8455 | 7658391.8455 | 62.428 | 62.1472 | 1.0017 | 0.99792 | 685737.8552 | 887679.3817 | 461.7667 | 0.47354 | 0 | 0 | 31.4184 | 23.7801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017891 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 576.8906 | 1368.1871 | 54.0891 | 43.9986 | 31.0862 | 1787.1366 | 81.9179 | 24.7438 | 460.9337 | 0.0067985 | 60.0077 | 0.54628 | 0.65337 | 90.8449 | 2.2494 | 0.14642 | 0.24789 | 4.7299 | 1.2211 | 0.29827 | 0 | 100 | 577.2 | 316 | 113.1 | 106.68 | 100.38 | 303.7 | 4 | 94.47 | 42.74 | 4 | 37.95 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.43 | 0 | 38.64 | 60 | 60 | 107.1 | 91.38 | 90.45 | 0 | 100.38 | 2.36 | 93.63 | 43.42 | 113.1 | 12.2 | 106.68 | 110 | 0 | 15654 | 82.53 | 116.1 | 221.31 | 215.25 | 220.63 | 0 | 39.46 | 51.42 | 14435 | 94.47 | 42.74 | 37.95 | 0.88 | 42.74 | 0 | 608 | 427.1 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 312.9 | 0 | 306.7 | 100.43 | 15653 | 15654 | 317
03/26/22 10:51:06.188 | 551.7024 | 1367.551 | 53.8907 | 44.2362 | 9.6545 | 30.6143 | 51.0467 | 0 | 1779.5229 | 92.7501 | 84.134 | 8.6161 | 24.7976 | 70.4828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 462.6101 | 459.6101 | 463.1901 | 409.2701 | 439.1601 | 417.2401 | 313.1201 | 0.56755 | 0.71984 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6647333.3545 | 7660400.6944 | 7660400.6944 | 62.428 | 62.1472 | 1.0017 | 0.99792 | 684539.138 | 887632.014 | 461.8034 | 0.47495 | 0 | 0 | 30.6143 | 24.7976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017895 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 576.6955 | 1368.1916 | 54.0887 | 44.0016 | 31.0811 | 1787.1208 | 81.9391 | 24.7477 | 460.9425 | 0.0068175 | 60.0078 | 0.54645 | 0.65565 | 90.8633 | 2.2482 | 0.14685 | 0.2474 | 4.7502 | 1.2263 | 0.29922 | 0 | 100 | 577.3 | 314 | 113.13 | 106.7 | 100.47 | 305.4 | 4 | 94.5 | 42.74 | 4 | 37.95 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.45 | 0 | 38.65 | 60 | 60 | 107.15 | 91.4 | 90.47 | 0 | 100.47 | 2.36 | 93.64 | 43.43 | 113.15 | 12.19 | 106.7 | 110 | 0 | 15654 | 82.55 | 116.1 | 221.31 | 215.25 | 220.63 | 0 | 39.52 | 51.38 | 14440 | 94.51 | 42.75 | 37.96 | 0.88 | 42.75 | 0 | 608 | 426.6 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 311.6 | 0 | 305.4 | 100.4 | 15653 | 15654 | 314
03/26/22 10:51:11.188 | 551.0153 | 1365.5176 | 53.8915 | 44.2376 | 9.6539 | 30.8897 | 51.0496 | 0 | 1782.5575 | 92.7581 | 84.1412 | 8.6169 | 24.4687 | 70.4415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.015 | 462.6 | 459.59 | 463.19 | 409.26 | 439.23 | 417.21 | 313.11 | 0.56824 | 0.47487 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6639221.6332 | 7671116.8793 | 7671116.8793 | 62.428 | 62.1471 | 1.0017 | 0.99792 | 683722.7637 | 888835.9388 | 461.7934 | 0.47713 | 0 | 0 | 30.8897 | 24.4687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017893 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 576.4921 | 1368.1779 | 54.0883 | 44.0047 | 31.0775 | 1787.1149 | 81.9602 | 24.7488 | 460.9516 | 0.0067935 | 60.0079 | 0.54663 | 0.65619 | 90.8817 | 2.2545 | 0.1473 | 0.2469 | 4.756 | 1.2312 | 0.30057 | 0 | 100 | 577.5 | 312 | 113.15 | 106.74 | 100.43 | 305.7 | 4 | 94.52 | 42.75 | 4 | 37.96 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.5 | 0 | 38.65 | 60 | 60 | 107.18 | 91.42 | 90.49 | 0 | 100.43 | 2.37 | 93.67 | 43.43 | 113.15 | 12.21 | 106.74 | 110 | 0 | 15654 | 82.55 | 116.1 | 221.31 | 215.25 | 220.63 | 0 | 39.54 | 51.33 | 14445 | 94.51 | 42.75 | 37.96 | 0.88 | 42.75 | 0 | 607 | 430.6 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 311.9 | 0 | 305.7 | 100.4 | 15653 | 15654 | 314
03/26/22 10:51:16.189 | 550.9402 | 1366.0336 | 53.8925 | 44.2397 | 9.6528 | 31.0253 | 51.0811 | 0 | 1784.1729 | 92.7685 | 84.1513 | 8.6172 | 24.9092 | 70.4072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0131 | 462.5801 | 459.5601 | 463.1701 | 409.3301 | 439.3201 | 417.2501 | 313.1401 | 0.56837 | 0.34497 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6638459.5185 | 7680294.4066 | 7680294.4066 | 62.428 | 62.147 | 1.0017 | 0.99792 | 683702.0412 | 889812.75 | 461.7701 | 0.47859 | 0 | 0 | 31.0253 | 24.9092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017896 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 576.2825 | 1368.1513 | 54.0879 | 44.0077 | 31.0781 | 1787.1355 | 81.9814 | 24.7455 | 460.9604 | 0.0067041 | 60.008 | 0.54681 | 0.65444 | 90.9001 | 2.2532 | 0.14774 | 0.24637 | 4.7339 | 1.2359 | 0.30187 | 0 | 100 | 577.3 | 315 | 113.15 | 106.74 | 100.4 | 303.6 | 4 | 94.51 | 42.75 | 4 | 37.96 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.5 | 0 | 38.65 | 60 | 60 | 107.18 | 91.42 | 90.59 | 0 | 100.4 | 2.37 | 93.67 | 43.43 | 113.2 | 12.2 | 106.74 | 110 | 0 | 15654 | 82.57 | 116.08 | 221.31 | 215.25 | 220.63 | 0 | 39.59 | 51.29 | 14450 | 94.54 | 42.75 | 37.96 | 0.88 | 42.75 | 0 | 607 | 429.6 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 313 | 0 | 306.7 | 100.47 | 15653 | 15654 | 314
03/26/22 10:51:21.189 | 551.2322 | 1366.8955 | 53.8939 | 44.2429 | 9.6509 | 30.5613 | 51.0878 | 0 | 1790.0255 | 92.7838 | 84.1667 | 8.6171 | 25.9166 | 70.4146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.009 | 462.55 | 459.5 | 463.14 | 409.43 | 439.41 | 417.26 | 313.17 | 0.56813 | 0.030515 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6641631.4196 | 7707756.8949 | 7707756.8949 | 62.428 | 62.1468 | 1.0017 | 0.99792 | 684210.9097 | 892865.9978 | 461.73 | 0.48297 | 0 | 0 | 30.5613 | 25.9166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.01788 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 576.0737 | 1368.1298 | 54.0875 | 44.0108 | 31.0768 | 1787.1554 | 82.0027 | 24.7472 | 460.9688 | 0.0066573 | 60.0081 | 0.54699 | 0.65301 | 90.9186 | 2.2552 | 0.14819 | 0.24583 | 4.7239 | 1.2404 | 0.3031 | 0 | 100 | 577.6 | 316 | 113.05 | 106.76 | 100.45 | 303.7 | 4 | 94.46 | 42.76 | 4 | 37.98 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.45 | 0 | 38.66 | 60 | 60 | 107.1 | 91.38 | 90.57 | 0 | 100.45 | 2.36 | 93.64 | 43.44 | 113.05 | 12.3 | 106.76 | 110 | 0 | 15654 | 82.57 | 116.08 | 221.31 | 215.25 | 220.63 | 0 | 39.65 | 51.39 | 14455 | 94.46 | 42.76 | 37.98 | 0.87 | 42.76 | 0 | 607 | 427.9 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 313.5 | 0 | 307.2 | 100.47 | 15653 | 15654 | 315
03/26/22 10:51:26.188 | 551.7067 | 1367.4013 | 53.8962 | 44.2461 | 9.65 | 30.8954 | 51.0665 | 0 | 1797.6896 | 92.7997 | 84.1828 | 8.617 | 25.3003 | 70.4427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0091 | 462.5501 | 459.5001 | 463.1401 | 409.4301 | 439.4101 | 417.2601 | 313.1701 | 0.56764 | -0.24601 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6647372.1098 | 7734958.1057 | 7734958.1057 | 62.428 | 62.1467 | 1.0017 | 0.99792 | 684861.8559 | 896079.557 | 461.7301 | 0.48297 | 0 | 0 | 30.8954 | 25.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017865 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 575.8706 | 1368.1217 | 54.087 | 44.0139 | 31.07 | 1787.2227 | 82.0239 | 24.7551 | 460.9769 | 0.0066746 | 60.0081 | 0.54717 | 0.64937 | 90.9371 | 2.2523 | 0.14862 | 0.24528 | 4.7699 | 1.2447 | 0.30387 | 0 | 100 | 578.1 | 316 | 113.03 | 106.74 | 100.54 | 307.8 | 4 | 94.45 | 42.78 | 4 | 37.99 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.38 | 0 | 38.68 | 60 | 60 | 107.03 | 91.35 | 90.65 | 0 | 100.54 | 2.36 | 93.61 | 43.46 | 113.03 | 12.29 | 106.74 | 110 | 0 | 15654 | 82.59 | 116.08 | 221.31 | 215.25 | 220.63 | 0 | 39.81 | 51.45 | 14460 | 94.45 | 42.78 | 37.99 | 0.86 | 42.78 | 0 | 607 | 427.2 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.2 | 311.2 | 0 | 305 | 100.56 | 15653 | 15654 | 316
03/26/22 10:51:31.188 | 551.4515 | 1367.5458 | 53.8974 | 44.2472 | 9.6502 | 31.121 | 51.0698 | 0 | 1798.3295 | 92.8054 | 84.1885 | 8.6168 | 24.9605 | 70.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0091 | 462.5501 | 459.5001 | 463.1401 | 409.4301 | 439.4101 | 417.2601 | 313.1701 | 0.5679 | -0.37284 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6644766.9872 | 7742159.0678 | 7742159.0678 | 62.428 | 62.1466 | 1.0017 | 0.99792 | 684536.2577 | 897004.8631 | 461.7301 | 0.48297 | 0 | 0 | 31.121 | 24.9605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.01787 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 575.663 | 1368.1028 | 54.0866 | 44.0169 | 31.0666 | 1787.2951 | 82.0452 | 24.7596 | 460.985 | 0.0065836 | 60.0082 | 0.54735 | 0.64488 | 90.9556 | 2.2428 | 0.14904 | 0.24471 | 4.8389 | 1.2488 | 0.30443 | 0 | 100 | 578.9 | 316 | 113.03 | 106.72 | 100.68 | 307.9 | 4 | 94.45 | 42.79 | 4 | 38 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.38 | 0 | 38.69 | 60 | 60 | 107.05 | 91.36 | 90.65 | 0 | 100.68 | 2.36 | 93.61 | 43.47 | 113 | 12.29 | 106.72 | 110 | 0 | 15654 | 82.59 | 116.1 | 221.31 | 215.25 | 220.63 | 0 | 39.89 | 51.43 | 14466 | 94.44 | 42.79 | 38 | 0.85 | 42.79 | 0 | 608 | 428.6 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 312.5 | 0 | 306.2 | 100.61 | 15656 | 15654 | 315
03/26/22 10:51:36.188 | 550.7282 | 1365.5537 | 53.9034 | 44.2518 | 9.6516 | 31.5499 | 51.0686 | 0 | 1787.8011 | 92.8277 | 84.2117 | 8.6161 | 23.8639 | 70.4712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.003 | 462.53 | 459.42 | 463.12 | 409.81 | 439.69 | 417.41 | 313.36 | 0.56899 | 0.13695 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6636424.2122 | 7694868.5844 | 7694868.5844 | 62.4279 | 62.1463 | 1.0017 | 0.99792 | 683538.7978 | 891749.9227 | 461.69 | 0.49167 | 0 | 0 | 31.5499 | 23.8639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017879 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 575.4574 | 1368.088 | 54.0862 | 44.02 | 31.0654 | 1787.3585 | 82.0665 | 24.7617 | 460.9928 | 0.0065135 | 60.0081 | 0.54752 | 0.64124 | 90.9741 | 2.2385 | 0.14945 | 0.24412 | 4.8472 | 1.2527 | 0.30514 | 0 | 100 | 578.5 | 315 | 113.03 | 106.72 | 100.61 | 307.6 | 4 | 94.45 | 42.79 | 4 | 38 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.43 | 0 | 38.69 | 60 | 60 | 107.08 | 91.37 | 90.59 | 0 | 100.61 | 2.36 | 93.63 | 43.47 | 113.03 | 12.28 | 106.72 | 110 | 0 | 15654 | 82.59 | 116.1 | 221.31 | 215.25 | 220.63 | 0 | 39.95 | 51.41 | 14471 | 94.45 | 42.79 | 38 | 0.86 | 42.79 | 0 | 608 | 427.8 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 312.4 | 0 | 306.2 | 100.52 | 15653 | 15654 | 316
03/26/22 10:51:41.188 | 550.7625 | 1365.8272 | 53.9071 | 44.2545 | 9.6525 | 31.6307 | 51.0647 | 0 | 1786.6967 | 92.8377 | 84.2214 | 8.6164 | 23.7658 | 70.4844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0021 | 462.5201 | 459.4001 | 463.1101 | 409.8401 | 439.7101 | 417.3801 | 313.3701 | 0.56897 | 0.18394 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6636862.77 | 7691929.6471 | 7691929.6471 | 62.4279 | 62.1462 | 1.0017 | 0.99792 | 683528.3426 | 891396.0853 | 461.6768 | 0.49313 | 0 | 0 | 31.6307 | 23.7658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017877 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 575.2463 | 1368.0562 | 54.0858 | 44.0231 | 31.0639 | 1787.395 | 82.0879 | 24.76 | 461.0002 | 0.0064644 | 60.0081 | 0.54771 | 0.63856 | 90.9927 | 2.2369 | 0.14982 | 0.24352 | 4.8232 | 1.2565 | 0.30579 | 0 | 100 | 578.4 | 315 | 113.13 | 106.72 | 100.59 | 305.3 | 4 | 94.49 | 42.8 | 4 | 38.01 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.5 | 0 | 38.69 | 57 | 57 | 107.25 | 91.46 | 90.59 | 0 | 100.59 | 2.36 | 93.67 | 43.47 | 113.13 | 12.24 | 106.72 | 110 | 0 | 15654 | 82.61 | 116.1 | 221.31 | 215.25 | 220.63 | 0 | 40.05 | 51.53 | 14475 | 94.49 | 42.8 | 38.01 | 0.85 | 42.8 | 0 | 607 | 429.7 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.4 | 311.7 | 0 | 305.4 | 100.59 | 15655 | 15654 | 316
03/26/22 10:51:46.188 | 551.0343 | 1366.1111 | 53.9093 | 44.2563 | 9.6531 | 31.6066 | 51.0706 | 0 | 1784.3897 | 92.843 | 84.2263 | 8.6166 | 23.8081 | 70.4729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0021 | 462.5201 | 459.4001 | 463.1101 | 409.8401 | 439.7101 | 417.3801 | 313.3701 | 0.56869 | 0.37453 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6640158.6579 | 7680601.4716 | 7680601.4716 | 62.4279 | 62.1461 | 1.0017 | 0.99792 | 683817.5588 | 890046.1867 | 461.6767 | 0.49313 | 0 | 0 | 31.6066 | 23.8081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017883 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 575.0358 | 1368.027 | 54.0855 | 44.0262 | 31.0665 | 1787.3894 | 82.1092 | 24.7543 | 461.0074 | 0.0064149 | 60.008 | 0.54789 | 0.63812 | 91.0112 | 2.2277 | 0.15018 | 0.24292 | 4.8261 | 1.26 | 0.30642 | 0 | 100 | 577.2 | 315 | 113.13 | 106.74 | 100.4 | 306.8 | 4 | 94.5 | 42.78 | 4 | 37.99 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.55 | 0 | 38.68 | 56 | 56 | 107.48 | 91.58 | 90.63 | 0 | 100.4 | 2.37 | 93.7 | 43.46 | 113.15 | 12.23 | 106.74 | 110 | 0 | 15654 | 82.61 | 116.1 | 221.31 | 215.25 | 220.63 | 0 | 40.33 | 51.76 | 14480 | 94.51 | 42.78 | 37.99 | 0.88 | 42.78 | 0 | 608 | 427.7 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 313.3 | 0 | 307 | 100.37 | 15653 | 15654 | 317
03/26/22 10:51:51.188 | 551.3812 | 1366.6014 | 53.9195 | 44.2638 | 9.6557 | 30.826 | 51.0525 | 0 | 1787.1044 | 92.8614 | 84.2427 | 8.6187 | 25.387 | 70.4671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 462.5601 | 459.4101 | 463.1401 | 409.7501 | 439.6201 | 417.1701 | 313.3201 | 0.56825 | 0.21993 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6643645.6936 | 7695895.6897 | 7695895.6897 | 62.4279 | 62.146 | 1.0017 | 0.99792 | 684062.5223 | 891397.8657 | 461.7034 | 0.49671 | 0 | 0 | 30.826 | 25.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017874 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 574.8288 | 1368.0046 | 54.0851 | 44.0293 | 31.0675 | 1787.3437 | 82.1306 | 24.7503 | 461.0144 | 0.0064301 | 60.008 | 0.54807 | 0.64032 | 91.0298 | 2.2263 | 0.1505 | 0.24231 | 4.8359 | 1.2633 | 0.30724 | 0 | 100 | 576.5 | 315 | 113.15 | 106.78 | 100.26 | 306.9 | 4 | 94.51 | 42.76 | 4 | 37.98 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.58 | 0 | 38.66 | 56 | 56 | 107.6 | 91.65 | 90.59 | 0 | 100.4 | 2.37 | 93.71 | 43.44 | 113.18 | 12.27 | 106.78 | 110 | 0 | 15654 | 82.61 | 116.08 | 221.31 | 215.25 | 220.63 | 0 | 40.4 | 51.53 | 14485 | 94.52 | 42.76 | 37.98 | 0.89 | 42.76 | 0 | 608 | 428 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 312.7 | 0 | 306.5 | 100.37 | 15653 | 15654 | 315
03/26/22 10:51:56.188 | 551.9835 | 1368.8619 | 53.925 | 44.2676 | 9.6574 | 30.9248 | 51.0706 | 0 | 1790.1029 | 92.8691 | 84.2489 | 8.6202 | 25.3178 | 70.4943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.007 | 462.56 | 459.41 | 463.14 | 409.75 | 439.62 | 417.17 | 313.32 | 0.56763 | 0.17972 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6650973.9283 | 7706203.9676 | 7706203.9676 | 62.4279 | 62.1459 | 1.0017 | 0.99792 | 684728.8776 | 892478.4344 | 461.7034 | 0.49671 | 0 | 0 | 30.9248 | 25.3178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017871 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 574.6283 | 1368.0017 | 54.0848 | 44.0325 | 31.0714 | 1787.3279 | 82.1519 | 24.7445 | 461.0215 | 0.0064455 | 60.0079 | 0.54824 | 0.64186 | 91.0485 | 2.2249 | 0.15076 | 0.24171 | 4.8221 | 1.2664 | 0.30822 | 0 | 100 | 576.8 | 316 | 113.18 | 106.82 | 100.24 | 305.4 | 4 | 94.52 | 42.76 | 4 | 37.96 | 43.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.58 | 0 | 38.65 | 56 | 56 | 107.7 | 91.7 | 90.45 | 0 | 100.24 | 2.37 | 93.71 | 43.43 | 113.18 | 12.3 | 106.82 | 110 | 0 | 15654 | 82.61 | 116.05 | 221.31 | 215.25 | 220.63 | 0 | 40.26 | 51.08 | 14490 | 94.52 | 42.76 | 37.98 | 0.91 | 42.76 | 0 | 608 | 428.4 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.8 | 311.7 | 0 | 305.4 | 100.31 | 15654 | 15654 | 316
03/26/22 10:52:01.188 | 552.9766 | 1369.987 | 53.9311 | 44.2713 | 9.6597 | 31.2878 | 51.082 | 0 | 1795.9348 | 92.8767 | 84.2546 | 8.622 | 24.1126 | 70.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.007 | 462.56 | 459.41 | 463.14 | 409.75 | 439.62 | 417.17 | 313.32 | 0.56661 | -0.039785 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6663263.9913 | 7735432.7561 | 7735432.7561 | 62.4279 | 62.1458 | 1.0017 | 0.99792 | 685756.7204 | 895800.7122 | 461.7033 | 0.49671 | 0 | 0 | 31.2878 | 24.1126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.01786 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 574.4453 | 1368.0318 | 54.0846 | 44.0356 | 31.074 | 1787.2886 | 82.1733 | 24.7387 | 461.0287 | 0.0064175 | 60.0079 | 0.5484 | 0.64697 | 91.0671 | 2.2149 | 0.151 | 0.24112 | 4.7214 | 1.2693 | 0.30904 | 0 | 100 | 576.3 | 315 | 113.25 | 106.84 | 100.28 | 302.7 | 4 | 94.56 | 42.75 | 4 | 37.96 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.6 | 0 | 38.64 | 56 | 56 | 107.75 | 91.73 | 90.31 | 0 | 100.28 | 2.37 | 93.72 | 43.42 | 113.25 | 12.28 | 106.84 | 110 | 0 | 15654 | 82.61 | 116.03 | 221.31 | 215.25 | 220.63 | 0 | 40.05 | 50.71 | 14495 | 94.56 | 42.75 | 37.96 | 0.94 | 42.75 | 0 | 608 | 427.6 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.5 | 308.9 | 0 | 302.7 | 100.26 | 15653 | 15654 | 316
03/26/22 10:52:06.188 | 551.7042 | 1366.2298 | 53.9402 | 44.2762 | 9.664 | 31.2223 | 51.063 | 0 | 1787.6772 | 92.8867 | 84.2616 | 8.6251 | 24.2312 | 70.4642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 462.6101 | 459.4801 | 463.1801 | 409.3201 | 439.0901 | 416.7001 | 313.0301 | 0.56739 | 0.17783 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6647862.3122 | 7702732.3767 | 7702732.3767 | 62.4279 | 62.1457 | 1.0017 | 0.99792 | 683875.6042 | 891680.8621 | 461.7567 | 0.49304 | 0 | 0 | 31.2223 | 24.2312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017878 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 574.2582 | 1368.05 | 54.0843 | 44.0388 | 31.0767 | 1787.2629 | 82.1946 | 24.734 | 461.0361 | 0.0064334 | 60.0079 | 0.54856 | 0.65106 | 91.0857 | 2.201 | 0.15122 | 0.24051 | 4.6652 | 1.2719 | 0.31062 | 0 | 100 | 576.6 | 315 | 113.3 | 106.86 | 100.28 | 304.2 | 4 | 94.59 | 42.75 | 4 | 37.96 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.65 | 0 | 38.64 | 56 | 56 | 107.85 | 91.78 | 89.96 | 0 | 100.24 | 2.37 | 93.75 | 43.42 | 113.3 | 12.27 | 106.86 | 110 | 0 | 15654 | 82.63 | 115.98 | 221.31 | 215.25 | 220.63 | 0 | 39.85 | 50.44 | 14500 | 94.59 | 42.75 | 37.96 | 0.94 | 42.75 | 0 | 607 | 427.9 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 310.4 | 0 | 304.2 | 100.28 | 15653 | 15654 | 315
03/26/22 10:52:11.188 | 551.3075 | 1364.8363 | 53.9454 | 44.2785 | 9.6669 | 31.361 | 51.0692 | 0 | 1783.8013 | 92.8919 | 84.265 | 8.6269 | 23.9523 | 70.5084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.015 | 462.6 | 459.47 | 463.16 | 409.14 | 438.85 | 416.51 | 312.88 | 0.56752 | 0.31202 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6643195.1827 | 7687274.5618 | 7687274.5618 | 62.4278 | 62.1457 | 1.0017 | 0.99792 | 683177.8692 | 889747.082 | 461.7434 | 0.49234 | 0 | 0 | 31.361 | 23.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017874 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 574.0558 | 1368.0302 | 54.084 | 44.0419 | 31.0805 | 1787.243 | 82.2159 | 24.7243 | 461.0434 | 0.0064058 | 60.008 | 0.54873 | 0.65203 | 91.1043 | 2.2114 | 0.15142 | 0.23991 | 4.6708 | 1.2743 | 0.31197 | 0 | 100 | 576 | 316 | 113.3 | 106.9 | 100.17 | 306.3 | 4 | 94.59 | 42.74 | 4 | 37.95 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.73 | 0 | 38.63 | 56 | 56 | 107.9 | 91.8 | 89.77 | 0 | 100.16 | 2.37 | 93.77 | 43.41 | 113.3 | 12.31 | 106.9 | 110 | 0 | 15654 | 82.63 | 115.96 | 221.31 | 215.25 | 220.63 | 0 | 39.6 | 50.14 | 14505 | 94.59 | 42.74 | 37.95 | 0.95 | 42.74 | 0 | 607 | 427.6 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 312.5 | 0 | 306.3 | 100.17 | 15654 | 15654 | 316
03/26/22 10:52:16.188 | 551.3259 | 1364.3718 | 53.9514 | 44.2808 | 9.6706 | 31.6834 | 51.0669 | 0 | 1780.3899 | 92.8991 | 84.2703 | 8.6288 | 23.6388 | 70.4708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.018 | 462.61 | 459.47 | 463.14 | 408.97 | 438.56 | 416.3 | 312.72 | 0.56721 | 0.48568 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6643690.2632 | 7673919.3069 | 7673919.3069 | 62.4278 | 62.1456 | 1.0017 | 0.99792 | 682945.0956 | 888044.7188 | 461.74 | 0.49162 | 0 | 0 | 31.6834 | 23.6388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.01789 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 573.8491 | 1367.9998 | 54.0838 | 44.045 | 31.0846 | 1787.2134 | 82.2372 | 24.7142 | 461.0505 | 0.0064212 | 60.008 | 0.5489 | 0.65307 | 91.1228 | 2.2196 | 0.15161 | 0.23928 | 4.6731 | 1.2764 | 0.31322 | 0 | 100 | 575.6 | 316 | 113.45 | 106.96 | 100.1 | 302 | 4 | 94.66 | 42.71 | 4 | 37.93 | 43.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.8 | 0 | 38.61 | 56 | 56 | 107.98 | 91.84 | 89.52 | 0 | 100.14 | 2.37 | 93.82 | 43.39 | 113.45 | 12.3 | 106.96 | 110 | 0 | 15654 | 82.63 | 115.89 | 221.31 | 215.25 | 220.63 | 0 | 39.42 | 50 | 14510 | 94.66 | 42.71 | 37.93 | 1 | 42.71 | 0 | 607 | 424.7 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.6 | 308.2 | 0 | 302 | 100.1 | 15653 | 15654 | 316
03/26/22 10:52:21.188 | 552.4285 | 1367.3291 | 53.9541 | 44.2816 | 9.6725 | 31.2921 | 51.0737 | 0 | 1775.5179 | 92.9053 | 84.2756 | 8.6297 | 23.9163 | 70.4551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 462.6101 | 459.4701 | 463.1301 | 408.9001 | 438.4001 | 416.1901 | 312.6301 | 0.56592 | 0.93577 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6656774.7737 | 7651878.5299 | 7651878.5299 | 62.4278 | 62.1455 | 1.0017 | 0.99792 | 684197.9224 | 885418.3479 | 461.7367 | 0.4909 | 0 | 0 | 31.2921 | 23.9163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017896 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 573.6401 | 1367.9622 | 54.0836 | 44.0482 | 31.0909 | 1787.1441 | 82.2585 | 24.7018 | 461.0577 | 0.006415 | 60.0081 | 0.54908 | 0.65578 | 91.1415 | 2.1892 | 0.15177 | 0.23864 | 4.7372 | 1.2782 | 0.3142 | 0 | 100 | 576.1 | 316 | 113.55 | 107 | 100.19 | 305.9 | 4 | 94.71 | 42.73 | 4 | 37.94 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.93 | 0 | 38.63 | 56 | 56 | 108.08 | 91.9 | 89.35 | 0 | 100.19 | 2.37 | 93.87 | 43.41 | 113.55 | 12.28 | 107 | 110 | 0 | 15654 | 82.63 | 115.84 | 221.31 | 215.25 | 220.63 | 0 | 39.22 | 49.91 | 14515 | 94.71 | 42.73 | 37.94 | 1 | 42.73 | 0 | 608 | 426.6 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 312.6 | 0 | 306.4 | 100.17 | 15652 | 15654 | 316
03/26/22 10:52:26.189 | 552.9133 | 1367.4271 | 53.9557 | 44.2814 | 9.6743 | 30.7171 | 51.075 | 0 | 1778.4132 | 92.9145 | 84.2841 | 8.6304 | 25.1904 | 70.4786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 462.6101 | 459.4701 | 463.1301 | 408.9001 | 438.4001 | 416.1901 | 312.6301 | 0.56542 | 0.85128 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6662094.9125 | 7663317.2713 | 7663317.2713 | 62.4278 | 62.1455 | 1.0017 | 0.99792 | 684665.4392 | 886493.2278 | 461.7368 | 0.4909 | 0 | 0 | 30.7171 | 25.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017894 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 573.4544 | 1367.9782 | 54.0833 | 44.0513 | 31.0908 | 1787.0174 | 82.2798 | 24.6997 | 461.0648 | 0.0064303 | 60.0082 | 0.54923 | 0.66491 | 91.1601 | 2.1772 | 0.15194 | 0.23797 | 4.7249 | 1.2797 | 0.31497 | 0 | 100 | 576.3 | 315 | 113.6 | 107.04 | 100.23 | 306.5 | 4 | 94.74 | 42.74 | 4 | 37.95 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.98 | 0 | 38.64 | 56 | 56 | 108.2 | 91.96 | 89.15 | 0 | 100.23 | 2.37 | 93.91 | 43.42 | 113.6 | 12.3 | 107.04 | 110 | 0 | 15654 | 82.63 | 115.77 | 221.31 | 215.25 | 220.63 | 0 | 39.04 | 49.85 | 14520 | 94.74 | 42.74 | 37.95 | 1.01 | 42.74 | 0 | 608 | 427 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.9 | 311.7 | 0 | 305.5 | 100.16 | 15653 | 15654 | 316
03/26/22 10:52:31.187 | 552.918 | 1367.4168 | 53.9563 | 44.2803 | 9.676 | 30.3395 | 51.0793 | 0 | 1785.1122 | 92.9233 | 84.2923 | 8.631 | 25.981 | 70.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.02 | 462.61 | 459.47 | 463.13 | 408.9 | 438.4 | 416.19 | 312.63 | 0.56542 | 0.48456 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6661567.4314 | 7690947.0427 | 7690947.0427 | 62.4278 | 62.1454 | 1.0017 | 0.99792 | 684567.2426 | 889488.5868 | 461.7367 | 0.4909 | 0 | 0 | 30.3395 | 25.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017885 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 573.2656 | 1367.9853 | 54.0831 | 44.0544 | 31.0843 | 1787.0062 | 82.3012 | 24.7092 | 461.072 | 0.0063589 | 60.0084 | 0.54939 | 0.66747 | 91.1787 | 2.1733 | 0.15211 | 0.23728 | 4.727 | 1.2811 | 0.31558 | 0 | 100 | 575.9 | 316 | 113.53 | 107.08 | 100.17 | 302.3 | 4 | 94.7 | 42.74 | 4 | 37.95 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.9 | 0 | 38.63 | 56 | 56 | 108.15 | 91.94 | 89.03 | 0 | 100.16 | 2.37 | 93.89 | 43.41 | 113.5 | 12.37 | 107.08 | 110 | 0 | 15654 | 82.63 | 115.72 | 221.31 | 215.25 | 220.63 | 0 | 38.87 | 49.81 | 14525 | 94.7 | 42.74 | 37.95 | 1.05 | 42.74 | 0 | 607 | 425.2 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.9 | 308.5 | 0 | 302.3 | 100.16 | 15654 | 15654 | 316
03/26/22 10:52:36.188 | 554.5362 | 1370.8179 | 53.9572 | 44.276 | 9.6811 | 31.6355 | 51.0793 | 0 | 1789.9274 | 92.9453 | 84.3114 | 8.6339 | 24.1876 | 70.4761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0101 | 462.5401 | 459.4101 | 463.0201 | 408.9201 | 438.0901 | 416.0401 | 312.4801 | 0.5635 | 0.36796 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6682302.9875 | 7720171.5593 | 7720171.5593 | 62.4278 | 62.1451 | 1.0017 | 0.99792 | 686171.4771 | 892795.9748 | 461.6567 | 0.48665 | 0 | 0 | 31.6355 | 24.1876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017885 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 573.0846 | 1368.0097 | 54.0828 | 44.0575 | 31.0874 | 1787.0466 | 82.3227 | 24.706 | 461.0785 | 0.0063512 | 60.0084 | 0.54954 | 0.66824 | 91.1975 | 2.1803 | 0.15228 | 0.23652 | 4.7207 | 1.2822 | 0.31547 | 0 | 100 | 576.6 | 315 | 113.53 | 107.08 | 100.28 | 306.3 | 4 | 94.69 | 42.74 | 4 | 37.95 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.88 | 0 | 38.64 | 56 | 56 | 108.13 | 91.92 | 88.91 | 0 | 100.28 | 2.37 | 93.86 | 43.42 | 113.53 | 12.37 | 107.08 | 110 | 0 | 15654 | 82.63 | 115.67 | 221.31 | 215.25 | 220.63 | 0 | 38.7 | 49.81 | 14530 | 94.7 | 42.75 | 37.96 | 1.06 | 42.75 | 0 | 607 | 428 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 311.1 | 0 | 304.8 | 100.23 | 15653 | 15654 | 314
03/26/22 10:52:41.188 | 555.2048 | 1371.8914 | 53.9578 | 44.2726 | 9.6852 | 30.9957 | 51.0849 | 0 | 1788.8591 | 92.9591 | 84.3228 | 8.6364 | 24.5171 | 70.4877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.005 | 462.52 | 459.39 | 462.99 | 408.89 | 438.04 | 416.03 | 312.45 | 0.56277 | 0.48869 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6689782.8937 | 7718096.1289 | 7718096.1289 | 62.4278 | 62.145 | 1.0017 | 0.99792 | 686708.7876 | 892261.4344 | 461.6334 | 0.48596 | 0 | 0 | 30.9957 | 24.5171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017881 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 572.9058 | 1368.0393 | 54.0826 | 44.0606 | 31.0885 | 1787.0648 | 82.3442 | 24.7015 | 461.0849 | 0.0063 | 60.0085 | 0.54969 | 0.67045 | 91.2163 | 2.1885 | 0.15247 | 0.23574 | 4.7215 | 1.283 | 0.3154 | 0 | 100 | 576.5 | 314 | 113.63 | 107.1 | 100.26 | 303.8 | 4 | 94.75 | 42.76 | 4 | 37.98 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.95 | 0 | 38.65 | 56 | 56 | 108.18 | 91.95 | 88.81 | 0 | 100.26 | 2.37 | 93.9 | 43.43 | 113.6 | 12.36 | 107.1 | 110 | 0 | 15654 | 82.63 | 115.62 | 221.31 | 215.25 | 220.63 | 0 | 38.53 | 49.81 | 14535 | 94.74 | 42.76 | 37.98 | 1.09 | 42.76 | 0 | 607 | 425.2 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.5 | 312.7 | 0 | 306.5 | 100.26 | 15656 | 15654 | 315
03/26/22 10:52:46.187 | 555.4153 | 1371.7004 | 53.9586 | 44.2684 | 9.6902 | 31.2515 | 51.0814 | 0 | 1789.3339 | 92.9738 | 84.3347 | 8.6392 | 24.1111 | 70.4861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 462.5 | 459.37 | 462.99 | 408.87 | 438.04 | 416.01 | 312.44 | 0.56253 | 0.47126 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6692530.9317 | 7722142.508 | 7722142.508 | 62.4278 | 62.1448 | 1.0017 | 0.99792 | 686613.1643 | 892496.5259 | 461.62 | 0.48741 | 0 | 0 | 31.2515 | 24.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017881 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 572.7283 | 1368.0709 | 54.0823 | 44.0636 | 31.0856 | 1787.0813 | 82.3657 | 24.7026 | 461.091 | 0.0063132 | 60.0085 | 0.54983 | 0.67286 | 91.2352 | 2.207 | 0.15266 | 0.23491 | 4.7235 | 1.2835 | 0.31528 | 0 | 100 | 575.3 | 316 | 113.53 | 107.1 | 100.05 | 304.7 | 4 | 94.7 | 42.76 | 4 | 37.98 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.95 | 0 | 38.66 | 56 | 56 | 108.18 | 91.95 | 88.66 | 0 | 100.05 | 2.37 | 93.9 | 43.44 | 113.53 | 12.39 | 107.1 | 110 | 0 | 15654 | 82.61 | 115.6 | 221.31 | 215.25 | 220.63 | 0 | 38.37 | 49.83 | 14540 | 94.7 | 42.76 | 37.98 | 1.13 | 42.76 | 0 | 607 | 427.4 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 311 | 0 | 304.7 | 100.14 | 15653 | 15654 | 316
03/26/22 10:52:51.187 | 554.9974 | 1369.667 | 53.9594 | 44.2636 | 9.6958 | 31.1127 | 51.0646 | 0 | 1788.6733 | 92.9903 | 84.3478 | 8.6425 | 24.7695 | 70.4799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 462.48 | 459.34 | 462.97 | 408.92 | 438.1 | 416.05 | 312.46 | 0.56299 | 0.38964 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6687481.8112 | 7723419.0245 | 7723419.0245 | 62.4278 | 62.1447 | 1.0017 | 0.99792 | 685770.9569 | 892307.0394 | 461.5967 | 0.48888 | 0 | 0 | 31.1127 | 24.7695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017881 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 572.5554 | 1368.1081 | 54.0819 | 44.0666 | 31.0865 | 1787.1293 | 82.3874 | 24.7026 | 461.0967 | 0.0063255 | 60.0085 | 0.54998 | 0.67397 | 91.2542 | 2.1828 | 0.15285 | 0.23402 | 4.6982 | 1.2838 | 0.31512 | 0 | 100 | 576.1 | 316 | 113.55 | 107.12 | 100.19 | 306.2 | 4 | 94.71 | 42.76 | 4 | 37.98 | 43.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112 | 0 | 38.65 | 56 | 56 | 108.25 | 91.99 | 88.6 | 0 | 100.19 | 2.37 | 93.93 | 43.43 | 113.6 | 12.39 | 107.12 | 110 | 0 | 15654 | 82.61 | 115.58 | 221.31 | 215.25 | 220.63 | 0 | 38.23 | 49.83 | 14545 | 94.73 | 42.76 | 37.98 | 1.18 | 42.76 | 0 | 607 | 424.9 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.9 | 311.6 | 0 | 305.4 | 100.16 | 15654 | 15654 | 317
03/26/22 10:52:56.187 | 554.761 | 1368.9755 | 53.9598 | 44.2618 | 9.6981 | 30.6473 | 51.0634 | 0 | 1787.9405 | 92.9977 | 84.3538 | 8.6439 | 25.4366 | 70.4786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 462.48 | 459.34 | 462.97 | 408.92 | 438.1 | 416.05 | 312.46 | 0.56323 | 0.36769 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6684093.1601 | 7721805.7788 | 7721805.7788 | 62.4279 | 62.1446 | 1.0017 | 0.99792 | 685249.0994 | 891798.6895 | 461.5967 | 0.48888 | 0 | 0 | 30.6473 | 25.4366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017869 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 572.3836 | 1368.1459 | 54.0816 | 44.0696 | 31.086 | 1787.1871 | 82.4091 | 24.7041 | 461.1023 | 0.0063375 | 60.0084 | 0.55012 | 0.67456 | 91.2732 | 2.1378 | 0.15305 | 0.23308 | 4.6431 | 1.2839 | 0.31501 | 0 | 100 | 576.4 | 316 | 113.55 | 107.16 | 100.17 | 305.3 | 4 | 94.71 | 42.76 | 4 | 37.98 | 43.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112 | 0 | 38.65 | 56 | 56 | 108.25 | 91.99 | 88.56 | 0 | 100.17 | 2.37 | 93.93 | 43.43 | 113.55 | 12.44 | 107.16 | 110 | 0 | 15654 | 82.61 | 115.55 | 221.31 | 215.25 | 220.63 | 0 | 38.06 | 49.75 | 14550 | 94.71 | 42.76 | 37.98 | 1.22 | 42.76 | 0 | 607 | 428.8 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 310.4 | 0 | 304.2 | 100.24 | 15654 | 15654 | 315
03/26/22 10:53:01.187 | 553.9289 | 1366.0543 | 53.9615 | 44.2573 | 9.7043 | 31.0256 | 51.0853 | 0 | 1795.2949 | 93.021 | 84.3736 | 8.6474 | 24.5664 | 70.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9921 | 462.4801 | 459.3401 | 462.9701 | 408.9201 | 438.1001 | 416.0501 | 312.4601 | 0.56408 | -0.19511 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6674382.5139 | 7755657.5929 | 7755657.5929 | 62.4279 | 62.1444 | 1.0017 | 0.99792 | 683786.8233 | 895464.0552 | 461.5967 | 0.48888 | 0 | 0 | 31.0256 | 24.5664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017867 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 572.2011 | 1368.1541 | 54.0813 | 44.0725 | 31.0841 | 1787.2541 | 82.4309 | 24.7053 | 461.1079 | 0.0063496 | 60.0084 | 0.55027 | 0.67282 | 91.2923 | 2.1269 | 0.15324 | 0.23211 | 4.6727 | 1.2837 | 0.3148 | 0 | 100 | 575.7 | 314 | 113.53 | 107.18 | 100.23 | 302.8 | 4 | 94.7 | 42.76 | 4 | 37.98 | 43.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.95 | 0 | 38.65 | 56 | 56 | 108.18 | 91.95 | 88.53 | 0 | 100.23 | 2.37 | 93.9 | 43.43 | 113.53 | 12.46 | 107.18 | 110 | 0 | 15654 | 82.59 | 115.53 | 221.31 | 215.25 | 220.51 | 0 | 37.83 | 49.65 | 14555 | 94.71 | 42.76 | 37.98 | 1.22 | 42.76 | 0 | 607 | 426.5 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 309.2 | 0 | 303 | 100.21 | 15654 | 15654 | 315
03/26/22 10:53:06.187 | 553.5716 | 1364.7847 | 53.9629 | 44.256 | 9.7069 | 31.1117 | 51.0845 | 0 | 1792.8073 | 93.0309 | 84.3817 | 8.6492 | 24.4855 | 70.4671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 462.44 | 459.3 | 462.96 | 408.94 | 438.16 | 416.09 | 312.48 | 0.56448 | -0.16239 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6670123.9813 | 7748922.8021 | 7748922.8021 | 62.4279 | 62.1443 | 1.0017 | 0.99792 | 683202.9324 | 894554.4316 | 461.5667 | 0.49108 | 0 | 0 | 31.1117 | 24.4855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017869 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 572.0119 | 1368.1432 | 54.081 | 44.0754 | 31.0853 | 1787.3054 | 82.4528 | 24.7027 | 461.1129 | 0.0063603 | 60.0083 | 0.55043 | 0.67088 | 91.3115 | 2.1391 | 0.15344 | 0.23111 | 4.6827 | 1.2833 | 0.31495 | 0 | 100 | 576.3 | 314 | 113.58 | 107.18 | 100.19 | 304.7 | 4 | 94.73 | 42.76 | 4 | 37.98 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 111.98 | 0 | 38.65 | 56 | 56 | 108.23 | 91.98 | 88.45 | 0 | 100.19 | 2.37 | 93.91 | 43.43 | 113.6 | 12.45 | 107.18 | 110 | 0 | 15654 | 82.59 | 115.53 | 221.19 | 215.25 | 220.51 | 0 | 37.6 | 49.61 | 14560 | 94.73 | 42.76 | 37.98 | 1.28 | 42.76 | 0 | 607 | 429.2 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.9 | 312.5 | 0 | 306.3 | 100.16 | 15654 | 15654 | 317
03/26/22 10:53:11.187 | 555.5554 | 1370.0386 | 53.9658 | 44.2546 | 9.7112 | 31.3299 | 51.0717 | 0 | 1785.3858 | 93.0461 | 84.3936 | 8.6525 | 24.2512 | 70.5084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 462.44 | 459.27 | 462.95 | 408.96 | 438.21 | 416.04 | 312.47 | 0.56245 | 0.5058 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6694147.2528 | 7721186.5057 | 7721186.5057 | 62.4279 | 62.1441 | 1.0017 | 0.99792 | 685359.933 | 891054.4021 | 461.5534 | 0.49471 | 0 | 0 | 31.3299 | 24.2512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017879 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 571.8286 | 1368.1513 | 54.0806 | 44.0783 | 31.0873 | 1787.2984 | 82.4746 | 24.6992 | 461.1176 | 0.0063705 | 60.0082 | 0.55058 | 0.67278 | 91.3308 | 2.1435 | 0.15362 | 0.23008 | 4.6847 | 1.2826 | 0.31515 | 0 | 100 | 575.6 | 314 | 113.7 | 107.18 | 100.1 | 306 | 4 | 94.79 | 42.78 | 4 | 37.99 | 44.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.08 | 0 | 38.66 | 56 | 56 | 108.33 | 92.03 | 88.37 | 0 | 100.14 | 2.38 | 93.96 | 43.44 | 113.7 | 12.39 | 107.18 | 110 | 0 | 15654 | 82.59 | 115.53 | 221.19 | 215.25 | 220.51 | 0 | 37.4 | 49.63 | 14565 | 94.79 | 42.78 | 37.99 | 1.31 | 42.78 | 0 | 607 | 426.2 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.6 | 311.7 | 0 | 305.4 | 100.1 | 15653 | 15654 | 316
03/26/22 10:53:16.187 | 557.726 | 1373.9506 | 53.9685 | 44.2539 | 9.7146 | 30.5926 | 51.0717 | 0 | 1782.9549 | 93.0615 | 84.4056 | 8.6559 | 25.3538 | 70.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 462.45 | 459.26 | 462.96 | 408.93 | 438.19 | 415.96 | 312.44 | 0.5602 | 0.96851 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6719722.701 | 7710768.7129 | 7710768.7129 | 62.4279 | 62.144 | 1.0017 | 0.99792 | 687739.0776 | 889304.421 | 461.5567 | 0.49759 | 0 | 0 | 30.5926 | 25.3538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017878 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 571.6579 | 1368.1819 | 54.0803 | 44.0812 | 31.0838 | 1787.2687 | 82.4966 | 24.7025 | 461.1221 | 0.0063801 | 60.008 | 0.55072 | 0.67761 | 91.3501 | 2.1866 | 0.1538 | 0.22903 | 4.6952 | 1.2817 | 0.31563 | 0 | 100 | 575.7 | 316 | 113.75 | 107.23 | 100.1 | 305.9 | 4 | 94.82 | 42.76 | 4 | 37.98 | 44.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.13 | 0 | 38.65 | 56 | 56 | 108.35 | 92.04 | 88.37 | 0 | 100.1 | 2.38 | 93.99 | 43.43 | 113.75 | 12.42 | 107.23 | 110 | 0 | 15654 | 82.59 | 115.53 | 221.19 | 215.14 | 220.51 | 0 | 37.24 | 49.65 | 14570 | 94.82 | 42.76 | 37.98 | 1.34 | 42.76 | 0 | 607 | 427.8 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7 | 312.1 | 0 | 305.9 | 100.12 | 15653 | 15654 | 316
03/26/22 10:53:21.186 | 557.2644 | 1372.6036 | 53.9708 | 44.2547 | 9.7161 | 30.5966 | 51.0851 | 0 | 1785.329 | 93.0763 | 84.4178 | 8.6585 | 25.5836 | 70.4918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.986 | 462.46 | 459.29 | 462.99 | 408.86 | 438.07 | 415.86 | 312.38 | 0.56056 | 0.7288 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6714161.1338 | 7723584.6335 | 7723584.6335 | 62.4278 | 62.1438 | 1.0017 | 0.99792 | 687064.7033 | 890486.7732 | 461.58 | 0.49612 | 0 | 0 | 30.5966 | 25.5836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017874 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 571.4918 | 1368.2213 | 54.0799 | 44.084 | 31.0814 | 1787.2518 | 82.5185 | 24.7033 | 461.1264 | 0.0063894 | 60.0079 | 0.55085 | 0.6822 | 91.3694 | 2.2183 | 0.15398 | 0.22798 | 4.6993 | 1.2806 | 0.3164 | 0 | 100 | 575.9 | 316 | 113.7 | 107.23 | 100.1 | 306.1 | 4 | 94.79 | 42.76 | 4 | 37.98 | 44.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.13 | 0 | 38.65 | 56 | 56 | 108.35 | 92.04 | 88.35 | 0 | 100.1 | 2.38 | 93.99 | 43.43 | 113.7 | 12.46 | 107.23 | 110 | 0 | 15654 | 82.59 | 115.53 | 221.19 | 215.14 | 220.51 | 0 | 37.07 | 49.65 | 14575 | 94.78 | 42.76 | 37.98 | 1.33 | 42.76 | 0 | 607 | 426.7 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7 | 312.2 | 0 | 306 | 100.12 | 15653 | 15654 | 314
03/26/22 10:53:26.187 | 555.9764 | 1369.4038 | 53.9719 | 44.2556 | 9.7163 | 30.3843 | 51.0799 | 0 | 1788.152 | 93.0832 | 84.4239 | 8.6593 | 25.8692 | 70.4617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 462.4601 | 459.2901 | 462.9901 | 408.8601 | 438.0701 | 415.8601 | 312.3801 | 0.56186 | 0.35473 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6698454.4932 | 7736844.9245 | 7736844.9245 | 62.4278 | 62.1438 | 1.0017 | 0.99792 | 685462.9745 | 891893.9791 | 461.5801 | 0.49612 | 0 | 0 | 30.3843 | 25.8692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017871 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 571.3167 | 1368.2369 | 54.0796 | 44.0868 | 31.0762 | 1787.264 | 82.5404 | 24.7096 | 461.1306 | 0.0063986 | 60.0077 | 0.551 | 0.68356 | 91.3888 | 2.2231 | 0.15416 | 0.22691 | 4.6975 | 1.2792 | 0.31734 | 0 | 100 | 576.1 | 316 | 113.73 | 107.23 | 100.19 | 306.5 | 4 | 94.8 | 42.78 | 4 | 37.99 | 44.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.1 | 0 | 38.66 | 56 | 56 | 108.35 | 92.04 | 88.35 | 0 | 100.14 | 2.38 | 93.98 | 43.44 | 113.7 | 12.44 | 107.23 | 110 | 0 | 15654 | 82.59 | 115.5 | 221.19 | 215.14 | 220.51 | 0 | 36.89 | 49.68 | 14580 | 94.79 | 42.78 | 37.99 | 1.28 | 42.78 | 0 | 607 | 426 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 309.4 | 0 | 303.2 | 100.23 | 15657 | 15654 | 315
03/26/22 10:53:31.187 | 555.0948 | 1367.2155 | 53.9734 | 44.257 | 9.7164 | 31.1855 | 51.0795 | 0 | 1788.4049 | 93.0926 | 84.432 | 8.6606 | 24.7141 | 70.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9841 | 462.5001 | 459.3301 | 463.0101 | 408.8801 | 437.9601 | 415.7801 | 312.3801 | 0.56275 | 0.21504 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6688537.4399 | 7737764.447 | 7737764.447 | 62.4278 | 62.1437 | 1.0017 | 0.99792 | 684367.5558 | 892018.9214 | 461.6134 | 0.49464 | 0 | 0 | 31.1855 | 24.7141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017877 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 571.1342 | 1368.2356 | 54.0792 | 44.0897 | 31.0744 | 1787.3119 | 82.5623 | 24.7149 | 461.1349 | 0.0064077 | 60.0076 | 0.55115 | 0.68168 | 91.4081 | 2.2234 | 0.15433 | 0.22584 | 4.6721 | 1.2776 | 0.31822 | 0 | 100 | 576 | 317 | 113.65 | 107.23 | 100.16 | 305.6 | 4 | 94.76 | 42.78 | 4 | 37.99 | 44.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.05 | 0 | 38.68 | 56 | 56 | 108.33 | 92.03 | 88.27 | 0 | 100.19 | 2.37 | 93.95 | 43.46 | 113.65 | 12.47 | 107.23 | 110 | 0 | 15654 | 82.59 | 115.5 | 221.19 | 215.14 | 220.51 | 0 | 36.75 | 49.76 | 14585 | 94.76 | 42.78 | 37.99 | 1.31 | 42.78 | 0 | 607 | 426.9 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 311.8 | 0 | 305.6 | 100.17 | 15652 | 15654 | 317
03/26/22 10:53:36.186 | 555.0854 | 1367.1897 | 53.9749 | 44.2584 | 9.7165 | 31.6347 | 51.0828 | 0 | 1786.6347 | 93.1012 | 84.4389 | 8.6623 | 24.0502 | 70.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.984 | 462.5 | 459.33 | 463.01 | 408.88 | 437.96 | 415.78 | 312.38 | 0.56276 | 0.3132 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6688811.9455 | 7730446.8167 | 7730446.8167 | 62.4278 | 62.1436 | 1.0017 | 0.99792 | 684352.0006 | 891109.3992 | 461.6134 | 0.49464 | 0 | 0 | 31.6347 | 24.0502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017883 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 570.9501 | 1368.2301 | 54.0789 | 44.0925 | 31.0756 | 1787.3601 | 82.5842 | 24.7158 | 461.139 | 0.0064167 | 60.0074 | 0.5513 | 0.67946 | 91.4275 | 2.2247 | 0.1545 | 0.22475 | 4.6193 | 1.2758 | 0.31955 | 0 | 100 | 575.7 | 314 | 113.75 | 107.23 | 100.12 | 303.8 | 4 | 94.82 | 42.78 | 4 | 37.99 | 44.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.13 | 0 | 38.68 | 56 | 56 | 108.4 | 92.07 | 88.21 | 0 | 100.16 | 2.38 | 93.99 | 43.46 | 113.75 | 12.42 | 107.23 | 110 | 0 | 15654 | 82.59 | 115.53 | 221.19 | 215.14 | 220.51 | 0 | 36.61 | 49.8 | 14590 | 94.82 | 42.78 | 37.99 | 1.35 | 42.78 | 0 | 608 | 425.9 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.9 | 313.3 | 0 | 307.1 | 100.16 | 15655 | 15654 | 315
03/26/22 10:53:41.186 | 556.9507 | 1371.7262 | 53.9778 | 44.2609 | 9.7169 | 30.8942 | 51.0702 | 0 | 1782.4749 | 93.1148 | 84.4499 | 8.6649 | 24.8605 | 70.4997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9891 | 462.5201 | 459.3801 | 463.0201 | 408.9101 | 437.8101 | 415.7901 | 312.3801 | 0.56088 | 0.78025 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6710642.0227 | 7716085.9758 | 7716085.9758 | 62.4278 | 62.1434 | 1.0017 | 0.99792 | 686625.2263 | 889058.5696 | 461.6401 | 0.48956 | 0 | 0 | 30.8942 | 24.8605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016213 | 0.017884 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 570.7693 | 1368.2322 | 54.0785 | 44.0953 | 31.0768 | 1787.38 | 82.6061 | 24.715 | 461.1433 | 0.0064258 | 60.0073 | 0.55144 | 0.67921 | 91.4468 | 2.2242 | 0.15466 | 0.22364 | 4.5973 | 1.2737 | 0.32111 | 0 | 100 | 576.1 | 314 | 113.75 | 107.27 | 100.19 | 305.9 | 4 | 94.82 | 42.8 | 4 | 38.01 | 44.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.18 | 0 | 38.69 | 56 | 56 | 108.5 | 92.11 | 88.21 | 0 | 100.21 | 2.38 | 94.02 | 43.47 | 113.75 | 12.44 | 107.27 | 110 | 0 | 15654 | 82.59 | 115.53 | 221.19 | 215.14 | 220.39 | 0 | 36.44 | 49.8 | 14595 | 94.82 | 42.8 | 38.01 | 1.29 | 42.8 | 0 | 608 | 426.2 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 312.2 | 0 | 305.9 | 100.19 | 15654 | 15654 | 314
03/26/22 10:53:46.186 | 555.8152 | 1368.8722 | 53.9797 | 44.2624 | 9.7173 | 31.0885 | 51.0636 | 0 | 1785.7109 | 93.122 | 84.4557 | 8.6663 | 25.0003 | 70.5484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 462.54 | 459.43 | 463.03 | 408.9 | 437.71 | 415.85 | 312.4 | 0.56206 | 0.40829 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6697129.3254 | 7731450.8518 | 7731450.8518 | 62.4278 | 62.1434 | 1.0017 | 0.99792 | 685196.5411 | 890671.737 | 461.6667 | 0.48448 | 0 | 0 | 31.0885 | 25.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017875 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 570.593 | 1368.2447 | 54.0782 | 44.0981 | 31.072 | 1787.4091 | 82.6279 | 24.7197 | 461.1475 | 0.0064349 | 60.0072 | 0.55158 | 0.6788 | 91.4662 | 2.2329 | 0.15482 | 0.22253 | 4.5609 | 1.2714 | 0.32264 | 0 | 100 | 576.3 | 315 | 113.8 | 107.29 | 100.23 | 305.3 | 4 | 94.83 | 42.8 | 4 | 38.01 | 44.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.18 | 0 | 38.69 | 56 | 56 | 108.5 | 92.12 | 88.21 | 0 | 100.23 | 2.38 | 94.02 | 43.47 | 113.78 | 12.46 | 107.29 | 110 | 0 | 15654 | 82.61 | 115.53 | 221.19 | 215.14 | 220.39 | 0 | 36.28 | 49.8 | 14600 | 94.83 | 42.8 | 38.01 | 1.27 | 42.8 | 0 | 607 | 427.5 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 311.8 | 0 | 305.6 | 100.24 | 15657 | 15654 | 313
03/26/22 10:53:51.187 | 555.2408 | 1367.3652 | 53.9825 | 44.2645 | 9.718 | 31.3875 | 51.0698 | 0 | 1786.3663 | 93.1312 | 84.4628 | 8.6684 | 24.3835 | 70.5083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9931 | 462.5501 | 459.4601 | 463.0301 | 408.9301 | 437.7001 | 415.9801 | 312.4401 | 0.56271 | 0.27113 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6690469.1477 | 7735420.5148 | 7735420.5148 | 62.4278 | 62.1433 | 1.0017 | 0.99792 | 684442.0671 | 890997.6167 | 461.6801 | 0.48085 | 0 | 0 | 31.3875 | 24.3835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.01788 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 570.4088 | 1368.2347 | 54.0778 | 44.1009 | 31.0724 | 1787.4375 | 82.6498 | 24.7168 | 461.1517 | 0.0064441 | 60.0071 | 0.55173 | 0.67755 | 91.4855 | 2.2329 | 0.15497 | 0.2214 | 4.5447 | 1.2689 | 0.32441 | 0 | 100 | 575.9 | 313 | 113.78 | 107.29 | 100.16 | 303.9 | 4 | 94.82 | 42.81 | 4 | 38.02 | 44.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.18 | 0 | 38.7 | 56 | 56 | 108.43 | 92.08 | 88.21 | 0 | 100.23 | 2.38 | 94.02 | 43.48 | 113.75 | 12.48 | 107.29 | 110 | 0 | 15654 | 82.61 | 115.58 | 221.19 | 215.03 | 220.39 | 0 | 36.14 | 49.88 | 14605 | 94.82 | 42.81 | 38.02 | 1.24 | 42.81 | 0 | 607 | 427.8 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 311.4 | 0 | 305.2 | 100.21 | 15655 | 15654 | 317
03/26/22 10:53:56.187 | 555.6364 | 1368.0568 | 53.9856 | 44.2672 | 9.7185 | 30.7035 | 51.0777 | 0 | 1783.0117 | 93.1409 | 84.4705 | 8.6705 | 24.8247 | 70.4993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9931 | 462.5501 | 459.4601 | 463.0301 | 408.9301 | 437.7001 | 415.9801 | 312.4401 | 0.56231 | 0.44784 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6694760.1368 | 7726171.1528 | 7726171.1528 | 62.4278 | 62.1432 | 1.0017 | 0.99792 | 684896.6308 | 889709.5662 | 461.6801 | 0.48085 | 0 | 0 | 30.7035 | 24.8247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.01789 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 570.2227 | 1368.2257 | 54.0774 | 44.1037 | 31.0761 | 1787.441 | 82.6716 | 24.7082 | 461.156 | 0.0064533 | 60.007 | 0.55188 | 0.67721 | 91.5049 | 2.2303 | 0.15512 | 0.22026 | 4.5436 | 1.2661 | 0.32626 | 0 | 100 | 576.1 | 316 | 113.73 | 107.29 | 100.19 | 305.6 | 4 | 94.8 | 42.81 | 4 | 38.02 | 44.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.2 | 0 | 38.71 | 56 | 56 | 108.48 | 92.11 | 88.21 | 0 | 100.17 | 2.38 | 94.03 | 43.49 | 113.73 | 12.49 | 107.29 | 110 | 0 | 15654 | 82.61 | 115.6 | 221.07 | 215.03 | 220.39 | 0 | 36.04 | 49.96 | 14610 | 94.8 | 42.81 | 38.02 | 1.24 | 42.81 | 0 | 607 | 424.6 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 308.8 | 0 | 302.6 | 100.19 | 15652 | 15654 | 315
03/26/22 10:54:01.186 | 555.6749 | 1368.3406 | 53.9871 | 44.2684 | 9.7186 | 30.4321 | 51.0764 | 0 | 1784.6838 | 93.145 | 84.4737 | 8.6713 | 25.664 | 70.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.993 | 462.55 | 459.46 | 463.03 | 408.93 | 437.7 | 415.98 | 312.44 | 0.56227 | 0.37074 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6694858.5486 | 7732228.2462 | 7732228.2462 | 62.4278 | 62.1431 | 1.0017 | 0.99792 | 684930.1353 | 890156.8489 | 461.68 | 0.48085 | 0 | 0 | 30.4321 | 25.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017875 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 570.0471 | 1368.2396 | 54.077 | 44.1065 | 31.0711 | 1787.4138 | 82.6935 | 24.7122 | 461.1603 | 0.0064626 | 60.0069 | 0.55202 | 0.67978 | 91.5242 | 2.2232 | 0.15525 | 0.21912 | 4.5454 | 1.2631 | 0.32805 | 0 | 100 | 576.3 | 316 | 113.78 | 107.29 | 100.23 | 306.7 | 4 | 94.83 | 42.8 | 4 | 38.01 | 44.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.2 | 0 | 38.7 | 56 | 56 | 108.45 | 92.09 | 88.21 | 0 | 100.24 | 2.38 | 94.03 | 43.48 | 113.78 | 12.46 | 107.29 | 110 | 0 | 15654 | 82.63 | 115.62 | 221.07 | 215.03 | 220.39 | 0 | 35.95 | 50.04 | 14615 | 94.83 | 42.8 | 38.01 | 1.25 | 42.8 | 0 | 607 | 429.2 | 459.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 311.6 | 0 | 305.4 | 100.19 | 15652 | 15654 | 315
03/26/22 10:54:06.187 | 556.1284 | 1369.2954 | 53.9932 | 44.2734 | 9.7198 | 31.6788 | 51.0863 | 0 | 1789.3855 | 93.1585 | 84.4835 | 8.6751 | 23.7788 | 70.4956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.976 | 462.45 | 459.42 | 462.92 | 409.06 | 437.75 | 416.32 | 312.53 | 0.56197 | 0.18134 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6701416.1429 | 7753739.0647 | 7753739.0647 | 62.4278 | 62.143 | 1.0017 | 0.99792 | 685407.7811 | 892500.4957 | 461.5967 | 0.47155 | 0 | 0 | 31.6788 | 23.7788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017876 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 569.8675 | 1368.2445 | 54.0767 | 44.1093 | 31.0711 | 1787.428 | 82.7153 | 24.7086 | 461.1644 | 0.0064713 | 60.0068 | 0.55217 | 0.6795 | 91.5435 | 2.2245 | 0.15537 | 0.21798 | 4.5476 | 1.2599 | 0.32934 | 0 | 100 | 576 | 315 | 113.73 | 107.29 | 100.17 | 305.3 | 4 | 94.8 | 42.8 | 4 | 38.01 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.18 | 0 | 38.7 | 56 | 56 | 108.45 | 92.09 | 88.17 | 0 | 100.19 | 2.38 | 94.02 | 43.48 | 113.75 | 12.48 | 107.29 | 110 | 0 | 15654 | 82.63 | 115.65 | 221.07 | 215.03 | 220.39 | 0 | 35.84 | 50.09 | 14620 | 94.82 | 42.8 | 38.01 | 1.21 | 42.8 | 0 | 607 | 429.6 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 309.7 | 0 | 303.5 | 100.19 | 15655 | 15654 | 316
03/26/22 10:54:11.186 | 555.6257 | 1367.5717 | 53.9968 | 44.276 | 9.7208 | 31.786 | 51.0859 | 0 | 1785.9225 | 93.1644 | 84.4874 | 8.6771 | 23.5746 | 70.4877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.976 | 462.45 | 459.42 | 462.92 | 409.06 | 437.75 | 416.32 | 312.53 | 0.56248 | 0.20601 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6695491.2024 | 7745913.9396 | 7745913.9396 | 62.4278 | 62.143 | 1.0017 | 0.99792 | 684735.997 | 891480.7244 | 461.5967 | 0.47155 | 0 | 0 | 31.786 | 23.5746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017885 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 569.6783 | 1368.224 | 54.0763 | 44.1121 | 31.0727 | 1787.4366 | 82.7371 | 24.7056 | 461.1683 | 0.0064797 | 60.0067 | 0.55232 | 0.6777 | 91.5628 | 2.2135 | 0.15548 | 0.21684 | 4.5432 | 1.2564 | 0.33029 | 0 | 100 | 576.1 | 316 | 113.85 | 107.29 | 100.19 | 305.1 | 4 | 94.87 | 42.8 | 4 | 38.01 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.25 | 0 | 38.7 | 56 | 56 | 108.53 | 92.13 | 88.13 | 0 | 100.24 | 2.38 | 94.05 | 43.48 | 113.85 | 12.43 | 107.29 | 110 | 0 | 15654 | 82.63 | 115.67 | 221.07 | 215.03 | 220.39 | 0 | 35.78 | 50.15 | 14624 | 94.87 | 42.8 | 38.01 | 1.23 | 42.8 | 0 | 607 | 426.6 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 311.3 | 0 | 305.1 | 100.19 | 15654 | 15654 | 316
03/26/22 10:54:16.186 | 555.1013 | 1366.3949 | 54.0017 | 44.28 | 9.7218 | 31.4966 | 51.063 | 0 | 1780.937 | 93.1722 | 84.4935 | 8.6787 | 24.2152 | 70.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9771 | 462.4201 | 459.4001 | 462.9001 | 409.0201 | 437.8201 | 416.3701 | 312.5301 | 0.56301 | 0.39059 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6688822.6832 | 7724987.1329 | 7724987.1329 | 62.4278 | 62.1429 | 1.0017 | 0.99792 | 684007.2508 | 888766.6676 | 461.5734 | 0.47085 | 0 | 0 | 31.4966 | 24.2152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017892 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 569.4872 | 1368.2013 | 54.076 | 44.115 | 31.0731 | 1787.4248 | 82.7588 | 24.7059 | 461.172 | 0.0064878 | 60.0065 | 0.55247 | 0.67661 | 91.5821 | 2.2112 | 0.15558 | 0.21568 | 4.5573 | 1.2527 | 0.33102 | 0 | 100 | 575.7 | 315 | 113.95 | 107.31 | 100.12 | 305.5 | 4 | 94.93 | 42.8 | 4 | 38.01 | 44.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.33 | 0 | 38.69 | 56 | 56 | 108.6 | 92.17 | 88.17 | 0 | 100.16 | 2.38 | 94.08 | 43.47 | 113.93 | 12.43 | 107.33 | 110 | 0 | 15654 | 82.63 | 115.7 | 221.07 | 215.03 | 220.39 | 0 | 35.68 | 50.17 | 14629 | 94.9 | 42.8 | 38.01 | 1.29 | 42.8 | 0 | 607 | 428.3 | 459.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.6 | 311.4 | 0 | 305.2 | 100.1 | 15654 | 15654 | 315
03/26/22 10:54:21.186 | 556.1036 | 1369.0735 | 54.0059 | 44.2849 | 9.721 | 31.3769 | 51.0764 | 0 | 1780.3331 | 93.1806 | 84.5031 | 8.6775 | 24.2892 | 70.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9811 | 462.3901 | 459.3601 | 462.9001 | 408.9701 | 437.9501 | 416.4001 | 312.5401 | 0.56202 | 0.64687 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6700848.4317 | 7717196.9162 | 7717196.9162 | 62.4278 | 62.1428 | 1.0017 | 0.99792 | 685296.1236 | 887982.5242 | 461.5501 | 0.47449 | 0 | 0 | 31.3769 | 24.2892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017894 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 569.3065 | 1368.2046 | 54.0756 | 44.1178 | 31.074 | 1787.3946 | 82.7806 | 24.7017 | 461.1757 | 0.0064956 | 60.0063 | 0.55262 | 0.67851 | 91.6014 | 2.2121 | 0.15567 | 0.21456 | 4.5863 | 1.2488 | 0.33156 | 0 | 100 | 576.5 | 314 | 113.95 | 107.35 | 100.26 | 305.4 | 4 | 94.92 | 42.8 | 4 | 38.01 | 44.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.33 | 0 | 38.69 | 56 | 56 | 108.58 | 92.16 | 88.21 | 0 | 100.24 | 2.38 | 94.09 | 43.47 | 113.95 | 12.44 | 107.35 | 110 | 0 | 15654 | 82.63 | 115.72 | 221.07 | 215.03 | 220.27 | 0 | 35.57 | 50.17 | 14635 | 94.92 | 42.8 | 38.01 | 1.29 | 42.8 | 0 | 607 | 427.9 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.5 | 311.7 | 0 | 305.4 | 100.26 | 15652 | 15654 | 314
03/26/22 10:54:26.186 | 556.7674 | 1370.9831 | 54.0091 | 44.2901 | 9.719 | 31.967 | 51.0636 | 0 | 1783.311 | 93.1902 | 84.5154 | 8.6748 | 23.871 | 70.4423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9851 | 462.3701 | 459.3401 | 462.9201 | 408.9801 | 438.1501 | 416.4901 | 312.6001 | 0.56146 | 0.62895 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6709371.8152 | 7727253.376 | 7727253.376 | 62.4277 | 62.1427 | 1.0017 | 0.99792 | 686251.83 | 889466.0129 | 461.5434 | 0.47738 | 0 | 0 | 31.967 | 23.871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016214 | 0.017893 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 569.1252 | 1368.2077 | 54.0752 | 44.1206 | 31.0784 | 1787.3722 | 82.8023 | 24.6956 | 461.1793 | 0.0065034 | 60.0062 | 0.55276 | 0.68001 | 91.6207 | 2.2154 | 0.15575 | 0.21344 | 4.5999 | 1.2447 | 0.332 | 0 | 100 | 577 | 316 | 114.03 | 107.35 | 100.35 | 306 | 4 | 94.95 | 42.8 | 4 | 38.01 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.33 | 0 | 38.7 | 56 | 56 | 108.58 | 92.16 | 88.27 | 0 | 100.37 | 2.38 | 94.09 | 43.48 | 114.03 | 12.4 | 107.35 | 110 | 0 | 15654 | 82.63 | 115.72 | 221.07 | 215.03 | 220.27 | 0 | 35.46 | 50.17 | 14640 | 94.95 | 42.8 | 38.01 | 1.23 | 42.8 | 0 | 607 | 429.3 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 311.8 | 0 | 305.6 | 100.24 | 15653 | 15654 | 317
03/26/22 10:54:31.186 | 556.518 | 1370.4721 | 54.0108 | 44.2925 | 9.7183 | 31.7792 | 51.0436 | 0 | 1784.2349 | 93.1965 | 84.5222 | 8.6742 | 24.2388 | 70.4184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9951 | 462.3301 | 459.3001 | 462.9601 | 408.9001 | 438.4901 | 416.5501 | 312.6601 | 0.56181 | 0.53744 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6706203.3943 | 7731176.0163 | 7731176.0163 | 62.4277 | 62.1426 | 1.0017 | 0.99792 | 685996.0015 | 889925.8059 | 461.5301 | 0.48318 | 0 | 0 | 31.7792 | 24.2388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016214 | 0.017892 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 568.9472 | 1368.2197 | 54.0748 | 44.1234 | 31.0812 | 1787.3391 | 82.824 | 24.6953 | 461.1829 | 0.0065113 | 60.0061 | 0.55291 | 0.68247 | 91.6399 | 2.2234 | 0.15582 | 0.21235 | 4.6056 | 1.2404 | 0.33239 | 0 | 100 | 576.3 | 317 | 114 | 107.37 | 100.23 | 305.6 | 4 | 94.94 | 42.81 | 4 | 38.02 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.33 | 0 | 38.71 | 56 | 56 | 108.58 | 92.16 | 88.27 | 0 | 100.23 | 2.38 | 94.09 | 43.49 | 114 | 12.43 | 107.37 | 110 | 0 | 15654 | 82.63 | 115.72 | 220.95 | 215.03 | 220.27 | 0 | 35.35 | 50.19 | 14645 | 94.94 | 42.81 | 38.02 | 1.2 | 42.81 | 0 | 607 | 424.5 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 312.1 | 0 | 305.9 | 100.28 | 15653 | 15654 | 316
03/26/22 10:54:36.186 | 555.1398 | 1367.1433 | 54.014 | 44.2962 | 9.7178 | 30.4896 | 51.0502 | 0 | 1791.3261 | 93.2077 | 84.5334 | 8.6742 | 25.6647 | 70.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0021 | 462.3401 | 459.3101 | 463.0001 | 408.8901 | 438.6301 | 416.5701 | 312.7001 | 0.56328 | -0.10594 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6688464.0727 | 7763524.0173 | 7763524.0173 | 62.4277 | 62.1425 | 1.0017 | 0.99792 | 684329.5848 | 893461.0568 | 461.5501 | 0.48532 | 0 | 0 | 30.4896 | 25.6647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.01788 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 568.7587 | 1368.2071 | 54.0745 | 44.1262 | 31.0774 | 1787.3496 | 82.8457 | 24.7004 | 461.1865 | 0.0065189 | 60.006 | 0.55306 | 0.6807 | 91.6591 | 2.2194 | 0.15589 | 0.21126 | 4.6104 | 1.2359 | 0.33266 | 0 | 100 | 576.6 | 317 | 113.93 | 107.37 | 100.28 | 305.5 | 4 | 94.9 | 42.81 | 4 | 38.02 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.28 | 0 | 38.71 | 56 | 56 | 108.55 | 92.14 | 88.29 | 0 | 100.28 | 2.38 | 94.07 | 43.49 | 113.9 | 12.48 | 107.37 | 110 | 0 | 15654 | 82.65 | 115.77 | 220.95 | 215.03 | 220.27 | 0 | 35.24 | 50.24 | 14650 | 94.89 | 42.81 | 38.02 | 1.22 | 42.81 | 0 | 607 | 428.1 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 311.4 | 0 | 305.2 | 100.28 | 15654 | 15654 | 315
03/26/22 10:54:41.186 | 554.7827 | 1366.7149 | 54.0172 | 44.299 | 9.7182 | 30.8717 | 51.0572 | 0 | 1796.0277 | 93.2172 | 84.5427 | 8.6745 | 25.1954 | 70.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0021 | 462.3401 | 459.3101 | 463.0001 | 408.8901 | 438.6301 | 416.5701 | 312.7001 | 0.56364 | -0.4115 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6684434.5645 | 7783373.6788 | 7783373.6788 | 62.4277 | 62.1424 | 1.0017 | 0.99792 | 683872.2102 | 895779.2847 | 461.5501 | 0.48532 | 0 | 0 | 30.8717 | 25.1954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017871 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 568.5651 | 1368.1854 | 54.0741 | 44.129 | 31.0773 | 1787.3882 | 82.8674 | 24.7004 | 461.19 | 0.0065265 | 60.006 | 0.55322 | 0.67636 | 91.6784 | 2.2149 | 0.15594 | 0.21019 | 4.6538 | 1.2311 | 0.33314 | 0 | 100 | 577.3 | 316 | 113.88 | 107.37 | 100.4 | 307.2 | 4 | 94.88 | 42.83 | 4 | 38.04 | 44.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.23 | 0 | 38.73 | 56 | 56 | 108.5 | 92.12 | 88.31 | 0 | 100.4 | 2.38 | 94.04 | 43.51 | 113.88 | 12.49 | 107.37 | 110 | 0 | 15654 | 82.65 | 115.79 | 220.95 | 214.92 | 220.27 | 0 | 35.27 | 50.49 | 14655 | 94.88 | 42.83 | 38.04 | 1.22 | 42.83 | 0 | 607 | 429 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 313.1 | 0 | 306.8 | 100.43 | 15654 | 15654 | 317
03/26/22 10:54:46.186 | 555.497 | 1367.6697 | 54.0231 | 44.3028 | 9.7204 | 30.4641 | 51.0463 | 0 | 1796.5077 | 93.2298 | 84.5546 | 8.6752 | 25.3663 | 70.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0131 | 462.4001 | 459.3701 | 463.1301 | 408.8901 | 439.0101 | 416.6901 | 312.8601 | 0.56321 | -0.33721 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6692738.7661 | 7786473.2023 | 7786473.2023 | 62.4277 | 62.1422 | 1.0017 | 0.99792 | 684592.6904 | 896042.3918 | 461.6334 | 0.49029 | 0 | 0 | 30.4641 | 25.3663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017864 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 568.3742 | 1368.1675 | 54.0736 | 44.1318 | 31.0821 | 1787.4011 | 82.8891 | 24.693 | 461.1935 | 0.0065341 | 60.006 | 0.55337 | 0.67385 | 91.6976 | 2.2092 | 0.15599 | 0.20912 | 4.6746 | 1.2261 | 0.33389 | 0 | 100 | 577.8 | 316 | 113.9 | 107.33 | 100.47 | 305.6 | 4 | 94.88 | 42.85 | 4 | 38.06 | 43.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.25 | 0 | 38.74 | 56 | 56 | 108.53 | 92.13 | 88.19 | 0 | 100.47 | 2.38 | 94.05 | 43.52 | 113.9 | 12.44 | 107.33 | 110 | 0 | 15654 | 82.68 | 115.84 | 220.95 | 214.92 | 220.27 | 0 | 35.34 | 50.71 | 14660 | 94.89 | 42.85 | 38.06 | 1.12 | 42.85 | 0 | 607 | 429.2 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 311.8 | 0 | 305.6 | 100.49 | 15653 | 15654 | 316
03/26/22 10:54:51.186 | 555.6842 | 1367.8503 | 54.0269 | 44.3046 | 9.7224 | 30.2976 | 51.0523 | 0 | 1795.9606 | 93.2355 | 84.5596 | 8.6759 | 25.5627 | 70.4266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0131 | 462.4001 | 459.3701 | 463.1301 | 408.8901 | 439.0101 | 416.6901 | 312.8601 | 0.56302 | -0.29065 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6694842.3499 | 7784959.0777 | 7784959.0777 | 62.4277 | 62.1422 | 1.0017 | 0.99792 | 684682.935 | 895768.799 | 461.6334 | 0.49029 | 0 | 0 | 30.2976 | 25.5627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017857 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 568.1831 | 1368.1471 | 54.0732 | 44.1345 | 31.0831 | 1787.412 | 82.9107 | 24.6895 | 461.1971 | 0.0065419 | 60.0061 | 0.55353 | 0.67149 | 91.7168 | 2.195 | 0.15601 | 0.2081 | 4.6924 | 1.2209 | 0.33512 | 0 | 100 | 576.8 | 314 | 113.8 | 107.33 | 100.37 | 305.2 | 4 | 94.84 | 42.84 | 4 | 38.05 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.23 | 0 | 38.74 | 56 | 56 | 108.55 | 92.13 | 88.23 | 0 | 100.37 | 2.38 | 94.04 | 43.52 | 113.83 | 12.48 | 107.33 | 110 | 0 | 15654 | 82.68 | 115.86 | 220.95 | 214.92 | 220.27 | 0 | 35.43 | 50.94 | 14665 | 94.85 | 42.84 | 38.05 | 1.12 | 42.84 | 0 | 607 | 428.9 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.8 | 311.9 | 0 | 305.7 | 100.31 | 15654 | 15654 | 312
03/26/22 10:54:56.186 | 556.0729 | 1368.4439 | 54.0315 | 44.3065 | 9.725 | 30.3227 | 51.0558 | 0 | 1795.9039 | 93.2413 | 84.5643 | 8.677 | 25.7421 | 70.4192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 462.4201 | 459.3801 | 463.1601 | 408.9501 | 439.1601 | 416.7301 | 312.9301 | 0.56275 | -0.24148 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6699540.3955 | 7785841.1466 | 7785841.1466 | 62.4277 | 62.1421 | 1.0017 | 0.99792 | 684979.8197 | 895739.7895 | 461.6534 | 0.49243 | 0 | 0 | 30.3227 | 25.7421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016215 | 0.017854 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 567.9988 | 1368.1425 | 54.0727 | 44.1373 | 31.0818 | 1787.4231 | 82.9324 | 24.6911 | 461.2007 | 0.0065496 | 60.0062 | 0.55368 | 0.66994 | 91.7361 | 2.1936 | 0.15601 | 0.20711 | 4.7101 | 1.2155 | 0.33655 | 0 | 100 | 576.9 | 314 | 113.83 | 107.33 | 100.33 | 304.3 | 4 | 94.85 | 42.84 | 4 | 38.05 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.2 | 0 | 38.73 | 56 | 56 | 108.48 | 92.11 | 88.19 | 0 | 100.33 | 2.38 | 94.03 | 43.51 | 113.83 | 12.49 | 107.33 | 110 | 0 | 15654 | 82.7 | 115.89 | 220.95 | 214.92 | 220.27 | 0 | 35.55 | 51.09 | 14670 | 94.84 | 42.84 | 38.05 | 1.17 | 42.84 | 0 | 607 | 428.2 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 310.4 | 0 | 304.2 | 100.4 | 15654 | 15654 | 315
03/26/22 10:55:01.186 | 555.7462 | 1366.1524 | 54.0403 | 44.3103 | 9.73 | 31.6102 | 51.0545 | 0 | 1789.9842 | 93.2502 | 84.5701 | 8.6801 | 23.6898 | 70.4444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0141 | 462.4301 | 459.3801 | 463.2001 | 408.9601 | 439.3301 | 416.6101 | 312.9401 | 0.5631 | -0.0068144 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6696639.8292 | 7764930.241 | 7764930.241 | 62.4277 | 62.142 | 1.0017 | 0.99792 | 684248.365 | 893296.11 | 461.6701 | 0.49603 | 0 | 0 | 31.6102 | 23.6898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017865 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 567.8131 | 1368.133 | 54.0723 | 44.14 | 31.0878 | 1787.411 | 82.954 | 24.6814 | 461.2043 | 0.0065573 | 60.0063 | 0.55383 | 0.66949 | 91.7553 | 2.1949 | 0.15599 | 0.20614 | 4.698 | 1.2097 | 0.33792 | 0 | 100 | 576.4 | 315 | 113.83 | 107.33 | 100.24 | 304.4 | 4 | 94.87 | 42.83 | 4 | 38.04 | 44.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.23 | 0 | 38.73 | 56 | 56 | 108.48 | 92.11 | 88.17 | 0 | 100.24 | 2.38 | 94.04 | 43.51 | 113.83 | 12.47 | 107.33 | 110 | 0 | 15654 | 82.7 | 115.91 | 220.95 | 214.92 | 220.27 | 0 | 35.61 | 51.07 | 14675 | 94.87 | 42.83 | 38.04 | 1.24 | 42.83 | 0 | 607 | 426.5 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.8 | 309 | 0 | 302.8 | 100.31 | 15654 | 15654 | 315
03/26/22 10:55:06.186 | 555.7146 | 1366.4104 | 54.0461 | 44.3129 | 9.7332 | 31.4796 | 51.0388 | 0 | 1785.9741 | 93.2546 | 84.5712 | 8.6834 | 23.6427 | 70.4386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 462.43 | 459.38 | 463.2 | 408.96 | 439.33 | 416.61 | 312.94 | 0.56313 | 0.23117 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6696216.6872 | 7746085.0515 | 7746085.0515 | 62.4277 | 62.142 | 1.0017 | 0.99792 | 683961.3259 | 890786.1251 | 461.67 | 0.49603 | 0 | 0 | 31.4796 | 23.6427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017866 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 567.6265 | 1368.119 | 54.0718 | 44.1427 | 31.0907 | 1787.3857 | 82.9757 | 24.6731 | 461.2078 | 0.0065647 | 60.0064 | 0.55398 | 0.66952 | 91.7745 | 2.1978 | 0.15593 | 0.20525 | 4.6934 | 1.2035 | 0.33948 | 0 | 100 | 576.6 | 314 | 113.95 | 107.35 | 100.28 | 305 | 4 | 94.92 | 42.84 | 4 | 38.05 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.3 | 0 | 38.74 | 56 | 56 | 108.58 | 92.16 | 88.11 | 0 | 100.28 | 2.38 | 94.08 | 43.52 | 113.93 | 12.45 | 107.35 | 110 | 0 | 15654 | 82.7 | 115.91 | 220.95 | 214.92 | 220.27 | 0 | 35.53 | 50.88 | 14680 | 94.9 | 42.84 | 38.05 | 1.33 | 42.84 | 0 | 607 | 428.1 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 311.1 | 0 | 304.8 | 100.28 | 15654 | 15654 | 314
03/26/22 10:55:11.186 | 556.5852 | 1368.2477 | 54.05 | 44.3146 | 9.7354 | 31.3481 | 51.0461 | 0 | 1782.6401 | 93.257 | 84.5712 | 8.6858 | 23.8359 | 70.4055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.011 | 462.42 | 459.36 | 463.2 | 408.96 | 439.41 | 416.53 | 312.93 | 0.56223 | 0.52091 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6706585.8536 | 7733954.9082 | 7733954.9082 | 62.4276 | 62.142 | 1.0017 | 0.99792 | 684880.8199 | 889123.2232 | 461.66 | 0.4982 | 0 | 0 | 31.3481 | 23.8359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017886 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 567.4389 | 1368.1026 | 54.0713 | 44.1453 | 31.093 | 1787.3503 | 82.9973 | 24.6669 | 461.2112 | 0.0065721 | 60.0065 | 0.55413 | 0.66991 | 91.7938 | 2.1856 | 0.15586 | 0.20436 | 4.7051 | 1.197 | 0.34093 | 0 | 100 | 576.3 | 315 | 113.95 | 107.37 | 100.23 | 303.8 | 4 | 94.92 | 42.84 | 4 | 38.05 | 44.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.33 | 0 | 38.74 | 56 | 56 | 108.6 | 92.17 | 88.09 | 0 | 100.23 | 2.38 | 94.09 | 43.52 | 113.95 | 12.47 | 107.39 | 110 | 0 | 15654 | 82.7 | 115.91 | 220.95 | 214.92 | 220.27 | 0 | 35.4 | 50.71 | 14684 | 94.92 | 42.84 | 38.05 | 1.41 | 42.84 | 0 | 607 | 426.6 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.9 | 311.9 | 0 | 305.7 | 100.16 | 15654 | 15654 | 315
03/26/22 10:55:16.185 | 556.3226 | 1367.0917 | 54.0578 | 44.3188 | 9.739 | 31.5839 | 51.0475 | 0 | 1776.3488 | 93.2601 | 84.5696 | 8.6905 | 23.5317 | 70.4002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0141 | 462.3901 | 459.3201 | 463.1801 | 408.9301 | 439.3801 | 416.3201 | 312.8401 | 0.56234 | 0.78227 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6703618.2014 | 7710518.5451 | 7710518.5451 | 62.4276 | 62.142 | 1.0017 | 0.99792 | 684301.8008 | 885985.5846 | 461.6301 | 0.5004 | 0 | 0 | 31.5839 | 23.5317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.01789 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 567.2553 | 1368.0936 | 54.0708 | 44.148 | 31.0979 | 1787.291 | 83.0189 | 24.6564 | 461.2145 | 0.0065792 | 60.0066 | 0.55428 | 0.67217 | 91.813 | 2.1853 | 0.15575 | 0.2035 | 4.7793 | 1.19 | 0.34229 | 0 | 100 | 576.1 | 315 | 114.08 | 107.41 | 100.19 | 302.6 | 4 | 94.98 | 42.83 | 4 | 38.04 | 44.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.45 | 0 | 38.73 | 56 | 56 | 108.73 | 92.24 | 88.13 | 0 | 100.19 | 2.38 | 94.16 | 43.51 | 114.1 | 12.43 | 107.41 | 110 | 0 | 15654 | 82.7 | 115.91 | 220.95 | 214.92 | 220.27 | 0 | 35.31 | 50.6 | 14689 | 94.98 | 42.83 | 38.04 | 1.44 | 42.83 | 0 | 607 | 426.4 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 309.5 | 0 | 303.3 | 100.19 | 15656 | 15654 | 315
03/26/22 10:55:21.185 | 555.8849 | 1365.9253 | 54.0605 | 44.3209 | 9.7397 | 30.8383 | 51.0452 | 0 | 1777.9591 | 93.2609 | 84.5696 | 8.6914 | 24.5473 | 70.4171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 462.39 | 459.32 | 463.18 | 408.93 | 439.38 | 416.32 | 312.84 | 0.56278 | 0.59053 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6697687.153 | 7719421.0691 | 7719421.0691 | 62.4276 | 62.142 | 1.0017 | 0.99792 | 683717.8486 | 886788.7302 | 461.63 | 0.5004 | 0 | 0 | 30.8383 | 24.5473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017883 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 567.0786 | 1368.0995 | 54.0703 | 44.1506 | 31.0937 | 1787.2173 | 83.0405 | 24.6578 | 461.2178 | 0.0065863 | 60.0067 | 0.55442 | 0.67608 | 91.8322 | 2.1779 | 0.15562 | 0.20269 | 4.8204 | 1.1826 | 0.34343 | 0 | 100 | 576.3 | 316 | 114.15 | 107.43 | 100.23 | 303.6 | 4 | 95.02 | 42.84 | 4 | 38.05 | 44.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.48 | 0 | 38.74 | 56 | 56 | 108.8 | 92.28 | 88.07 | 0 | 100.23 | 2.38 | 94.17 | 43.52 | 114.13 | 12.43 | 107.43 | 110 | 0 | 15654 | 82.7 | 115.91 | 220.95 | 214.92 | 220.27 | 0 | 35.2 | 50.5 | 14694 | 95 | 42.84 | 38.05 | 1.39 | 42.84 | 0 | 607 | 429.8 | 459.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 313.3 | 0 | 307 | 100.37 | 15653 | 15654 | 315
03/26/22 10:55:26.186 | 555.2847 | 1364.4492 | 54.0661 | 44.3264 | 9.7397 | 29.99 | 51.0644 | 0 | 1788.7352 | 93.2633 | 84.5721 | 8.6912 | 26.2274 | 70.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.017 | 462.37 | 459.29 | 463.16 | 408.88 | 439.34 | 416.21 | 312.78 | 0.56328 | -0.14254 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6689712.3566 | 7768026.5374 | 7768026.5374 | 62.4276 | 62.142 | 1.0017 | 0.99792 | 682978.749 | 892163.1584 | 461.6067 | 0.50187 | 0 | 0 | 29.99 | 26.2274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017876 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 566.8907 | 1368.0786 | 54.0697 | 44.1532 | 31.0893 | 1787.2495 | 83.0621 | 24.6632 | 461.2209 | 0.0065931 | 60.0068 | 0.55458 | 0.67245 | 91.8514 | 2.1987 | 0.15547 | 0.20192 | 4.8084 | 1.1748 | 0.34438 | 0 | 100 | 576.5 | 316 | 114.05 | 107.45 | 100.28 | 304.3 | 4 | 94.95 | 42.84 | 4 | 38.05 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.38 | 0 | 38.74 | 56 | 56 | 108.7 | 92.22 | 88.17 | 0 | 100.28 | 2.38 | 94.12 | 43.52 | 114.03 | 12.49 | 107.45 | 110 | 0 | 15654 | 82.7 | 115.91 | 220.95 | 214.92 | 220.27 | 0 | 35.08 | 50.44 | 14699 | 94.95 | 42.84 | 38.05 | 1.31 | 42.84 | 0 | 607 | 425 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 310.5 | 0 | 304.3 | 100.24 | 15653 | 15654 | 315
03/26/22 10:55:31.186 | 556.35 | 1367.1123 | 54.068 | 44.3286 | 9.7394 | 30.3534 | 51.0653 | 0 | 1793.055 | 93.2655 | 84.5745 | 8.691 | 25.5488 | 70.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0191 | 462.3201 | 459.2201 | 463.1401 | 408.8001 | 439.4601 | 416.1501 | 312.7501 | 0.56215 | -0.20188 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6702866.3083 | 7785818.1912 | 7785818.1912 | 62.4276 | 62.1419 | 1.0017 | 0.99792 | 684311.6702 | 894317.3527 | 461.5601 | 0.50698 | 0 | 0 | 30.3534 | 25.5488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017866 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 566.7072 | 1368.0693 | 54.0692 | 44.1557 | 31.0859 | 1787.3117 | 83.0838 | 24.6683 | 461.2241 | 0.0065999 | 60.0069 | 0.55472 | 0.66798 | 91.8706 | 2.2014 | 0.15529 | 0.20116 | 4.8015 | 1.1665 | 0.34529 | 0 | 100 | 576.5 | 314 | 113.9 | 107.45 | 100.3 | 304.8 | 4 | 94.89 | 42.85 | 4 | 38.06 | 44.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.3 | 0 | 38.76 | 56 | 56 | 108.6 | 92.17 | 88.17 | 0 | 100.3 | 2.38 | 94.08 | 43.54 | 113.88 | 12.57 | 107.45 | 110 | 0 | 15654 | 82.72 | 115.91 | 220.95 | 214.92 | 220.27 | 0 | 35 | 50.46 | 14704 | 94.88 | 42.85 | 38.06 | 1.26 | 42.85 | 0 | 607 | 428 | 459.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 311.7 | 0 | 305.5 | 100.24 | 15650 | 15654 | 312
03/26/22 10:55:36.185 | 556.8285 | 1368.0981 | 54.0701 | 44.3309 | 9.7391 | 30.5149 | 51.0638 | 0 | 1795.7439 | 93.2685 | 84.5775 | 8.691 | 25.1207 | 70.4113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0191 | 462.3201 | 459.2201 | 463.1401 | 408.8001 | 439.4601 | 416.1501 | 312.7501 | 0.56166 | -0.24389 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6708668.3626 | 7794802.7425 | 7794802.7425 | 62.4276 | 62.1419 | 1.0017 | 0.99792 | 684916.1025 | 895387.8458 | 461.5601 | 0.50698 | 0 | 0 | 30.5149 | 25.1207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017858 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 566.5212 | 1368.0541 | 54.0686 | 44.1583 | 31.0794 | 1787.3856 | 83.1054 | 24.6759 | 461.2272 | 0.0066066 | 60.007 | 0.55487 | 0.66271 | 91.8899 | 2.1916 | 0.1551 | 0.20042 | 4.8284 | 1.1577 | 0.34581 | 0 | 100 | 577.1 | 316 | 113.88 | 107.43 | 100.37 | 306.5 | 4 | 94.88 | 42.88 | 4 | 38.09 | 44.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.28 | 0 | 38.78 | 56 | 56 | 108.58 | 92.14 | 88.19 | 0 | 100.37 | 2.37 | 94.07 | 43.55 | 113.9 | 12.54 | 107.43 | 110 | 0 | 15654 | 82.72 | 115.94 | 220.95 | 214.92 | 220.27 | 0 | 35.07 | 50.84 | 14709 | 94.89 | 42.88 | 38.09 | 1.26 | 42.88 | 0 | 607 | 428.9 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 310.9 | 0 | 304.6 | 100.37 | 15654 | 15654 | 313
03/26/22 10:55:41.185 | 555.9988 | 1366.3124 | 54.0732 | 44.3343 | 9.7389 | 30.3961 | 51.051 | 0 | 1799.4908 | 93.2735 | 84.582 | 8.6915 | 25.2506 | 70.4093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 462.3301 | 459.2001 | 463.1301 | 408.9401 | 439.4901 | 416.2201 | 312.8201 | 0.56263 | -0.61532 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6698674.1547 | 7813856.32 | 7813856.32 | 62.4276 | 62.1418 | 1.0017 | 0.99792 | 683911.0321 | 897526.2026 | 461.5534 | 0.50987 | 0 | 0 | 30.3961 | 25.2506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017848 | 0.010952 | 0.004474 | 0.011584 | 0.0119 | 566.338 | 1368.0454 | 54.068 | 44.1609 | 31.0735 | 1787.4747 | 83.1271 | 24.6835 | 461.2303 | 0.0066132 | 60.0071 | 0.55502 | 0.65682 | 91.9091 | 2.1954 | 0.15489 | 0.1997 | 4.9028 | 1.1486 | 0.34625 | 0 | 100 | 577.3 | 315 | 113.85 | 107.41 | 100.37 | 304.9 | 4 | 94.87 | 42.88 | 4 | 38.09 | 44.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.25 | 0 | 38.78 | 56 | 56 | 108.53 | 92.13 | 88.23 | 0 | 100.37 | 2.37 | 94.05 | 43.55 | 113.85 | 12.54 | 107.41 | 110 | 0 | 15654 | 82.72 | 115.96 | 220.95 | 214.92 | 220.27 | 0 | 35.27 | 51.13 | 14714 | 94.87 | 42.88 | 38.09 | 1.35 | 42.88 | 0 | 607 | 426.1 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 311.1 | 0 | 304.9 | 100.4 | 15653 | 15654 | 315
03/26/22 10:55:46.185 | 555.8048 | 1365.8169 | 54.0758 | 44.3366 | 9.7392 | 30.2174 | 51.0452 | 0 | 1797.0961 | 93.2768 | 84.5846 | 8.6922 | 25.4461 | 70.3866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.02 | 462.33 | 459.2 | 463.13 | 408.94 | 439.49 | 416.22 | 312.82 | 0.56282 | -0.56791 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6696190.976 | 7807792.4586 | 7807792.4586 | 62.4276 | 62.1418 | 1.0017 | 0.99792 | 683657.7676 | 896756.2179 | 461.5534 | 0.50987 | 0 | 0 | 30.2174 | 25.4461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017845 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 566.1679 | 1368.0596 | 54.0675 | 44.1634 | 31.0708 | 1787.5277 | 83.1487 | 24.6832 | 461.2333 | 0.0066198 | 60.0073 | 0.55516 | 0.65423 | 91.9283 | 2.1722 | 0.15468 | 0.199 | 4.955 | 1.1391 | 0.34666 | 0 | 100 | 576.6 | 314 | 113.83 | 107.39 | 100.4 | 304.8 | 4 | 94.85 | 42.88 | 4 | 38.09 | 44.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.23 | 0 | 38.78 | 56 | 56 | 108.53 | 92.13 | 88.17 | 0 | 100.4 | 2.37 | 94.04 | 43.55 | 113.85 | 12.53 | 107.39 | 110 | 0 | 15654 | 82.74 | 116.01 | 220.95 | 214.92 | 220.27 | 0 | 35.33 | 51.09 | 14719 | 94.87 | 42.88 | 38.09 | 1.33 | 42.88 | 0 | 607 | 427.7 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.7 | 310.5 | 0 | 304.3 | 100.3 | 15653 | 15654 | 314
03/26/22 10:55:51.186 | 556.2718 | 1366.8026 | 54.0798 | 44.3398 | 9.74 | 31.3022 | 51.043 | 0 | 1794.1027 | 93.2806 | 84.5875 | 8.6931 | 24.1709 | 70.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.017 | 462.35 | 459.22 | 463.12 | 409.05 | 439.48 | 416.35 | 312.9 | 0.56249 | -0.28576 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6702672.1503 | 7792567.079 | 7792567.079 | 62.4276 | 62.1418 | 1.0017 | 0.99792 | 684182.0134 | 895061.9946 | 461.5634 | 0.50769 | 0 | 0 | 31.3022 | 24.1709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017845 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 565.9932 | 1368.0545 | 54.067 | 44.166 | 31.0739 | 1787.5543 | 83.1702 | 24.6755 | 461.2364 | 0.0066264 | 60.0074 | 0.5553 | 0.65197 | 91.9476 | 2.1741 | 0.15451 | 0.1983 | 4.9774 | 1.1294 | 0.34713 | 0 | 100 | 577 | 315 | 113.9 | 107.39 | 100.4 | 304.8 | 4 | 94.89 | 42.88 | 4 | 38.09 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.23 | 0 | 38.78 | 56 | 56 | 108.5 | 92.12 | 88.19 | 0 | 100.4 | 2.37 | 94.04 | 43.55 | 113.9 | 12.5 | 107.39 | 110 | 0 | 15654 | 82.76 | 116.03 | 220.95 | 214.92 | 220.27 | 0 | 35.29 | 51.02 | 14724 | 94.89 | 42.88 | 38.09 | 1.3 | 42.88 | 0 | 607 | 427.2 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 311.9 | 0 | 305.7 | 100.35 | 15656 | 15654 | 315
03/26/22 10:55:56.186 | 556.2276 | 1366.622 | 54.0846 | 44.3439 | 9.7408 | 31.521 | 51.0452 | 0 | 1789.499 | 93.2844 | 84.5899 | 8.6945 | 23.886 | 70.3737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.018 | 462.37 | 459.26 | 463.13 | 409.1 | 439.42 | 416.46 | 312.94 | 0.56261 | -0.017002 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6702413.3245 | 7771529.8514 | 7771529.8514 | 62.4276 | 62.1417 | 1.0017 | 0.99792 | 684065.5217 | 892541.506 | 461.5867 | 0.50406 | 0 | 0 | 31.521 | 23.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.01785 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 565.8133 | 1368.0262 | 54.0666 | 44.1685 | 31.0782 | 1787.5487 | 83.1917 | 24.6679 | 461.2396 | 0.0066333 | 60.0075 | 0.55545 | 0.65026 | 91.9668 | 2.1594 | 0.15438 | 0.19761 | 4.9746 | 1.1194 | 0.34769 | 0 | 100 | 576.4 | 316 | 113.83 | 107.39 | 100.24 | 307.2 | 4 | 94.85 | 42.86 | 4 | 38.07 | 44.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.28 | 0 | 38.76 | 55 | 55 | 108.58 | 92.14 | 88.09 | 0 | 100.24 | 2.38 | 94.07 | 43.54 | 113.83 | 12.54 | 107.39 | 110 | 0 | 15654 | 82.76 | 116.03 | 220.95 | 214.92 | 220.27 | 0 | 35.29 | 51.04 | 14730 | 94.85 | 42.86 | 38.07 | 1.29 | 42.86 | 0 | 607 | 427.8 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 313.4 | 0 | 307.2 | 100.24 | 15653 | 15654 | 316
03/26/22 10:56:01.185 | 556.9994 | 1369.8115 | 54.0872 | 44.3482 | 9.739 | 30.6928 | 51.0438 | 0 | 1788.1624 | 93.2875 | 84.5933 | 8.6943 | 24.3904 | 70.4084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0181 | 462.3701 | 459.2601 | 463.1301 | 409.1001 | 439.4201 | 416.4601 | 312.9401 | 0.56183 | 0.24782 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6711127.8914 | 7759669.4336 | 7759669.4336 | 62.4275 | 62.1417 | 1.0017 | 0.99792 | 685057.4306 | 891055.962 | 461.5867 | 0.50406 | 0 | 0 | 30.6928 | 24.3904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017843 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 565.6416 | 1368.0195 | 54.0663 | 44.1711 | 31.0764 | 1787.5298 | 83.213 | 24.6651 | 461.2428 | 0.0066402 | 60.0076 | 0.55559 | 0.64996 | 91.9859 | 2.1518 | 0.15428 | 0.19689 | 4.9658 | 1.1092 | 0.34822 | 0 | 100 | 574.2 | 316 | 114.1 | 107.39 | 99.86 | 304.9 | 4 | 94.99 | 42.83 | 4 | 38.04 | 44.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.48 | 0 | 38.73 | 55 | 55 | 108.83 | 92.29 | 88.13 | 0 | 99.86 | 2.38 | 94.17 | 43.51 | 114.15 | 12.37 | 107.39 | 110 | 0 | 15654 | 82.78 | 116.03 | 220.95 | 214.92 | 220.27 | 0 | 35.29 | 50.93 | 14735 | 95.02 | 42.81 | 38.02 | 1.34 | 42.81 | 0 | 607 | 424.6 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 311.8 | 0 | 305.6 | 99.83 | 15655 | 15654 | 315
03/26/22 10:56:06.185 | 557.6128 | 1370.7302 | 54.0856 | 44.3498 | 9.7358 | 30.7982 | 51.0517 | 0 | 1786.1186 | 93.2883 | 84.5965 | 8.6918 | 24.4806 | 70.3796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0171 | 462.3901 | 459.2701 | 463.1001 | 408.9601 | 439.0601 | 416.2001 | 312.7401 | 0.56086 | 0.40041 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6718482.5209 | 7755163.0418 | 7755163.0418 | 62.4275 | 62.1417 | 1.0017 | 0.99792 | 686121.8353 | 890854.5007 | 461.5867 | 0.50189 | 0 | 0 | 30.7982 | 24.4806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017851 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 565.501 | 1368.0585 | 54.0662 | 44.1737 | 31.0774 | 1787.496 | 83.234 | 24.6615 | 461.246 | 0.0066471 | 60.0077 | 0.55571 | 0.65249 | 92.005 | 2.1368 | 0.15425 | 0.19612 | 4.9544 | 1.0994 | 0.34872 | 0 | 100 | 573.9 | 315 | 114.33 | 107.47 | 99.81 | 304.4 | 4 | 95.09 | 42.73 | 4 | 37.94 | 44.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.63 | 0 | 38.61 | 55 | 55 | 108.95 | 92.35 | 88.15 | 0 | 99.81 | 2.39 | 94.24 | 43.41 | 114.33 | 12.36 | 107.47 | 110 | 0 | 15664 | 82.78 | 116.03 | 220.95 | 214.92 | 220.27 | 0 | 35.22 | 50.66 | 14740 | 95.11 | 42.71 | 37.93 | 1.48 | 42.71 | 0 | 607 | 426.2 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 310.5 | 0 | 304.3 | 99.83 | 15665 | 15664 | 316
03/26/22 10:56:11.185 | 555.1608 | 1367.52 | 54.071 | 44.3553 | 9.7157 | 30.9704 | 51.03 | 0 | 1787.9921 | 93.2912 | 84.6135 | 8.6778 | 24.5953 | 70.3201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0131 | 462.3901 | 459.2601 | 463.0501 | 408.7701 | 438.5801 | 415.8901 | 312.4801 | 0.56286 | 0.063421 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6689145.688 | 7750863.5113 | 7750863.5113 | 62.4276 | 62.1416 | 1.0017 | 0.99792 | 684515.627 | 891786.4182 | 461.5668 | 0.49975 | 0 | 0 | 30.9704 | 24.5953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017854 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 565.3553 | 1368.0792 | 54.0661 | 44.1764 | 31.0769 | 1787.4745 | 83.2547 | 24.6611 | 461.2491 | 0.0066538 | 60.0078 | 0.55583 | 0.65255 | 92.0239 | 2.1378 | 0.15424 | 0.19528 | 4.9518 | 1.0897 | 0.34902 | 0 | 100 | 574 | 317 | 114.35 | 107.53 | 99.83 | 304.1 | 4 | 95.12 | 42.65 | 4 | 37.86 | 44.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.75 | 0 | 38.54 | 55 | 55 | 109.08 | 92.42 | 88.11 | 0 | 99.83 | 2.39 | 94.31 | 43.32 | 114.4 | 12.38 | 107.53 | 110 | 0 | 15674 | 82.8 | 116.03 | 220.95 | 214.92 | 220.27 | 0 | 35.08 | 50.36 | 14745 | 95.14 | 42.64 | 37.85 | 1.63 | 42.64 | 0 | 607 | 428 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574.2 | 310.8 | 0 | 304.6 | 99.86 | 15671 | 15674 | 315
03/26/22 10:56:16.185 | 554.3523 | 1367.0401 | 54.0598 | 44.3567 | 9.7031 | 31.2449 | 51.0397 | 0 | 1785.8606 | 93.2933 | 84.6243 | 8.669 | 23.8002 | 70.3259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0131 | 462.3901 | 459.2601 | 463.0501 | 408.7701 | 438.5801 | 415.8901 | 312.4801 | 0.56368 | 0.1589 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6679582.4018 | 7733509.828 | 7733509.828 | 62.4276 | 62.1415 | 1.0017 | 0.99792 | 684260.3035 | 890621.5893 | 461.5668 | 0.49975 | 0 | 0 | 31.2449 | 23.8002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017855 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 565.2007 | 1368.0725 | 54.0662 | 44.1791 | 31.0808 | 1787.4703 | 83.2751 | 24.6539 | 461.2522 | 0.0066604 | 60.0079 | 0.55596 | 0.64895 | 92.0425 | 2.1392 | 0.15424 | 0.1943 | 4.9529 | 1.0807 | 0.34938 | 0 | 100 | 575.2 | 313 | 114.5 | 107.61 | 99.97 | 305.2 | 4 | 95.19 | 42.61 | 4 | 37.82 | 44.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.9 | 0 | 38.5 | 55 | 55 | 109.25 | 92.51 | 88.13 | 0 | 99.97 | 2.4 | 94.38 | 43.28 | 114.5 | 12.4 | 107.61 | 110 | 0 | 15683 | 82.8 | 116.03 | 220.95 | 214.92 | 220.27 | 0 | 34.91 | 50.23 | 14749 | 95.21 | 42.61 | 37.81 | 1.62 | 42.61 | 0 | 607 | 429.8 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.2 | 311.4 | 0 | 305.2 | 100.03 | 15680 | 15683 | 313
03/26/22 10:56:21.185 | 553.2988 | 1369.538 | 54.024 | 44.3552 | 9.6688 | 31.4027 | 51.049 | 0 | 1776.7204 | 93.3012 | 84.6579 | 8.6433 | 23.9498 | 70.3164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0181 | 462.3901 | 459.3301 | 463.0501 | 408.5201 | 438.3201 | 415.8701 | 312.3501 | 0.56452 | 0.80987 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6667222.6137 | 7670731.5622 | 7670731.5622 | 62.4276 | 62.1413 | 1.0017 | 0.99792 | 685527.8299 | 886158.056 | 461.5901 | 0.48961 | 0 | 0 | 31.4027 | 23.9498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017875 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 565.0463 | 1368.0738 | 54.0663 | 44.1819 | 31.0854 | 1787.4129 | 83.2953 | 24.6444 | 461.2552 | 0.0066669 | 60.008 | 0.55609 | 0.64807 | 92.0611 | 2.1398 | 0.1542 | 0.19316 | 5.0098 | 1.0722 | 0.34981 | 0 | 100 | 574.2 | 315 | 114.63 | 107.68 | 99.86 | 304.6 | 4 | 95.26 | 42.56 | 4 | 37.78 | 44.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.08 | 0 | 38.45 | 55 | 55 | 109.43 | 92.6 | 88.25 | 0 | 99.86 | 2.4 | 94.47 | 43.23 | 114.65 | 12.42 | 107.68 | 110 | 0 | 15687 | 82.8 | 116.03 | 220.95 | 214.92 | 220.27 | 0 | 34.85 | 50.23 | 14754 | 95.27 | 42.55 | 37.76 | 1.66 | 42.55 | 0 | 607 | 429 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574.5 | 312.9 | 0 | 306.7 | 99.91 | 15684 | 15687 | 318
03/26/22 10:56:26.185 | 552.3652 | 1370.5495 | 53.9955 | 44.3502 | 9.6453 | 30.5988 | 51.0407 | 0 | 1777.7629 | 93.3102 | 84.6855 | 8.6247 | 25.1647 | 70.2999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0181 | 462.3901 | 459.3301 | 463.0501 | 408.5201 | 438.3201 | 415.8701 | 312.3501 | 0.56548 | 0.79283 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6655332.4787 | 7660141.005 | 7660141.005 | 62.4277 | 62.1411 | 1.0017 | 0.99792 | 686035.432 | 886673.987 | 461.5901 | 0.48961 | 0 | 0 | 30.5988 | 25.1647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017873 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 564.8991 | 1368.0891 | 54.0665 | 44.1848 | 31.0802 | 1787.3692 | 83.3152 | 24.6503 | 461.2584 | 0.0066738 | 60.0081 | 0.55622 | 0.64625 | 92.0793 | 2.15 | 0.15409 | 0.19177 | 5.0648 | 1.0644 | 0.35024 | 0 | 100 | 575.6 | 316 | 114.85 | 107.74 | 100.1 | 307.9 | 4 | 95.37 | 42.53 | 4 | 37.74 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.2 | 0 | 38.43 | 55 | 55 | 109.53 | 92.65 | 88.33 | 0 | 100.1 | 2.41 | 94.54 | 43.21 | 114.83 | 12.41 | 107.76 | 110 | 0 | 15694 | 82.8 | 116.03 | 220.95 | 214.92 | 220.27 | 0 | 34.82 | 50.21 | 14759 | 95.36 | 42.53 | 37.74 | 1.64 | 42.53 | 0 | 607 | 427.1 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7 | 310.7 | 0 | 304.5 | 100.12 | 15693 | 15694 | 316
03/26/22 10:56:31.184 | 549.7944 | 1366.6272 | 53.9588 | 44.3411 | 9.6177 | 30.7409 | 51.0481 | 0 | 1784.08 | 93.3252 | 84.7228 | 8.6025 | 25.4967 | 70.3296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0221 | 462.4001 | 459.3601 | 463.0901 | 408.3501 | 438.3301 | 415.8601 | 312.3201 | 0.56807 | 0.30074 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6624437.7748 | 7667126.6112 | 7667126.6112 | 62.4277 | 62.1408 | 1.0017 | 0.99792 | 684481.6003 | 889341.3733 | 461.6168 | 0.48886 | 0 | 0 | 30.7409 | 25.4967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017867 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 564.7444 | 1368.0942 | 54.0667 | 44.1877 | 31.0784 | 1787.3534 | 83.335 | 24.6554 | 461.2615 | 0.0066806 | 60.0082 | 0.55636 | 0.64181 | 92.0975 | 2.1474 | 0.15395 | 0.19015 | 5.0737 | 1.0572 | 0.35065 | 0 | 100 | 575.6 | 314 | 114.78 | 107.82 | 100.1 | 305.4 | 4 | 95.33 | 42.5 | 4 | 37.71 | 44.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.18 | 0 | 38.39 | 55 | 55 | 109.5 | 92.65 | 88.35 | 0 | 100.1 | 2.41 | 94.52 | 43.17 | 114.75 | 12.5 | 107.82 | 110 | 0 | 15694 | 82.8 | 116.03 | 220.95 | 214.92 | 220.15 | 0 | 34.74 | 50.19 | 14764 | 95.32 | 42.5 | 37.71 | 1.57 | 42.5 | 0 | 608 | 427.8 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.4 | 312.2 | 0 | 306 | 100.07 | 15695 | 15694 | 316
03/26/22 10:56:36.185 | 546.7555 | 1364.8724 | 53.9127 | 44.3258 | 9.5869 | 31.3757 | 51.0589 | 0 | 1787.672 | 93.3497 | 84.7723 | 8.5774 | 24.2229 | 70.2817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.022 | 462.4 | 459.36 | 463.09 | 408.35 | 438.33 | 415.86 | 312.32 | 0.57122 | -0.069154 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6588585.0146 | 7659559.6621 | 7659559.6621 | 62.4278 | 62.1404 | 1.0017 | 0.99791 | 683197.3909 | 891603.4806 | 461.6167 | 0.48886 | 0 | 0 | 31.3757 | 24.2229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017867 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 564.5742 | 1368.0797 | 54.0667 | 44.1906 | 31.0836 | 1787.3587 | 83.3547 | 24.649 | 461.2649 | 0.0066878 | 60.0084 | 0.55651 | 0.63489 | 92.1155 | 2.1603 | 0.15394 | 0.18825 | 5.0735 | 1.0506 | 0.35114 | 0 | 100 | 575.1 | 314 | 114.8 | 107.86 | 100.02 | 304.3 | 4 | 95.33 | 42.49 | 4 | 37.7 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.2 | 0 | 38.38 | 55 | 55 | 109.55 | 92.66 | 88.51 | 0 | 100.07 | 2.41 | 94.54 | 43.16 | 114.8 | 12.52 | 107.86 | 110 | 0 | 15694 | 82.8 | 116.05 | 220.95 | 214.92 | 220.15 | 0 | 34.69 | 50.21 | 14769 | 95.34 | 42.49 | 37.69 | 1.5 | 42.49 | 0 | 607 | 425.4 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574.9 | 313.4 | 0 | 307.1 | 99.98 | 15693 | 15694 | 317
03/26/22 10:56:41.185 | 545.15 | 1365.7446 | 53.8549 | 44.3024 | 9.5525 | 30.6822 | 51.057 | 0 | 1783.9355 | 93.3852 | 84.8363 | 8.5489 | 25.0022 | 70.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.021 | 462.42 | 459.42 | 463.17 | 408.41 | 438.71 | 416.27 | 312.57 | 0.57337 | 0.21286 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6568728.3418 | 7619025.8363 | 7619025.8363 | 62.4279 | 62.1398 | 1.0017 | 0.99791 | 683636.5155 | 889730.4685 | 461.67 | 0.48736 | 0 | 0 | 30.6822 | 25.0022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.01787 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 564.4008 | 1368.0725 | 54.0667 | 44.1936 | 31.0794 | 1787.3435 | 83.3743 | 24.6558 | 461.2684 | 0.0066953 | 60.0085 | 0.55667 | 0.62884 | 92.1334 | 2.1665 | 0.15401 | 0.18588 | 5.079 | 1.045 | 0.35172 | 0 | 100 | 575.1 | 316 | 114.9 | 107.88 | 100.02 | 305.9 | 4 | 95.41 | 42.49 | 4 | 37.7 | 43.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.3 | 0 | 38.38 | 55 | 55 | 109.6 | 92.69 | 88.55 | 0 | 100.02 | 2.41 | 94.59 | 43.16 | 114.9 | 12.51 | 107.9 | 110 | 0 | 15696 | 82.8 | 116.1 | 220.95 | 214.92 | 220.15 | 0 | 34.8 | 50.56 | 14774 | 95.4 | 42.49 | 37.69 | 1.4 | 42.49 | 0 | 607 | 426.5 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575 | 313.7 | 0 | 307.4 | 100 | 15696 | 15696 | 317
03/26/22 10:56:46.185 | 544.5944 | 1367.8709 | 53.8085 | 44.2807 | 9.5278 | 30.3863 | 51.0653 | 0 | 1791.3054 | 93.4168 | 84.889 | 8.5278 | 25.5651 | 70.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0241 | 462.4701 | 459.4801 | 463.2201 | 408.5201 | 438.8701 | 416.4801 | 312.7301 | 0.57424 | -0.051009 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6561842.407 | 7632267.2318 | 7632267.2318 | 62.428 | 62.1394 | 1.0017 | 0.99791 | 684702.9219 | 893398.3997 | 461.7234 | 0.48586 | 0 | 0 | 30.3863 | 25.5651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017859 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 564.2208 | 1368.0692 | 54.0664 | 44.1964 | 31.0726 | 1787.3847 | 83.3939 | 24.665 | 461.2721 | 0.0067032 | 60.0087 | 0.55683 | 0.61984 | 92.1511 | 2.1664 | 0.1544 | 0.18318 | 5.081 | 1.0401 | 0.35243 | 0 | 100 | 575.4 | 317 | 114.85 | 107.92 | 100.07 | 306 | 4 | 95.37 | 42.46 | 4 | 37.68 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.28 | 0 | 38.35 | 55 | 55 | 109.58 | 92.68 | 88.67 | 0 | 100.07 | 2.41 | 94.57 | 43.14 | 114.85 | 12.55 | 107.92 | 110 | 0 | 15696 | 82.8 | 116.15 | 220.95 | 214.92 | 220.15 | 0 | 35.01 | 50.84 | 14779 | 95.37 | 42.46 | 37.68 | 1.43 | 42.46 | 0 | 607 | 427.3 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.2 | 312.3 | 0 | 306 | 100.03 | 15695 | 15696 | 317
03/26/22 10:56:51.185 | 544.4304 | 1369.3625 | 53.7723 | 44.2616 | 9.5107 | 30.692 | 51.0405 | 0 | 1795.5735 | 93.444 | 84.9306 | 8.5135 | 24.9326 | 70.2697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.024 | 462.47 | 459.48 | 463.22 | 408.52 | 438.87 | 416.48 | 312.73 | 0.57442 | -0.069815 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6560078.4534 | 7632483.7668 | 7632483.7668 | 62.4281 | 62.1391 | 1.0018 | 0.99791 | 685492.1188 | 894706.2867 | 461.7234 | 0.48586 | 0 | 0 | 30.692 | 24.9326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017841 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 564.0447 | 1368.0871 | 54.066 | 44.1993 | 31.0709 | 1787.4599 | 83.4136 | 24.6658 | 461.2761 | 0.006712 | 60.0089 | 0.55699 | 0.611 | 92.1689 | 2.1636 | 0.15505 | 0.18018 | 5.1015 | 1.0355 | 0.35339 | 0 | 100 | 575 | 316 | 114.8 | 107.94 | 100 | 306.1 | 4 | 95.34 | 42.44 | 4 | 37.65 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.25 | 0 | 38.34 | 55 | 55 | 109.55 | 92.66 | 88.69 | 0 | 100 | 2.41 | 94.56 | 43.12 | 114.8 | 12.6 | 107.94 | 110 | 0 | 15696 | 82.85 | 116.2 | 220.95 | 214.92 | 220.15 | 0 | 35.16 | 50.98 | 14784 | 95.34 | 42.44 | 37.65 | 1.45 | 42.44 | 0 | 607 | 430.7 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575 | 312.3 | 0 | 306.1 | 100 | 15697 | 15696 | 316
03/26/22 10:56:56.185 | 543.0386 | 1369.4038 | 53.7154 | 44.2256 | 9.4898 | 30.8483 | 51.0223 | 0 | 1793.1685 | 93.4949 | 84.9979 | 8.497 | 25.1205 | 70.2656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.027 | 462.48 | 459.5 | 463.24 | 408.59 | 439.05 | 416.64 | 312.84 | 0.57609 | -0.012991 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6543610.3879 | 7612053.3048 | 7612053.3048 | 62.4283 | 62.1383 | 1.0018 | 0.99791 | 685474.2829 | 894311.4985 | 461.74 | 0.48512 | 0 | 0 | 30.8483 | 25.1205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017852 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 563.8576 | 1368.0971 | 54.0654 | 44.202 | 31.0734 | 1787.4896 | 83.4332 | 24.6627 | 461.2809 | 0.0067223 | 60.0091 | 0.55716 | 0.60386 | 92.1864 | 2.1655 | 0.15622 | 0.17679 | 5.1192 | 1.0319 | 0.35382 | 0 | 100 | 575.7 | 315 | 114.88 | 107.94 | 100.12 | 306.2 | 4 | 95.4 | 42.45 | 4 | 37.66 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.28 | 0 | 38.34 | 55 | 55 | 109.6 | 92.69 | 88.79 | 0 | 100.12 | 2.41 | 94.57 | 43.12 | 114.9 | 12.56 | 107.96 | 110 | 0 | 15696 | 82.87 | 116.25 | 220.95 | 214.92 | 220.15 | 0 | 35.26 | 51.03 | 14789 | 95.38 | 42.45 | 37.66 | 1.44 | 42.45 | 0 | 608 | 427.9 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.6 | 311.3 | 0 | 305.1 | 100.1 | 15698 | 15696 | 315
03/26/22 10:57:01.185 | 542.4432 | 1369.0993 | 53.6814 | 44.2 | 9.4815 | 30.6391 | 51.0182 | 0 | 1788.8797 | 93.5296 | 85.0394 | 8.4902 | 25.5011 | 70.3106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.027 | 462.48 | 459.5 | 463.24 | 408.59 | 439.05 | 416.64 | 312.84 | 0.57672 | 0.1993 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6536215.9164 | 7588530.9587 | 7588530.9587 | 62.4283 | 62.138 | 1.0018 | 0.99791 | 685248.1842 | 892092.848 | 461.74 | 0.48512 | 0 | 0 | 30.6391 | 25.5011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017851 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 563.6643 | 1368.099 | 54.0646 | 44.2046 | 31.0716 | 1787.4842 | 83.4529 | 24.6642 | 461.2857 | 0.0067326 | 60.0094 | 0.55734 | 0.59811 | 92.2041 | 2.1663 | 0.15778 | 0.17322 | 5.1172 | 1.0285 | 0.35418 | 0 | 100 | 575.1 | 315 | 114.85 | 107.96 | 100.07 | 306.4 | 4 | 95.38 | 42.44 | 4 | 37.65 | 43.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.25 | 0 | 38.34 | 55 | 55 | 109.58 | 92.68 | 88.81 | 0 | 100.07 | 2.41 | 94.56 | 43.12 | 114.85 | 12.58 | 107.96 | 110 | 0 | 15697 | 82.87 | 116.29 | 220.83 | 214.92 | 220.15 | 0 | 35.38 | 51.13 | 14794 | 95.38 | 42.44 | 37.65 | 1.49 | 42.44 | 0 | 608 | 428.6 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.1 | 312.6 | 0 | 306.4 | 100.02 | 15698 | 15697 | 315
03/26/22 10:57:06.184 | 543.2169 | 1371.654 | 53.6439 | 44.1667 | 9.4772 | 30.7371 | 51.0328 | 0 | 1790.3248 | 93.5718 | 85.0852 | 8.4865 | 24.9454 | 70.2874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.034 | 462.47 | 459.48 | 463.26 | 408.66 | 439.21 | 416.76 | 312.93 | 0.57607 | 0.30232 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6545511.4044 | 7590290.7026 | 7590290.7026 | 62.4284 | 62.1375 | 1.0018 | 0.99791 | 686559.5628 | 892778.6562 | 461.7367 | 0.48873 | 0 | 0 | 30.7371 | 24.9454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017852 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 563.4758 | 1368.1187 | 54.0637 | 44.2071 | 31.0656 | 1787.4922 | 83.4726 | 24.6705 | 461.2909 | 0.0067439 | 60.0097 | 0.55751 | 0.59287 | 92.2216 | 2.1824 | 0.15984 | 0.16946 | 5.1205 | 1.0256 | 0.35384 | 0 | 100 | 575.4 | 315 | 114.9 | 107.96 | 100.07 | 306.3 | 4 | 95.4 | 42.44 | 4 | 37.65 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.28 | 0 | 38.33 | 55 | 55 | 109.6 | 92.69 | 88.87 | 0 | 100.07 | 2.41 | 94.57 | 43.11 | 114.93 | 12.55 | 107.96 | 110 | 0 | 15698 | 82.87 | 116.34 | 220.83 | 214.92 | 220.15 | 0 | 35.55 | 51.29 | 14799 | 95.41 | 42.44 | 37.65 | 1.44 | 42.44 | 0 | 607 | 427.9 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.4 | 312 | 0 | 305.8 | 100.07 | 15697 | 15698 | 315
03/26/22 10:57:11.184 | 541.9039 | 1368.3406 | 53.6053 | 44.1283 | 9.477 | 30.6392 | 51.0576 | 0 | 1785.2516 | 93.6189 | 85.132 | 8.4868 | 25.1622 | 70.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0291 | 462.4401 | 459.4501 | 463.2301 | 408.6501 | 439.2601 | 416.8301 | 312.9301 | 0.57746 | 0.37235 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6529788.2045 | 7569312.131 | 7569312.131 | 62.4286 | 62.1369 | 1.0018 | 0.99791 | 684946.9062 | 890343.2503 | 461.7068 | 0.48877 | 0 | 0 | 30.6392 | 25.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017862 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 563.2757 | 1368.1117 | 54.0625 | 44.2093 | 31.0642 | 1787.4894 | 83.4924 | 24.6715 | 461.2962 | 0.0067552 | 60.0099 | 0.5577 | 0.58681 | 92.2393 | 2.1797 | 0.16245 | 0.16565 | 5.1216 | 1.0231 | 0.35291 | 0 | 100 | 575.2 | 317 | 115 | 107.96 | 100.07 | 307.3 | 4 | 95.45 | 42.44 | 4 | 37.65 | 43.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.35 | 0 | 38.33 | 55 | 55 | 109.68 | 92.73 | 88.93 | 0 | 100.07 | 2.41 | 94.61 | 43.11 | 115 | 12.51 | 107.96 | 110 | 0 | 15698 | 82.89 | 116.37 | 220.83 | 214.92 | 220.15 | 0 | 35.76 | 51.32 | 14804 | 95.45 | 42.44 | 37.65 | 1.38 | 42.44 | 0 | 607 | 426 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.4 | 311.8 | 0 | 305.6 | 100.07 | 15698 | 15698 | 316
03/26/22 10:57:16.185 | 541.7901 | 1367.7884 | 53.5776 | 44.0988 | 9.4788 | 30.7445 | 51.0485 | 0 | 1787.0734 | 93.6544 | 85.1647 | 8.4896 | 25.0779 | 70.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.027 | 462.43 | 459.44 | 463.21 | 408.62 | 439.25 | 416.86 | 312.92 | 0.57757 | 0.22269 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6528505.375 | 7579369.2668 | 7579369.2668 | 62.4286 | 62.1365 | 1.0018 | 0.99791 | 684671.6938 | 891246.9977 | 461.6934 | 0.48806 | 0 | 0 | 30.7445 | 25.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017851 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 563.0732 | 1368.0997 | 54.0611 | 44.2114 | 31.0614 | 1787.4582 | 83.5121 | 24.6735 | 461.3017 | 0.0067671 | 60.0102 | 0.55788 | 0.58206 | 92.2568 | 2.1754 | 0.1655 | 0.16185 | 5.1069 | 1.0209 | 0.3513 | 0 | 100 | 574.6 | 317 | 114.95 | 107.98 | 99.93 | 306 | 4 | 95.42 | 42.4 | 4 | 37.61 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.3 | 0 | 38.3 | 55 | 55 | 109.6 | 92.69 | 88.93 | 0 | 99.93 | 2.42 | 94.59 | 43.09 | 114.95 | 12.56 | 107.98 | 110 | 0 | 15703 | 82.91 | 116.39 | 220.83 | 214.92 | 220.15 | 0 | 35.72 | 50.98 | 14809 | 95.42 | 42.4 | 37.61 | 1.35 | 42.4 | 0 | 607 | 425.9 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574.9 | 311.3 | 0 | 305.1 | 99.98 | 15700 | 15703 | 318
03/26/22 10:57:21.185 | 541.8016 | 1367.3342 | 53.5481 | 44.0661 | 9.482 | 30.3008 | 51.0539 | 0 | 1789.2978 | 93.6925 | 85.1973 | 8.4952 | 25.8346 | 70.2838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0261 | 462.4501 | 459.4501 | 463.2001 | 408.8101 | 439.3501 | 416.9801 | 313.0401 | 0.57778 | 0.023058 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6528244.5434 | 7594629.5691 | 7594629.5691 | 62.4287 | 62.1361 | 1.0018 | 0.99791 | 684445.6323 | 892351.5071 | 461.7001 | 0.48733 | 0 | 0 | 30.3008 | 25.8346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017848 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 562.8815 | 1368.1116 | 54.0595 | 44.2133 | 31.0547 | 1787.4714 | 83.5318 | 24.6811 | 461.3075 | 0.0067795 | 60.0104 | 0.55805 | 0.57617 | 92.2744 | 2.1665 | 0.16897 | 0.15815 | 5.1095 | 1.0189 | 0.34906 | 0 | 100 | 575.6 | 316 | 114.98 | 107.98 | 100.12 | 305.9 | 4 | 95.43 | 42.4 | 4 | 37.61 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.33 | 0 | 38.3 | 55 | 55 | 109.63 | 92.7 | 89.03 | 0 | 100.12 | 2.42 | 94.6 | 43.09 | 114.98 | 12.55 | 107.98 | 110 | 0 | 15706 | 82.91 | 116.41 | 220.83 | 214.92 | 220.15 | 0 | 35.69 | 50.91 | 14814 | 95.43 | 42.4 | 37.61 | 1.35 | 42.4 | 0 | 607 | 426.3 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.6 | 312.1 | 0 | 305.9 | 100.1 | 15703 | 15706 | 316
03/26/22 10:57:26.184 | 541.3677 | 1365.8427 | 53.5303 | 44.0456 | 9.4847 | 30.9633 | 51.0339 | 0 | 1790.0048 | 93.7154 | 85.2161 | 8.4992 | 24.8695 | 70.2053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0261 | 462.4501 | 459.4501 | 463.2001 | 408.8101 | 439.3501 | 416.9801 | 313.0401 | 0.57824 | -0.10957 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6523589.1465 | 7600048.3095 | 7600048.3095 | 62.4288 | 62.1359 | 1.0018 | 0.99791 | 683699.7898 | 892701.3378 | 461.7001 | 0.48733 | 0 | 0 | 30.9633 | 24.8695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017847 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 562.69 | 1368.1246 | 54.0578 | 44.215 | 31.0514 | 1787.5253 | 83.5515 | 24.6835 | 461.3136 | 0.0067926 | 60.0106 | 0.55822 | 0.56816 | 92.292 | 2.1459 | 0.17273 | 0.15455 | 5.0845 | 1.017 | 0.3463 | 0 | 100 | 576.3 | 316 | 115 | 108 | 100.21 | 305 | 4 | 95.45 | 42.4 | 4 | 37.61 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.33 | 0 | 38.3 | 55 | 55 | 109.63 | 92.7 | 89.04 | 0 | 100.21 | 2.42 | 94.6 | 43.09 | 115 | 12.55 | 108 | 110 | 0 | 15706 | 82.93 | 116.41 | 220.83 | 214.92 | 220.15 | 0 | 35.89 | 51.21 | 14819 | 95.45 | 42.4 | 37.61 | 1.35 | 42.4 | 0 | 608 | 428 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 312.5 | 0 | 306.3 | 100.23 | 15707 | 15706 | 315
03/26/22 10:57:31.184 | 541.0141 | 1365.2028 | 53.5165 | 44.0291 | 9.4874 | 31.1047 | 51.0256 | 0 | 1789.2255 | 93.7331 | 85.2299 | 8.5031 | 24.2531 | 70.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.026 | 462.45 | 459.45 | 463.2 | 408.81 | 439.35 | 416.98 | 313.04 | 0.57862 | -0.14596 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6519444.3705 | 7598663.359 | 7598663.359 | 62.4288 | 62.1358 | 1.0018 | 0.99791 | 683095.7585 | 892287.83 | 461.7 | 0.48733 | 0 | 0 | 31.1047 | 24.2531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017845 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 562.4949 | 1368.1221 | 54.056 | 44.2166 | 31.0505 | 1787.5781 | 83.5711 | 24.6814 | 461.3197 | 0.006719 | 60.0109 | 0.5584 | 0.55947 | 92.3094 | 2.1489 | 0.17668 | 0.1511 | 5.0523 | 1.0151 | 0.34341 | 0 | 100 | 575.6 | 317 | 115 | 108 | 100.1 | 306.1 | 4 | 95.46 | 42.4 | 4 | 37.61 | 43.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.35 | 0 | 38.3 | 55 | 55 | 109.63 | 92.7 | 89.1 | 0 | 100.1 | 2.42 | 94.61 | 43.09 | 114.98 | 12.57 | 108 | 110 | 0 | 15706 | 82.95 | 116.46 | 220.83 | 214.92 | 220.15 | 0 | 36.12 | 51.42 | 14824 | 95.43 | 42.4 | 37.61 | 1.31 | 42.4 | 0 | 608 | 428.9 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 311.4 | 0 | 305.2 | 100.23 | 15706 | 15706 | 315
03/26/22 10:57:36.184 | 542.2208 | 1366.911 | 53.5003 | 44.0082 | 9.4922 | 31.0253 | 51.0197 | 0 | 1786.8876 | 93.7549 | 85.2452 | 8.5097 | 24.0613 | 70.2218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0241 | 462.5001 | 459.4701 | 463.2001 | 409.0201 | 439.3901 | 417.1201 | 313.1501 | 0.57753 | 0.095132 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6533902.578 | 7595185.488 | 7595185.488 | 62.4289 | 62.1355 | 1.0018 | 0.99791 | 684235.8547 | 891142.4283 | 461.7234 | 0.48803 | 0 | 0 | 31.0253 | 24.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017853 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 562.2946 | 1368.1073 | 54.054 | 44.218 | 31.0529 | 1787.5854 | 83.5907 | 24.6739 | 461.3257 | 0.0066885 | 60.011 | 0.55858 | 0.55261 | 92.3269 | 2.148 | 0.18087 | 0.14788 | 5.0503 | 1.0132 | 0.34088 | 0 | 100 | 576.3 | 317 | 115.03 | 108.02 | 100.17 | 305.3 | 4 | 95.46 | 42.4 | 4 | 37.61 | 43.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.35 | 0 | 38.29 | 55 | 55 | 109.68 | 92.72 | 89.08 | 0 | 100.17 | 2.42 | 94.61 | 43.07 | 115.03 | 12.56 | 108.02 | 110 | 0 | 15706 | 82.95 | 116.49 | 220.83 | 214.81 | 220.15 | 0 | 36.34 | 51.45 | 14829 | 95.46 | 42.4 | 37.61 | 1.28 | 42.4 | 0 | 608 | 428.6 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 311.2 | 0 | 305 | 100.23 | 15705 | 15706 | 317
03/26/22 10:57:41.184 | 542.0505 | 1365.853 | 53.4906 | 43.9945 | 9.4961 | 31.7623 | 51.0219 | 0 | 1783.6981 | 93.7686 | 85.254 | 8.5146 | 23.1781 | 70.2127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.021 | 462.52 | 459.48 | 463.19 | 409.15 | 439.42 | 417.21 | 313.22 | 0.57784 | 0.19686 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6532479.9855 | 7586281.3103 | 7586281.3103 | 62.4289 | 62.1354 | 1.0018 | 0.99791 | 683786.696 | 889777.1944 | 461.73 | 0.4873 | 0 | 0 | 31.7623 | 23.1781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.01786 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 562.0933 | 1368.086 | 54.0519 | 44.2193 | 31.0595 | 1787.5373 | 83.6101 | 24.6605 | 461.3317 | 0.0066798 | 60.0111 | 0.55876 | 0.54824 | 92.3442 | 2.1512 | 0.18519 | 0.1449 | 5.0458 | 1.0114 | 0.33838 | 0 | 100 | 576 | 315 | 115.03 | 108.02 | 100.12 | 304.9 | 4 | 95.46 | 42.4 | 4 | 37.61 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.35 | 0 | 38.3 | 55 | 55 | 109.68 | 92.73 | 89.14 | 0 | 100.12 | 2.42 | 94.61 | 43.09 | 115.05 | 12.55 | 108.02 | 110 | 0 | 15706 | 82.97 | 116.49 | 220.83 | 214.81 | 220.15 | 0 | 36.31 | 51.1 | 14834 | 95.47 | 42.4 | 37.61 | 1.23 | 42.4 | 0 | 608 | 428.5 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 310.8 | 0 | 304.6 | 100.21 | 15707 | 15706 | 316
03/26/22 10:57:46.184 | 542.2259 | 1365.7756 | 53.4816 | 43.9809 | 9.5007 | 31.4725 | 51.037 | 0 | 1778.8261 | 93.7814 | 85.2615 | 8.5199 | 23.5135 | 70.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0221 | 462.5501 | 459.5101 | 463.2001 | 409.2701 | 439.4201 | 417.2701 | 313.2901 | 0.57779 | 0.42159 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6534302.1475 | 7571304.5082 | 7571304.5082 | 62.4289 | 62.1353 | 1.0018 | 0.99791 | 683676.0009 | 887438.981 | 461.7534 | 0.48583 | 0 | 0 | 31.4725 | 23.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017869 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 561.8913 | 1368.0618 | 54.0497 | 44.2205 | 31.064 | 1787.4567 | 83.6295 | 24.6493 | 461.3379 | 0.0066714 | 60.0112 | 0.55894 | 0.54571 | 92.3615 | 2.1526 | 0.18955 | 0.14205 | 5.0685 | 1.0094 | 0.33591 | 0 | 100 | 576.1 | 317 | 115.08 | 108.02 | 100.19 | 306.9 | 4 | 95.48 | 42.41 | 4 | 37.63 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.45 | 0 | 38.3 | 55 | 55 | 109.73 | 92.74 | 89.12 | 0 | 100.16 | 2.42 | 94.66 | 43.09 | 115.08 | 12.54 | 108.02 | 110 | 0 | 15706 | 83 | 116.49 | 220.83 | 214.81 | 220.15 | 0 | 36.23 | 50.86 | 14839 | 95.48 | 42.41 | 37.63 | 1.2 | 42.41 | 0 | 608 | 428.6 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 313.1 | 0 | 306.9 | 100.19 | 15706 | 15706 | 317
03/26/22 10:57:51.184 | 542.6771 | 1366.0027 | 53.472 | 43.9656 | 9.5064 | 31.3285 | 51.0331 | 0 | 1778.2946 | 93.7963 | 85.2705 | 8.5258 | 23.8771 | 70.2115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0231 | 462.6001 | 459.5501 | 463.2201 | 409.4101 | 439.4101 | 417.3001 | 313.3601 | 0.57743 | 0.47695 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6539626.369 | 7572650.4407 | 7572650.4407 | 62.429 | 62.1352 | 1.0018 | 0.99791 | 683782.3782 | 886853.2426 | 461.7901 | 0.48507 | 0 | 0 | 31.3285 | 23.8771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017869 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 561.6881 | 1368.0326 | 54.0474 | 44.2215 | 31.0715 | 1787.371 | 83.6488 | 24.6362 | 461.3441 | 0.006685 | 60.0112 | 0.55912 | 0.54352 | 92.3787 | 2.1446 | 0.19405 | 0.13959 | 5.0925 | 1.0074 | 0.33372 | 0 | 100 | 576.2 | 316 | 115.15 | 108.04 | 100.17 | 307.1 | 4 | 95.52 | 42.43 | 4 | 37.64 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.53 | 0 | 38.31 | 55 | 55 | 109.8 | 92.79 | 89.22 | 0 | 100.17 | 2.42 | 94.7 | 43.1 | 115.15 | 12.52 | 108.04 | 110 | 0 | 15706 | 83 | 116.49 | 220.83 | 214.81 | 220.15 | 0 | 36.21 | 50.8 | 14844 | 95.52 | 42.43 | 37.64 | 1.19 | 42.43 | 0 | 608 | 427.3 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 313.3 | 0 | 307.1 | 100.21 | 15707 | 15706 | 316
03/26/22 10:57:56.184 | 542.9708 | 1365.9821 | 53.463 | 43.9513 | 9.5116 | 31.621 | 51.0395 | 0 | 1779.3422 | 93.812 | 85.2818 | 8.5302 | 23.5869 | 70.1954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.022 | 462.65 | 459.56 | 463.21 | 409.64 | 439.39 | 417.34 | 313.44 | 0.57727 | 0.42444 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6543407.3029 | 7580664.9915 | 7580664.9915 | 62.429 | 62.135 | 1.0018 | 0.99791 | 683772.4563 | 887374.0538 | 461.8067 | 0.4865 | 0 | 0 | 31.621 | 23.5869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.01788 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 561.4897 | 1368.0124 | 54.0449 | 44.2224 | 31.0792 | 1787.2728 | 83.6681 | 24.6208 | 461.3504 | 0.0066985 | 60.0112 | 0.5593 | 0.5427 | 92.3958 | 2.1433 | 0.19856 | 0.13732 | 5.0654 | 1.0052 | 0.33168 | 0 | 100 | 575.8 | 317 | 115.15 | 108.06 | 100.17 | 307.4 | 4 | 95.52 | 42.41 | 4 | 37.63 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.58 | 0 | 38.3 | 55 | 55 | 109.85 | 92.82 | 89.2 | 0 | 100.17 | 2.42 | 94.71 | 43.09 | 115.18 | 12.54 | 108.06 | 110 | 0 | 15706 | 83.02 | 116.49 | 220.83 | 214.81 | 220.15 | 0 | 36.22 | 50.72 | 14849 | 95.52 | 42.41 | 37.63 | 1.18 | 42.41 | 0 | 608 | 427.5 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 313.6 | 0 | 307.4 | 100.14 | 15708 | 15706 | 317
03/26/22 10:58:01.184 | 542.8995 | 1365.8324 | 53.4591 | 43.945 | 9.514 | 31.8991 | 51.0473 | 0 | 1775.936 | 93.8207 | 85.2887 | 8.532 | 23.5435 | 70.1921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0171 | 462.6901 | 459.5801 | 463.1601 | 409.8901 | 439.2901 | 417.3701 | 313.4701 | 0.5774 | 0.559 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6542826.8939 | 7569893.9668 | 7569893.9668 | 62.429 | 62.135 | 1.0018 | 0.99791 | 683545.2418 | 885993.6676 | 461.8101 | 0.48288 | 0 | 0 | 31.8991 | 23.5435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017894 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 561.2904 | 1367.9881 | 54.0424 | 44.2232 | 31.086 | 1787.1696 | 83.6873 | 24.6085 | 461.3567 | 0.0067121 | 60.0112 | 0.55948 | 0.54198 | 92.413 | 2.1475 | 0.20305 | 0.13523 | 5.0774 | 1.0028 | 0.32951 | 0 | 100 | 576.1 | 315 | 115.25 | 108.08 | 100.19 | 304.7 | 4 | 95.56 | 42.41 | 4 | 37.63 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.65 | 0 | 38.3 | 55 | 55 | 109.88 | 92.83 | 89.32 | 0 | 100.19 | 2.42 | 94.76 | 43.09 | 115.25 | 12.52 | 108.08 | 110 | 0 | 15706 | 83.04 | 116.51 | 220.83 | 214.81 | 220.15 | 0 | 36.17 | 50.6 | 14854 | 95.57 | 42.41 | 37.63 | 1.18 | 42.41 | 0 | 608 | 428.7 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 311.3 | 0 | 305.1 | 100.17 | 15706 | 15706 | 316
03/26/22 10:58:06.184 | 543.4483 | 1366.3949 | 53.456 | 43.9389 | 9.5171 | 31.4009 | 51.0211 | 0 | 1776.3024 | 93.831 | 85.2973 | 8.5337 | 24.5939 | 70.2136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 462.68 | 459.58 | 463.13 | 409.98 | 439.26 | 417.39 | 313.47 | 0.57682 | 0.61404 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6548952.6693 | 7571918.3295 | 7571918.3295 | 62.429 | 62.1348 | 1.0018 | 0.99791 | 683979.4156 | 885855.7585 | 461.7967 | 0.48001 | 0 | 0 | 31.4009 | 24.5939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017896 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 561.096 | 1367.9754 | 54.0398 | 44.2238 | 31.0848 | 1787.0797 | 83.7064 | 24.6088 | 461.363 | 0.0067257 | 60.0112 | 0.55965 | 0.54125 | 92.43 | 2.1508 | 0.20754 | 0.13354 | 5.1283 | 1.0005 | 0.32722 | 0 | 100 | 575.9 | 318 | 115.35 | 108.1 | 100.19 | 305.8 | 4 | 95.62 | 42.43 | 4 | 37.65 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.7 | 0 | 38.31 | 55 | 55 | 109.9 | 92.85 | 89.34 | 0 | 100.19 | 2.42 | 94.79 | 43.1 | 115.35 | 12.48 | 108.1 | 110 | 0 | 15706 | 83.04 | 116.51 | 220.83 | 214.81 | 220.15 | 0 | 36.18 | 50.69 | 14859 | 95.62 | 42.43 | 37.64 | 1.17 | 42.43 | 0 | 607 | 425.6 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.9 | 312.5 | 0 | 306.3 | 100.16 | 15708 | 15706 | 317
03/26/22 10:58:11.184 | 543.5219 | 1366.3691 | 53.4532 | 43.9327 | 9.5205 | 30.7329 | 51.0182 | 0 | 1782.0001 | 93.8431 | 85.308 | 8.535 | 25.5237 | 70.2177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0141 | 462.6801 | 459.5801 | 463.1301 | 409.9801 | 439.2601 | 417.3901 | 313.4701 | 0.57674 | 0.38578 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6549252.976 | 7589521.5691 | 7589521.5691 | 62.429 | 62.1347 | 1.0018 | 0.99791 | 683876.1824 | 887679.3734 | 461.7967 | 0.48001 | 0 | 0 | 30.7329 | 25.5237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017886 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 560.9003 | 1367.9587 | 54.0371 | 44.2244 | 31.0801 | 1787.0541 | 83.7255 | 24.617 | 461.3694 | 0.0067393 | 60.0111 | 0.55982 | 0.53769 | 92.447 | 2.1515 | 0.21199 | 0.13207 | 5.1422 | 0.99797 | 0.3245 | 0 | 100 | 576.1 | 318 | 115.25 | 108.12 | 100.19 | 306.2 | 4 | 95.57 | 42.41 | 4 | 37.63 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.65 | 0 | 38.31 | 55 | 55 | 109.9 | 92.85 | 89.32 | 0 | 100.19 | 2.42 | 94.76 | 43.1 | 115.23 | 12.56 | 108.12 | 110 | 0 | 15706 | 83.06 | 116.54 | 220.83 | 214.81 | 220.15 | 0 | 36.27 | 50.75 | 14864 | 95.56 | 42.41 | 37.63 | 1.18 | 42.41 | 0 | 607 | 425.2 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 312.4 | 0 | 306.2 | 100.19 | 15705 | 15706 | 318
03/26/22 10:58:16.183 | 545.1531 | 1369.5948 | 53.4496 | 43.925 | 9.5246 | 31.227 | 51.0461 | 0 | 1790.7171 | 93.8636 | 85.3274 | 8.5361 | 24.6723 | 70.2334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0181 | 462.6901 | 459.5901 | 463.0901 | 410.1401 | 439.2201 | 417.5201 | 313.5201 | 0.5751 | 0.044221 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6569320.92 | 7635581.3547 | 7635581.3547 | 62.4291 | 62.1345 | 1.0018 | 0.99791 | 685581.4458 | 893040.0093 | 461.7901 | 0.47641 | 0 | 0 | 31.227 | 24.6723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017878 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 560.7133 | 1367.9613 | 54.0342 | 44.2249 | 31.0806 | 1787.0619 | 83.7446 | 24.6179 | 461.3757 | 0.006753 | 60.0111 | 0.55998 | 0.53286 | 92.4639 | 2.1501 | 0.21635 | 0.13081 | 5.1385 | 0.99529 | 0.32151 | 0 | 100 | 576.6 | 317 | 115.23 | 108.12 | 100.28 | 306.9 | 4 | 95.55 | 42.43 | 4 | 37.64 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.6 | 0 | 38.31 | 55 | 55 | 109.88 | 92.82 | 89.4 | 0 | 100.28 | 2.42 | 94.74 | 43.1 | 115.23 | 12.57 | 108.12 | 110 | 0 | 15706 | 83.06 | 116.54 | 220.83 | 214.81 | 220.15 | 0 | 36.25 | 50.65 | 14869 | 95.55 | 42.43 | 37.64 | 1.17 | 42.43 | 0 | 607 | 428.6 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 311.5 | 0 | 305.3 | 100.23 | 15705 | 15706 | 316
03/26/22 10:58:21.184 | 545.0309 | 1369.0787 | 53.4483 | 43.9222 | 9.5261 | 30.6514 | 51.0481 | 0 | 1791.197 | 93.8752 | 85.3393 | 8.5359 | 25.5163 | 70.2408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.018 | 462.69 | 459.59 | 463.09 | 410.14 | 439.22 | 417.52 | 313.52 | 0.57523 | -0.016153 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6567338.0363 | 7638346.0711 | 7638346.0711 | 62.4291 | 62.1344 | 1.0018 | 0.99791 | 685323.1529 | 893277.5991 | 461.79 | 0.47641 | 0 | 0 | 30.6514 | 25.5163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017871 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 560.5389 | 1367.9913 | 54.0313 | 44.2252 | 31.0821 | 1787.0748 | 83.7638 | 24.6182 | 461.3821 | 0.0067667 | 60.0112 | 0.56013 | 0.52987 | 92.4809 | 2.1277 | 0.22068 | 0.1299 | 5.146 | 0.99265 | 0.31822 | 0 | 100 | 577.1 | 315 | 115.28 | 108.12 | 100.37 | 305 | 4 | 95.58 | 42.44 | 4 | 37.65 | 43.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.63 | 0 | 38.34 | 55 | 55 | 109.85 | 92.82 | 89.46 | 0 | 100.37 | 2.42 | 94.75 | 43.12 | 115.28 | 12.54 | 108.12 | 110 | 0 | 15706 | 83.06 | 116.56 | 220.83 | 214.81 | 220.15 | 0 | 36.26 | 50.67 | 14874 | 95.58 | 42.44 | 37.65 | 1.14 | 42.44 | 0 | 608 | 428 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 311.7 | 0 | 305.5 | 100.37 | 15707 | 15706 | 315
03/26/22 10:58:26.183 | 544.5573 | 1367.6232 | 53.4472 | 43.9193 | 9.5279 | 31.0647 | 51.0425 | 0 | 1793.4524 | 93.8924 | 85.3577 | 8.5347 | 24.8097 | 70.2412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.017 | 462.68 | 459.59 | 463.06 | 410.19 | 439.23 | 417.63 | 313.55 | 0.57579 | -0.18592 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6561989.6768 | 7646068.6737 | 7646068.6737 | 62.4291 | 62.1342 | 1.0018 | 0.99791 | 684594.6499 | 894399.597 | 461.7767 | 0.47353 | 0 | 0 | 31.0647 | 24.8097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017861 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 560.3588 | 1368.0079 | 54.0283 | 44.2255 | 31.0803 | 1787.0788 | 83.7829 | 24.6233 | 461.3885 | 0.0067805 | 60.0111 | 0.56029 | 0.52658 | 92.4978 | 2.1228 | 0.2249 | 0.12914 | 5.1494 | 0.9898 | 0.31449 | 0 | 100 | 576.2 | 313 | 115.13 | 108.12 | 100.21 | 303.7 | 4 | 95.51 | 42.44 | 4 | 37.65 | 43.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.55 | 0 | 38.33 | 55 | 55 | 109.83 | 92.81 | 89.44 | 0 | 100.21 | 2.42 | 94.71 | 43.11 | 115.13 | 12.61 | 108.12 | 110 | 0 | 15706 | 83.06 | 116.58 | 220.83 | 214.81 | 220.15 | 0 | 36.3 | 50.69 | 14879 | 95.51 | 42.44 | 37.65 | 1.12 | 42.44 | 0 | 607 | 429.9 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 311.3 | 0 | 305.1 | 100.28 | 15706 | 15706 | 315
03/26/22 10:58:31.184 | 543.6576 | 1365.1872 | 53.4474 | 43.9183 | 9.5291 | 31.6696 | 51.0436 | 0 | 1794.7323 | 93.9029 | 85.3688 | 8.5341 | 23.919 | 70.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0171 | 462.6401 | 459.5901 | 463.0401 | 410.2301 | 439.3501 | 417.8101 | 313.6201 | 0.57687 | -0.37233 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6551674.7229 | 7649981.2728 | 7649981.2728 | 62.4291 | 62.134 | 1.0018 | 0.99791 | 683375.2527 | 895036.2556 | 461.7567 | 0.46922 | 0 | 0 | 31.6696 | 23.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017863 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 560.163 | 1367.9862 | 54.0253 | 44.2257 | 31.0818 | 1787.1297 | 83.802 | 24.6229 | 461.3949 | 0.0067942 | 60.0111 | 0.56046 | 0.51863 | 92.5148 | 2.1253 | 0.22902 | 0.1286 | 5.1794 | 0.98688 | 0.31059 | 0 | 100 | 576.5 | 317 | 115.05 | 108.12 | 100.3 | 306.6 | 4 | 95.47 | 42.44 | 4 | 37.65 | 43.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.53 | 0 | 38.34 | 55 | 55 | 109.78 | 92.78 | 89.52 | 0 | 100.3 | 2.42 | 94.7 | 43.12 | 115.08 | 12.65 | 108.12 | 110 | 0 | 15706 | 83.08 | 116.61 | 220.83 | 214.81 | 220.15 | 0 | 36.35 | 50.73 | 14884 | 95.47 | 42.44 | 37.65 | 1.14 | 42.44 | 0 | 607 | 429.6 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.5 | 311.9 | 0 | 305.7 | 100.26 | 15705 | 15706 | 317
03/26/22 10:58:36.184 | 545.5384 | 1369.5586 | 53.4494 | 43.9178 | 9.5316 | 31.3164 | 51.0388 | 0 | 1790.4848 | 93.9208 | 85.387 | 8.5338 | 24.7212 | 70.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 462.6501 | 459.6101 | 463.0501 | 410.2501 | 439.4101 | 417.9501 | 313.6901 | 0.57501 | 0.15596 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6574022.5244 | 7632463.673 | 7632463.673 | 62.4291 | 62.1338 | 1.0018 | 0.99791 | 685563.3654 | 892915.3155 | 461.7701 | 0.46777 | 0 | 0 | 31.3164 | 24.7212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017863 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 559.9636 | 1367.9617 | 54.0221 | 44.2259 | 31.0825 | 1787.1915 | 83.8211 | 24.6223 | 461.4012 | 0.0067428 | 60.0111 | 0.56063 | 0.50939 | 92.5317 | 2.1245 | 0.23303 | 0.12822 | 5.1947 | 0.98375 | 0.30632 | 0 | 100 | 576.4 | 316 | 115.13 | 108.1 | 100.24 | 304.1 | 4 | 95.51 | 42.45 | 4 | 37.66 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.58 | 0 | 38.35 | 55 | 55 | 109.8 | 92.79 | 89.48 | 0 | 100.35 | 2.42 | 94.73 | 43.14 | 115.18 | 12.58 | 108.1 | 110 | 0 | 15706 | 83.08 | 116.63 | 220.83 | 214.81 | 220.15 | 0 | 36.41 | 50.8 | 14889 | 95.52 | 42.45 | 37.66 | 1.18 | 42.45 | 0 | 608 | 428.3 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.9 | 314.4 | 0 | 308.1 | 100.33 | 15706 | 15706 | 317
03/26/22 10:58:41.183 | 546.8572 | 1372.6294 | 53.4512 | 43.9183 | 9.533 | 31.2028 | 51.0554 | 0 | 1790.9338 | 93.9301 | 85.396 | 8.5341 | 24.6597 | 70.2433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 462.6601 | 459.6301 | 463.0701 | 410.2101 | 439.4201 | 417.9901 | 313.7101 | 0.57366 | 0.36556 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6589932.0679 | 7632334.6102 | 7632334.6102 | 62.4291 | 62.1338 | 1.0018 | 0.99791 | 687139.2106 | 892888.4846 | 461.7867 | 0.46703 | 0 | 0 | 31.2028 | 24.6597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017857 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 559.7935 | 1368.0043 | 54.0189 | 44.226 | 31.081 | 1787.2729 | 83.8403 | 24.6277 | 461.4074 | 0.0066913 | 60.0111 | 0.56078 | 0.50376 | 92.5486 | 2.1423 | 0.23689 | 0.12807 | 5.1294 | 0.98064 | 0.30232 | 0 | 100 | 576.5 | 316 | 115.23 | 108.12 | 100.26 | 305.7 | 4 | 95.57 | 42.45 | 4 | 37.66 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.58 | 0 | 38.35 | 55 | 55 | 109.8 | 92.79 | 89.48 | 0 | 100.26 | 2.42 | 94.73 | 43.14 | 115.23 | 12.56 | 108.12 | 110 | 0 | 15706 | 83.1 | 116.65 | 220.83 | 214.81 | 220.15 | 0 | 36.48 | 50.86 | 14894 | 95.56 | 42.45 | 37.66 | 1.18 | 42.45 | 0 | 608 | 430.9 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.5 | 312 | 0 | 305.7 | 100.26 | 15707 | 15706 | 316
03/26/22 10:58:46.183 | 547.1492 | 1372.9701 | 53.4542 | 43.9195 | 9.5347 | 30.3026 | 51.0401 | 0 | 1789.1326 | 93.9403 | 85.4049 | 8.5354 | 25.1722 | 70.2838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0081 | 462.6601 | 459.6501 | 463.0901 | 410.1801 | 439.5201 | 418.1001 | 313.7601 | 0.57345 | 0.43551 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6592548.373 | 7629670.4077 | 7629670.4077 | 62.4291 | 62.1336 | 1.0018 | 0.99791 | 687384.5102 | 892395.4919 | 461.8001 | 0.46557 | 0 | 0 | 30.3026 | 25.1722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017862 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 559.628 | 1368.0582 | 54.0157 | 44.226 | 31.0768 | 1787.3341 | 83.8594 | 24.6307 | 461.4136 | 0.0066394 | 60.0111 | 0.56092 | 0.49994 | 92.5655 | 2.1455 | 0.24061 | 0.128 | 5.0968 | 0.97732 | 0.29863 | 0 | 100 | 576.4 | 315 | 115.2 | 108.12 | 100.24 | 306.4 | 4 | 95.53 | 42.44 | 4 | 37.65 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.55 | 0 | 38.34 | 55 | 55 | 109.8 | 92.79 | 89.5 | 0 | 100.28 | 2.42 | 94.71 | 43.12 | 115.2 | 12.57 | 108.12 | 110 | 0 | 15706 | 83.1 | 116.65 | 220.83 | 214.81 | 220.15 | 0 | 36.58 | 50.92 | 14899 | 95.55 | 42.44 | 37.65 | 1.19 | 42.44 | 0 | 608 | 428.5 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 312.6 | 0 | 306.4 | 100.24 | 15705 | 15706 | 315
03/26/22 10:58:51.183 | 546.665 | 1371.4166 | 53.4568 | 43.9208 | 9.536 | 30.336 | 51.0298 | 0 | 1789.7778 | 93.9464 | 85.4094 | 8.537 | 25.2135 | 70.2623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.008 | 462.66 | 459.65 | 463.09 | 410.18 | 439.52 | 418.1 | 313.76 | 0.57395 | 0.28281 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6586636.6392 | 7635604.9364 | 7635604.9364 | 62.4291 | 62.1336 | 1.0018 | 0.99791 | 686692.0366 | 892909.5753 | 461.8 | 0.46557 | 0 | 0 | 30.336 | 25.2135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017858 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 559.4565 | 1368.0957 | 54.0124 | 44.226 | 31.0708 | 1787.3736 | 83.8785 | 24.6361 | 461.4196 | 0.0066092 | 60.0111 | 0.56106 | 0.49605 | 92.5824 | 2.1448 | 0.24417 | 0.12804 | 5.0879 | 0.97382 | 0.29537 | 0 | 100 | 577.1 | 317 | 115.25 | 108.12 | 100.37 | 307.1 | 4 | 95.57 | 42.45 | 4 | 37.66 | 43.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.58 | 0 | 38.35 | 55 | 55 | 109.78 | 92.78 | 89.44 | 0 | 100.28 | 2.42 | 94.73 | 43.14 | 115.23 | 12.56 | 108.12 | 110 | 0 | 15706 | 83.12 | 116.68 | 220.83 | 214.81 | 220.15 | 0 | 36.59 | 50.82 | 14904 | 95.56 | 42.45 | 37.66 | 1.16 | 42.45 | 0 | 608 | 428.3 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 312.2 | 0 | 306 | 100.37 | 15703 | 15706 | 316
03/26/22 10:58:56.183 | 546.2649 | 1370.3844 | 53.4627 | 43.9241 | 9.5386 | 31.1438 | 51.032 | 0 | 1786.1135 | 93.9564 | 85.4148 | 8.5416 | 24.3087 | 70.2272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0031 | 462.6501 | 459.6601 | 463.1101 | 410.1401 | 439.6101 | 418.1901 | 313.8001 | 0.57445 | 0.43318 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6582605.7641 | 7620254.8014 | 7620254.8014 | 62.429 | 62.1335 | 1.0018 | 0.99791 | 685976.1353 | 890731.1826 | 461.8068 | 0.46484 | 0 | 0 | 31.1438 | 24.3087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017866 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 559.2683 | 1368.0959 | 54.009 | 44.2259 | 31.0711 | 1787.3972 | 83.8975 | 24.6348 | 461.4255 | 0.0066219 | 60.011 | 0.56123 | 0.49066 | 92.5992 | 2.145 | 0.24755 | 0.1282 | 5.0721 | 0.97023 | 0.29243 | 0 | 100 | 576.4 | 315 | 115.3 | 108.1 | 100.26 | 304.5 | 4 | 95.6 | 42.46 | 4 | 37.68 | 43.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.63 | 0 | 38.35 | 55 | 55 | 109.85 | 92.82 | 89.42 | 0 | 100.31 | 2.42 | 94.75 | 43.14 | 115.28 | 12.52 | 108.1 | 110 | 0 | 15706 | 83.12 | 116.68 | 220.83 | 214.81 | 220.15 | 0 | 36.55 | 50.7 | 14909 | 95.58 | 42.46 | 37.68 | 1.15 | 42.46 | 0 | 608 | 426.2 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.7 | 312.5 | 0 | 306.3 | 100.3 | 15707 | 15706 | 316
03/26/22 10:59:01.184 | 546.2194 | 1370.0902 | 53.4665 | 43.9267 | 9.5398 | 31.0954 | 51.0345 | 0 | 1783.4761 | 93.9602 | 85.4158 | 8.5444 | 24.6105 | 70.2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0021 | 462.6801 | 459.7201 | 463.1701 | 410.0301 | 439.5701 | 418.1101 | 313.7801 | 0.57446 | 0.53544 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6582011.0994 | 7611806.5582 | 7611806.5582 | 62.429 | 62.1335 | 1.0018 | 0.99791 | 685828.7179 | 889415.8187 | 461.8567 | 0.46263 | 0 | 0 | 31.0954 | 24.6105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017873 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 559.0824 | 1368.1027 | 54.0056 | 44.2258 | 31.0731 | 1787.3846 | 83.9164 | 24.6311 | 461.4314 | 0.0064395 | 60.011 | 0.56138 | 0.4876 | 92.6159 | 2.1502 | 0.25079 | 0.12846 | 5.0787 | 0.96644 | 0.28934 | 0 | 100 | 576.1 | 316 | 115.38 | 108.12 | 100.24 | 302.8 | 4 | 95.63 | 42.44 | 4 | 37.65 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.7 | 0 | 38.34 | 55 | 55 | 109.93 | 92.86 | 89.48 | 0 | 100.26 | 2.42 | 94.79 | 43.12 | 115.38 | 12.5 | 108.12 | 110 | 0 | 15706 | 83.12 | 116.68 | 220.83 | 214.81 | 220.15 | 0 | 36.5 | 50.55 | 14913 | 95.63 | 42.44 | 37.65 | 1.16 | 42.44 | 0 | 608 | 429.9 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 309 | 0 | 302.8 | 100.19 | 15708 | 15706 | 316
03/26/22 10:59:06.183 | 545.9538 | 1369.347 | 53.47 | 43.9296 | 9.5404 | 31.3996 | 51.0405 | 0 | 1784.4361 | 93.9621 | 85.4157 | 8.5464 | 24.6824 | 70.2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0011 | 462.7101 | 459.7401 | 463.1901 | 410.0201 | 439.5501 | 418.0701 | 313.7801 | 0.57474 | 0.41815 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6579076.5152 | 7617816.8639 | 7617816.8639 | 62.429 | 62.1334 | 1.0018 | 0.99791 | 685456.5556 | 889894.5585 | 461.8801 | 0.46332 | 0 | 0 | 31.3996 | 24.6824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017866 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 558.9008 | 1368.1224 | 54.0021 | 44.2256 | 31.0762 | 1787.349 | 83.9352 | 24.6272 | 461.4371 | 0.0063652 | 60.011 | 0.56154 | 0.48634 | 92.6325 | 2.1527 | 0.25388 | 0.12884 | 5.0878 | 0.96254 | 0.28745 | 0 | 100 | 576.7 | 316 | 115.33 | 108.14 | 100.24 | 305.6 | 4 | 95.61 | 42.44 | 4 | 37.65 | 43.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.68 | 0 | 38.34 | 55 | 55 | 109.95 | 92.87 | 89.52 | 0 | 100.24 | 2.42 | 94.78 | 43.12 | 115.35 | 12.53 | 108.14 | 110 | 0 | 15706 | 83.12 | 116.68 | 220.83 | 214.81 | 220.15 | 0 | 36.38 | 50.39 | 14918 | 95.61 | 42.44 | 37.65 | 1.16 | 42.44 | 0 | 608 | 426.2 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.7 | 311.8 | 0 | 305.6 | 100.3 | 15708 | 15706 | 316
03/26/22 10:59:11.184 | 544.9801 | 1366.4156 | 53.4733 | 43.9332 | 9.5401 | 31.9111 | 51.0397 | 0 | 1786.965 | 93.9641 | 85.4155 | 8.5486 | 23.7742 | 70.2272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.001 | 462.71 | 459.75 | 463.2 | 410 | 439.5 | 418.04 | 313.76 | 0.57573 | 0.14385 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6567672.8383 | 7627354.4672 | 7627354.4672 | 62.429 | 62.1334 | 1.0018 | 0.99791 | 684247.3777 | 890921.5396 | 461.8867 | 0.4626 | 0 | 0 | 31.9111 | 23.7742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017868 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 558.699 | 1368.0952 | 53.9985 | 44.2254 | 31.085 | 1787.3106 | 83.9538 | 24.6174 | 461.4428 | 0.0062906 | 60.011 | 0.56172 | 0.48214 | 92.649 | 2.1365 | 0.25678 | 0.12933 | 5.0679 | 0.95859 | 0.28606 | 0 | 100 | 576.8 | 317 | 115.28 | 108.16 | 100.31 | 307 | 4 | 95.58 | 42.45 | 4 | 37.66 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.65 | 0 | 38.35 | 55 | 55 | 109.9 | 92.85 | 89.54 | 0 | 100.31 | 2.42 | 94.76 | 43.14 | 115.28 | 12.57 | 108.16 | 110 | 0 | 15706 | 83.12 | 116.68 | 220.83 | 214.81 | 220.15 | 0 | 36.34 | 50.35 | 14924 | 95.58 | 42.45 | 37.66 | 1.2 | 42.45 | 0 | 608 | 426.1 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 311.9 | 0 | 305.6 | 100.4 | 15707 | 15706 | 317
03/26/22 10:59:16.184 | 544.34 | 1365.404 | 53.4747 | 43.935 | 9.5397 | 31.7369 | 51.0304 | 0 | 1786.0928 | 93.9652 | 85.4156 | 8.5496 | 23.5363 | 70.2441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0011 | 462.7101 | 459.7501 | 463.2001 | 410.0001 | 439.5001 | 418.0401 | 313.7601 | 0.5764 | 0.05379 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6559926.8892 | 7626416.656 | 7626416.656 | 62.429 | 62.1334 | 1.0018 | 0.99791 | 683482.5831 | 890720.768 | 461.8867 | 0.4626 | 0 | 0 | 31.7369 | 23.5363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017874 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 558.4987 | 1368.0735 | 53.9949 | 44.2251 | 31.0879 | 1787.2762 | 83.9722 | 24.6125 | 461.4484 | 0.0062377 | 60.011 | 0.56189 | 0.47768 | 92.6653 | 2.1439 | 0.25953 | 0.12992 | 5.055 | 0.95455 | 0.28487 | 0 | 100 | 576.5 | 316 | 115.3 | 108.16 | 100.26 | 305.6 | 4 | 95.58 | 42.45 | 4 | 37.66 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.73 | 0 | 38.35 | 55 | 55 | 109.95 | 92.87 | 89.54 | 0 | 100.26 | 2.42 | 94.8 | 43.14 | 115.28 | 12.57 | 108.16 | 110 | 0 | 15706 | 83.12 | 116.68 | 220.83 | 214.81 | 220.15 | 0 | 36.24 | 50.27 | 14929 | 95.58 | 42.45 | 37.66 | 1.2 | 42.45 | 0 | 608 | 428.6 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 313.1 | 0 | 306.8 | 100.23 | 15707 | 15706 | 316
03/26/22 10:59:21.183 | 545.0734 | 1367.5613 | 53.4771 | 43.9397 | 9.5374 | 30.5883 | 51.0275 | 0 | 1785.9431 | 93.9687 | 85.4189 | 8.5498 | 25.2014 | 70.2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.001 | 462.74 | 459.76 | 463.2 | 409.99 | 439.45 | 417.91 | 313.72 | 0.57556 | 0.13597 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6567762.7692 | 7627840.6508 | 7627840.6508 | 62.429 | 62.1334 | 1.0018 | 0.99791 | 684562.3795 | 890645.6345 | 461.9 | 0.4633 | 0 | 0 | 30.5883 | 25.2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017868 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 558.3066 | 1368.0741 | 53.9912 | 44.2248 | 31.0839 | 1787.2538 | 83.9906 | 24.6171 | 461.454 | 0.0061847 | 60.0111 | 0.56205 | 0.47357 | 92.6815 | 2.1437 | 0.26215 | 0.13054 | 5.0519 | 0.95031 | 0.2838 | 0 | 100 | 576.4 | 316 | 115.45 | 108.18 | 100.24 | 305.6 | 4 | 95.67 | 42.46 | 4 | 37.68 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.8 | 0 | 38.35 | 55 | 55 | 110 | 92.9 | 89.54 | 0 | 100.24 | 2.42 | 94.84 | 43.14 | 115.45 | 12.51 | 108.18 | 110 | 0 | 15706 | 83.12 | 116.7 | 220.83 | 214.92 | 220.15 | 0 | 36.22 | 50.31 | 14934 | 95.67 | 42.46 | 37.68 | 1.17 | 42.46 | 0 | 608 | 428.4 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 314.2 | 0 | 308 | 100.28 | 15705 | 15706 | 318
03/26/22 10:59:26.183 | 545.3196 | 1368.8051 | 53.4776 | 43.9415 | 9.5361 | 31.4443 | 51.0322 | 0 | 1787.254 | 93.9707 | 85.4224 | 8.5483 | 24.2778 | 70.1797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.003 | 462.74 | 459.76 | 463.19 | 410.07 | 439.44 | 417.89 | 313.75 | 0.57535 | 0.14114 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6571302.0326 | 7631083.2415 | 7631083.2415 | 62.429 | 62.1334 | 1.0018 | 0.99791 | 684949.8802 | 891234.6362 | 461.8967 | 0.46259 | 0 | 0 | 31.4443 | 24.2778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017869 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 558.1251 | 1368.1045 | 53.9874 | 44.2244 | 31.0866 | 1787.2485 | 84.0089 | 24.6153 | 461.4595 | 0.0061966 | 60.0111 | 0.56221 | 0.47045 | 92.6976 | 2.1145 | 0.26462 | 0.13128 | 5.0514 | 0.94603 | 0.28268 | 0 | 100 | 577.1 | 318 | 115.43 | 108.2 | 100.37 | 308.4 | 4 | 95.66 | 42.48 | 4 | 37.69 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.75 | 0 | 38.36 | 55 | 55 | 109.95 | 92.87 | 89.52 | 0 | 100.37 | 2.42 | 94.82 | 43.15 | 115.43 | 12.54 | 108.2 | 110 | 0 | 15706 | 83.15 | 116.73 | 220.95 | 214.92 | 220.15 | 0 | 36.16 | 50.27 | 14939 | 95.66 | 42.48 | 37.69 | 1.16 | 42.48 | 0 | 608 | 426.5 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.2 | 314.1 | 0 | 307.9 | 100.38 | 15705 | 15706 | 317
03/26/22 10:59:31.183 | 544.6994 | 1367.2155 | 53.4788 | 43.9446 | 9.5341 | 30.8441 | 51.0296 | 0 | 1788.5597 | 93.9767 | 85.4297 | 8.5471 | 24.9109 | 70.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.003 | 462.74 | 459.76 | 463.19 | 410.07 | 439.44 | 417.89 | 313.75 | 0.57601 | -0.021659 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6563478.8413 | 7635691.632 | 7635691.632 | 62.429 | 62.1333 | 1.0018 | 0.99791 | 684319.4625 | 891900.1727 | 461.8967 | 0.46259 | 0 | 0 | 30.8441 | 24.9109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017865 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 557.9314 | 1368.1069 | 53.9836 | 44.2239 | 31.0844 | 1787.2701 | 84.0271 | 24.618 | 461.465 | 0.0060785 | 60.0112 | 0.56238 | 0.46411 | 92.7136 | 2.1133 | 0.26695 | 0.1321 | 5.0486 | 0.94164 | 0.28146 | 0 | 100 | 576.4 | 317 | 115.4 | 108.2 | 100.24 | 307.9 | 4 | 95.66 | 42.49 | 4 | 37.7 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.78 | 0 | 38.38 | 55 | 55 | 110 | 92.9 | 89.5 | 0 | 100.24 | 2.42 | 94.83 | 43.16 | 115.4 | 12.55 | 108.2 | 110 | 0 | 15706 | 83.15 | 116.73 | 220.95 | 214.92 | 220.15 | 0 | 36.09 | 50.29 | 14944 | 95.65 | 42.49 | 37.7 | 1.16 | 42.49 | 0 | 608 | 429.9 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 314.1 | 0 | 307.9 | 100.24 | 15703 | 15706 | 317
03/26/22 10:59:36.184 | 544.7381 | 1367.3291 | 53.4809 | 43.9477 | 9.5332 | 31.1358 | 51.0426 | 0 | 1792.3634 | 93.9858 | 85.4393 | 8.5465 | 24.8373 | 70.1636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0211 | 462.8101 | 459.7601 | 463.1801 | 410.4401 | 439.3901 | 417.6501 | 313.8201 | 0.57609 | -0.22326 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6564215.7455 | 7651907.9046 | 7651907.9046 | 62.429 | 62.1332 | 1.0018 | 0.99791 | 684445.9454 | 893844.3747 | 461.9167 | 0.4669 | 0 | 0 | 31.1358 | 24.8373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017858 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 557.7282 | 1368.0886 | 53.9796 | 44.2235 | 31.0827 | 1787.3197 | 84.0452 | 24.6202 | 461.4705 | 0.0060254 | 60.0113 | 0.56255 | 0.45518 | 92.7296 | 2.1111 | 0.26915 | 0.13296 | 5.0476 | 0.93706 | 0.28041 | 0 | 100 | 577.1 | 318 | 115.4 | 108.2 | 100.31 | 307.6 | 4 | 95.65 | 42.48 | 4 | 37.69 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.73 | 0 | 38.38 | 55 | 55 | 110 | 92.9 | 89.54 | 0 | 100.31 | 2.42 | 94.8 | 43.16 | 115.4 | 12.56 | 108.2 | 110 | 0 | 15706 | 83.15 | 116.75 | 220.95 | 214.92 | 220.15 | 0 | 36.1 | 50.39 | 14949 | 95.65 | 42.48 | 37.69 | 1.17 | 42.48 | 0 | 608 | 428.2 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 313.9 | 0 | 307.6 | 100.37 | 15707 | 15706 | 318
03/26/22 10:59:41.183 | 544.9234 | 1367.809 | 53.4832 | 43.9501 | 9.5331 | 31.5167 | 51.0411 | 0 | 1788.214 | 93.9938 | 85.4475 | 8.5463 | 24.0684 | 70.1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.024 | 462.81 | 459.74 | 463.17 | 410.57 | 439.45 | 417.6 | 313.86 | 0.57597 | 0.060979 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6566783.5539 | 7633062.0424 | 7633062.0424 | 62.429 | 62.1331 | 1.0018 | 0.99791 | 684686.1112 | 891773.8471 | 461.9067 | 0.46907 | 0 | 0 | 31.5167 | 24.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017867 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 557.5231 | 1368.0671 | 53.9756 | 44.2229 | 31.0825 | 1787.2903 | 84.0633 | 24.6179 | 461.476 | 0.006037 | 60.0114 | 0.56273 | 0.45046 | 92.7455 | 2.0939 | 0.27112 | 0.13396 | 5.0268 | 0.93254 | 0.27938 | 0 | 100 | 577.1 | 316 | 115.3 | 108.18 | 100.37 | 307.5 | 4 | 95.6 | 42.49 | 4 | 37.7 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.7 | 0 | 38.38 | 55 | 55 | 109.93 | 92.87 | 89.6 | 0 | 100.37 | 2.42 | 94.79 | 43.16 | 115.33 | 12.57 | 108.18 | 110 | 0 | 15706 | 83.15 | 116.8 | 220.95 | 214.92 | 220.27 | 0 | 36.14 | 50.52 | 14954 | 95.61 | 42.49 | 37.7 | 1.16 | 42.49 | 0 | 608 | 427.6 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.2 | 314.3 | 0 | 308 | 100.38 | 15706 | 15706 | 316
03/26/22 10:59:46.183 | 545.7681 | 1370.1676 | 53.4865 | 43.9528 | 9.5338 | 31.6283 | 51.0205 | 0 | 1781.1434 | 94.0022 | 85.4548 | 8.5474 | 23.8198 | 70.1297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0271 | 462.8201 | 459.7201 | 463.1801 | 410.6901 | 439.5401 | 417.5301 | 313.9001 | 0.57515 | 0.52763 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6576981.5061 | 7607669.7229 | 7607669.7229 | 62.429 | 62.133 | 1.0018 | 0.99791 | 685711.6187 | 888741.0063 | 461.9067 | 0.4734 | 0 | 0 | 31.6283 | 23.8198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017877 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 557.3193 | 1368.0499 | 53.9715 | 44.2222 | 31.0831 | 1787.2707 | 84.0813 | 24.6151 | 461.4813 | 0.0060485 | 60.0115 | 0.56291 | 0.44551 | 92.7612 | 2.0746 | 0.27293 | 0.13502 | 5.0278 | 0.92781 | 0.27842 | 0 | 100 | 577.1 | 316 | 115.45 | 108.18 | 100.37 | 306.9 | 4 | 95.63 | 42.5 | 4 | 37.71 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.78 | 0 | 38.39 | 55 | 55 | 109.95 | 92.87 | 89.54 | 0 | 100.35 | 2.42 | 94.82 | 43.17 | 115.45 | 12.51 | 108.18 | 110 | 0 | 15706 | 83.15 | 116.8 | 220.95 | 214.92 | 220.27 | 0 | 36.2 | 50.64 | 14959 | 95.67 | 42.5 | 37.71 | 1.15 | 42.5 | 0 | 608 | 429.9 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 313.2 | 0 | 306.9 | 100.43 | 15704 | 15706 | 316
03/26/22 10:59:51.182 | 545.6234 | 1369.3935 | 53.4886 | 43.9542 | 9.5343 | 31.5696 | 51.024 | 0 | 1779.1564 | 94.0066 | 85.4584 | 8.5482 | 23.8127 | 70.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.027 | 462.82 | 459.72 | 463.18 | 410.69 | 439.54 | 417.53 | 313.9 | 0.57531 | 0.66313 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6575262.2629 | 7595795.543 | 7595795.543 | 62.429 | 62.133 | 1.0018 | 0.99791 | 685478.9968 | 887255.2599 | 461.9067 | 0.4734 | 0 | 0 | 31.5696 | 23.8127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017885 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 557.1205 | 1368.0438 | 53.9673 | 44.2215 | 31.0873 | 1787.2337 | 84.0993 | 24.6088 | 461.4865 | 0.0060598 | 60.0117 | 0.56308 | 0.44253 | 92.777 | 2.069 | 0.27455 | 0.13611 | 5.0629 | 0.9229 | 0.27749 | 0 | 100 | 577.5 | 315 | 115.48 | 108.18 | 100.43 | 307.4 | 4 | 95.68 | 42.5 | 4 | 37.71 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.85 | 0 | 38.38 | 55 | 55 | 110.03 | 92.91 | 89.6 | 0 | 100.43 | 2.42 | 94.87 | 43.16 | 115.48 | 12.49 | 108.18 | 110 | 0 | 15706 | 83.15 | 116.82 | 220.95 | 214.92 | 220.27 | 0 | 36.27 | 50.73 | 14964 | 95.68 | 42.5 | 37.71 | 1.13 | 42.5 | 0 | 608 | 428.2 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 312.9 | 0 | 306.6 | 100.37 | 15707 | 15706 | 313
03/26/22 10:59:56.183 | 545.2893 | 1368.2425 | 53.4952 | 43.9586 | 9.5365 | 31.1234 | 51.0246 | 0 | 1779.7293 | 94.0186 | 85.4688 | 8.5498 | 24.7305 | 70.0946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.027 | 462.82 | 459.7 | 463.18 | 410.78 | 439.61 | 417.45 | 313.93 | 0.57571 | 0.54198 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6570837.1372 | 7600704.5208 | 7600704.5208 | 62.4289 | 62.1328 | 1.0018 | 0.99791 | 684902.5903 | 887539.4233 | 461.9 | 0.47629 | 0 | 0 | 31.1234 | 24.7305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017883 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 556.9249 | 1368.043 | 53.9631 | 44.2206 | 31.0807 | 1787.2041 | 84.1173 | 24.6139 | 461.4917 | 0.0060709 | 60.0118 | 0.56325 | 0.43966 | 92.7927 | 2.0689 | 0.27595 | 0.13725 | 5.0994 | 0.91784 | 0.27644 | 0 | 100 | 576.8 | 318 | 115.5 | 108.2 | 100.31 | 308.3 | 4 | 95.7 | 42.5 | 4 | 37.71 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.88 | 0 | 38.39 | 55 | 55 | 110.05 | 92.92 | 89.56 | 0 | 100.31 | 2.42 | 94.87 | 43.17 | 115.48 | 12.51 | 108.2 | 110 | 0 | 15706 | 83.17 | 116.85 | 220.95 | 214.92 | 220.27 | 0 | 36.27 | 50.66 | 14969 | 95.68 | 42.5 | 37.71 | 1.13 | 42.5 | 0 | 608 | 426.6 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.8 | 313.6 | 0 | 307.4 | 100.31 | 15705 | 15706 | 316
03/26/22 11:00:01.183 | 545.6483 | 1368.9806 | 53.4989 | 43.9613 | 9.5377 | 31.2797 | 51.0097 | 0 | 1782.3253 | 94.0249 | 85.4751 | 8.5498 | 24.1844 | 70.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.027 | 462.82 | 459.7 | 463.18 | 410.78 | 439.61 | 417.45 | 313.93 | 0.57533 | 0.46297 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6575297.9795 | 7611151.766 | 7611151.766 | 62.4289 | 62.1328 | 1.0018 | 0.99791 | 685271.8675 | 888833.0873 | 461.9 | 0.47629 | 0 | 0 | 31.2797 | 24.1844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017883 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 556.7313 | 1368.0458 | 53.9588 | 44.2198 | 31.0788 | 1787.1856 | 84.1352 | 24.6121 | 461.4969 | 0.0060821 | 60.0119 | 0.56342 | 0.43647 | 92.8084 | 2.0698 | 0.27716 | 0.13839 | 5.111 | 0.91258 | 0.27529 | 0 | 100 | 577.3 | 316 | 115.53 | 108.22 | 100.4 | 306.9 | 4 | 95.71 | 42.5 | 4 | 37.71 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.39 | 55 | 55 | 110.1 | 92.95 | 89.63 | 0 | 100.4 | 2.42 | 94.89 | 43.17 | 115.55 | 12.49 | 108.22 | 110 | 0 | 15706 | 83.17 | 116.87 | 220.95 | 214.92 | 220.27 | 0 | 36.29 | 50.71 | 14973 | 95.72 | 42.5 | 37.71 | 1.13 | 42.5 | 0 | 608 | 429 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 313.2 | 0 | 306.9 | 100.4 | 15705 | 15706 | 316
03/26/22 11:00:06.183 | 546.6396 | 1371.2824 | 53.5042 | 43.9653 | 9.539 | 30.7283 | 51.0139 | 0 | 1787.5121 | 94.0338 | 85.4845 | 8.5494 | 24.9192 | 70.1178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0191 | 462.7801 | 459.6201 | 463.1701 | 410.9701 | 439.8801 | 417.3501 | 314.0201 | 0.57446 | 0.3198 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6586753.5801 | 7633747.8966 | 7633747.8966 | 62.4289 | 62.1327 | 1.0018 | 0.99791 | 686423.855 | 891418.311 | 461.8568 | 0.48428 | 0 | 0 | 30.7283 | 24.9192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017872 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 556.5464 | 1368.0684 | 53.9545 | 44.2189 | 31.0754 | 1787.1717 | 84.1531 | 24.6133 | 461.5021 | 0.0060933 | 60.012 | 0.56358 | 0.43437 | 92.8241 | 2.0827 | 0.2782 | 0.13953 | 5.114 | 0.90709 | 0.27385 | 0 | 100 | 577.4 | 317 | 115.53 | 108.24 | 100.42 | 307.6 | 4 | 95.71 | 42.51 | 4 | 37.73 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.4 | 55 | 55 | 110.13 | 92.96 | 89.6 | 0 | 100.42 | 2.42 | 94.89 | 43.18 | 115.55 | 12.51 | 108.24 | 110 | 0 | 15706 | 83.17 | 116.87 | 220.95 | 214.92 | 220.27 | 0 | 36.31 | 50.68 | 14978 | 95.72 | 42.51 | 37.73 | 1.12 | 42.51 | 0 | 608 | 428.2 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 312.2 | 0 | 306 | 100.4 | 15706 | 15706 | 316
03/26/22 11:00:11.182 | 546.0246 | 1369.6257 | 53.5083 | 43.9685 | 9.5398 | 31.0873 | 51.0238 | 0 | 1787.0063 | 94.0409 | 85.4909 | 8.55 | 24.5321 | 70.1149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.007 | 462.74 | 459.57 | 463.14 | 410.98 | 439.99 | 417.33 | 314.02 | 0.5751 | 0.254 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6579657.1249 | 7631727.9537 | 7631727.9537 | 62.4289 | 62.1326 | 1.0018 | 0.99791 | 685594.4079 | 891165.1366 | 461.8167 | 0.48648 | 0 | 0 | 31.0873 | 24.5321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017878 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 556.3646 | 1368.0925 | 53.9501 | 44.2179 | 31.0723 | 1787.1874 | 84.171 | 24.6152 | 461.507 | 0.0061038 | 60.012 | 0.56373 | 0.43083 | 92.8397 | 2.0861 | 0.27898 | 0.1407 | 5.1121 | 0.90151 | 0.27227 | 0 | 100 | 576.6 | 316 | 115.48 | 108.24 | 100.28 | 305.9 | 4 | 95.68 | 42.51 | 4 | 37.73 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.39 | 55 | 55 | 110.1 | 92.95 | 89.65 | 0 | 100.35 | 2.42 | 94.89 | 43.17 | 115.48 | 12.55 | 108.24 | 110 | 0 | 15706 | 83.17 | 116.87 | 221.07 | 215.03 | 220.27 | 0 | 36.2 | 50.47 | 14983 | 95.68 | 42.51 | 37.73 | 1.12 | 42.51 | 0 | 607 | 426.2 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.2 | 312.1 | 0 | 305.9 | 100.38 | 15705 | 15706 | 318
03/26/22 11:00:16.182 | 546.3939 | 1370.4773 | 53.5129 | 43.9726 | 9.5403 | 31.6568 | 51.0407 | 0 | 1785.8554 | 94.0493 | 85.498 | 8.5513 | 23.6172 | 70.1066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 462.7401 | 459.5701 | 463.1401 | 410.9801 | 439.9901 | 417.3301 | 314.0201 | 0.57471 | 0.38184 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6584606.7378 | 7626908.6606 | 7626908.6606 | 62.4289 | 62.1325 | 1.0018 | 0.99791 | 686020.4703 | 890590.1225 | 461.8167 | 0.48648 | 0 | 0 | 31.6568 | 23.6172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017877 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 556.1792 | 1368.1089 | 53.9457 | 44.2168 | 31.0728 | 1787.1993 | 84.1888 | 24.6108 | 461.5115 | 0.0061136 | 60.012 | 0.5639 | 0.42731 | 92.8553 | 2.0932 | 0.27957 | 0.14183 | 5.1065 | 0.89578 | 0.27057 | 0 | 100 | 577.1 | 315 | 115.5 | 108.24 | 100.37 | 305.7 | 4 | 95.7 | 42.51 | 4 | 37.73 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.88 | 0 | 38.39 | 55 | 55 | 110.05 | 92.92 | 89.65 | 0 | 100.37 | 2.42 | 94.88 | 43.17 | 115.5 | 12.54 | 108.24 | 110 | 0 | 15706 | 83.19 | 116.89 | 221.07 | 215.03 | 220.27 | 0 | 36.1 | 50.39 | 14988 | 95.7 | 42.51 | 37.73 | 1.12 | 42.51 | 0 | 607 | 430.2 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 311.9 | 0 | 305.7 | 100.37 | 15706 | 15706 | 315
03/26/22 11:00:21.183 | 544.8389 | 1366.5549 | 53.5186 | 43.9782 | 9.5405 | 31.76 | 51.0258 | 0 | 1782.7588 | 94.0591 | 85.5071 | 8.5521 | 23.6152 | 70.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0011 | 462.7001 | 459.5301 | 463.1201 | 410.9701 | 440.0701 | 417.3501 | 314.0401 | 0.57639 | 0.30402 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6565958.24 | 7614322.5714 | 7614322.5714 | 62.4289 | 62.1324 | 1.0018 | 0.99791 | 684056.8081 | 889044.5365 | 461.7834 | 0.48796 | 0 | 0 | 31.76 | 23.6152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017889 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 555.9875 | 1368.1077 | 53.9412 | 44.2157 | 31.079 | 1787.2112 | 84.2066 | 24.5978 | 461.5159 | 0.006123 | 60.0119 | 0.56407 | 0.42292 | 92.8708 | 2.0927 | 0.27998 | 0.14292 | 5.0981 | 0.88985 | 0.26863 | 0 | 100 | 577.1 | 317 | 115.53 | 108.24 | 100.37 | 306.6 | 4 | 95.71 | 42.53 | 4 | 37.73 | 43.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.4 | 55 | 55 | 110.1 | 92.95 | 89.62 | 0 | 100.43 | 2.42 | 94.89 | 43.18 | 115.55 | 12.51 | 108.24 | 110 | 0 | 15706 | 83.19 | 116.92 | 221.07 | 215.03 | 220.27 | 0 | 36.14 | 50.57 | 14993 | 95.72 | 42.51 | 37.73 | 1.12 | 42.51 | 0 | 608 | 429.4 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 311.4 | 0 | 305.2 | 100.35 | 15706 | 15706 | 315
03/26/22 11:00:26.182 | 544.8389 | 1366.7252 | 53.52 | 43.9794 | 9.5405 | 31.429 | 51.0234 | 0 | 1782.7795 | 94.0612 | 85.509 | 8.5522 | 24.1872 | 70.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0011 | 462.7001 | 459.5301 | 463.1201 | 410.9701 | 440.0701 | 417.3501 | 314.0401 | 0.57639 | 0.30402 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6565958.24 | 7614322.5714 | 7614322.5714 | 62.4289 | 62.1324 | 1.0018 | 0.99791 | 684056.8081 | 889044.5365 | 461.7834 | 0.48796 | 0 | 0 | 31.429 | 24.1872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.01788 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 555.7928 | 1368.0989 | 53.9367 | 44.2145 | 31.0834 | 1787.1865 | 84.2243 | 24.5909 | 461.5202 | 0.0061323 | 60.0118 | 0.56424 | 0.41993 | 92.8863 | 2.0952 | 0.28017 | 0.14399 | 5.1088 | 0.88382 | 0.26664 | 0 | 100 | 577.5 | 317 | 115.55 | 108.26 | 100.4 | 307.3 | 4 | 95.72 | 42.53 | 4 | 37.74 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.93 | 0 | 38.4 | 55 | 55 | 110.15 | 92.98 | 89.65 | 0 | 100.4 | 2.42 | 94.92 | 43.18 | 115.55 | 12.53 | 108.26 | 110 | 0 | 15706 | 83.19 | 116.94 | 221.07 | 215.03 | 220.27 | 0 | 36.25 | 50.74 | 14998 | 95.72 | 42.53 | 37.74 | 1.12 | 42.53 | 0 | 608 | 428.3 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 313.6 | 0 | 307.3 | 100.43 | 15704 | 15706 | 317
03/26/22 11:00:31.182 | 544.0251 | 1364.4441 | 53.5262 | 43.9852 | 9.541 | 30.7506 | 51.0325 | 0 | 1789.2617 | 94.0711 | 85.5193 | 8.5517 | 24.8702 | 70.0835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.001 | 462.7 | 459.53 | 463.12 | 410.97 | 440.07 | 417.35 | 314.04 | 0.57725 | -0.21518 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6555264.2939 | 7643241.9809 | 7643241.9809 | 62.4289 | 62.1323 | 1.0018 | 0.99791 | 682999.8585 | 892285.6227 | 461.7833 | 0.48796 | 0 | 0 | 30.7506 | 24.8702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017876 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 555.5952 | 1368.0801 | 53.9321 | 44.2133 | 31.0833 | 1787.1881 | 84.242 | 24.5891 | 461.5245 | 0.0061416 | 60.0117 | 0.56442 | 0.41475 | 92.9017 | 2.1128 | 0.28015 | 0.145 | 5.1094 | 0.87769 | 0.26456 | 0 | 100 | 577.1 | 318 | 115.5 | 108.28 | 100.47 | 306.1 | 4 | 95.7 | 42.53 | 4 | 37.74 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.88 | 0 | 38.4 | 55 | 55 | 110.1 | 92.95 | 89.71 | 0 | 100.47 | 2.42 | 94.88 | 43.18 | 115.48 | 12.59 | 108.28 | 110 | 0 | 15706 | 83.19 | 116.94 | 221.07 | 215.03 | 220.27 | 0 | 36.33 | 50.88 | 15004 | 95.68 | 42.53 | 37.74 | 1.12 | 42.53 | 0 | 608 | 427.5 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 311.2 | 0 | 305 | 100.4 | 15707 | 15706 | 314
03/26/22 11:00:36.183 | 544.8721 | 1366.493 | 53.5298 | 43.9883 | 9.5415 | 31.1312 | 51.0128 | 0 | 1789.5713 | 94.0772 | 85.5262 | 8.551 | 24.2159 | 70.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0021 | 462.6901 | 459.5401 | 463.1301 | 410.9401 | 440.1101 | 417.3301 | 314.1001 | 0.57647 | -0.072639 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6565803.2274 | 7643106.3318 | 7643106.3318 | 62.4289 | 62.1322 | 1.0018 | 0.99791 | 684025.3149 | 892439.0112 | 461.7867 | 0.48652 | 0 | 0 | 31.1312 | 24.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017875 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 555.3986 | 1368.0639 | 53.9275 | 44.212 | 31.0869 | 1787.1639 | 84.2596 | 24.5801 | 461.5286 | 0.0061505 | 60.0117 | 0.56459 | 0.41142 | 92.9171 | 2.1137 | 0.27986 | 0.14597 | 5.0876 | 0.8715 | 0.2628 | 0 | 100 | 577.3 | 316 | 115.48 | 108.28 | 100.4 | 305.4 | 4 | 95.67 | 42.53 | 4 | 37.74 | 43.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.43 | 55 | 55 | 110.1 | 92.95 | 89.69 | 0 | 100.45 | 2.42 | 94.88 | 43.2 | 115.48 | 12.59 | 108.28 | 110 | 0 | 15706 | 83.19 | 116.97 | 221.07 | 215.03 | 220.39 | 0 | 36.45 | 51.02 | 15009 | 95.68 | 42.54 | 37.75 | 1.11 | 42.54 | 0 | 608 | 430 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 314.1 | 0 | 307.9 | 100.43 | 15707 | 15706 | 317
03/26/22 11:00:41.182 | 545.2175 | 1366.8543 | 53.5335 | 43.9911 | 9.5423 | 30.3779 | 51.0052 | 0 | 1791.0319 | 94.0833 | 85.5328 | 8.5505 | 24.7899 | 70.0773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.003 | 462.68 | 459.55 | 463.13 | 410.92 | 440.14 | 417.33 | 314.11 | 0.57612 | -0.090687 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6569403.2371 | 7648123.3667 | 7648123.3667 | 62.4288 | 62.1321 | 1.0018 | 0.9979 | 684412.7008 | 892999.2876 | 461.7867 | 0.48435 | 0 | 0 | 30.3779 | 24.7899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017866 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 555.2015 | 1368.0449 | 53.9228 | 44.2106 | 31.0828 | 1787.1567 | 84.2771 | 24.581 | 461.5325 | 0.0061588 | 60.0116 | 0.56477 | 0.40711 | 92.9324 | 2.109 | 0.27932 | 0.14688 | 5.0811 | 0.86519 | 0.26149 | 0 | 100 | 577.4 | 316 | 115.58 | 108.28 | 100.4 | 306.9 | 4 | 95.73 | 42.54 | 4 | 37.75 | 43.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.93 | 0 | 38.43 | 55 | 55 | 110.13 | 92.96 | 89.63 | 0 | 100.47 | 2.42 | 94.9 | 43.21 | 115.58 | 12.54 | 108.28 | 110 | 0 | 15706 | 83.19 | 116.99 | 221.07 | 215.03 | 220.39 | 0 | 36.6 | 51.12 | 15013 | 95.73 | 42.54 | 37.75 | 1.13 | 42.54 | 0 | 608 | 425.4 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.4 | 313.1 | 0 | 306.9 | 100.42 | 15706 | 15706 | 316
03/26/22 11:00:46.182 | 544.9137 | 1366.1988 | 53.5394 | 43.9951 | 9.5443 | 29.1589 | 51.0329 | 0 | 1794.6394 | 94.092 | 85.5415 | 8.5505 | 26.4376 | 70.1145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 462.6901 | 459.5501 | 463.1501 | 410.9201 | 440.2001 | 417.3401 | 314.1501 | 0.57651 | -0.39689 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6564564.6745 | 7666857.7162 | 7666857.7162 | 62.4288 | 62.132 | 1.0018 | 0.9979 | 683877.6619 | 894964.1453 | 461.7968 | 0.48651 | 0 | 0 | 29.1589 | 26.4376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017854 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 555.0018 | 1368.0207 | 53.9181 | 44.2092 | 31.0704 | 1787.1836 | 84.2946 | 24.5957 | 461.5362 | 0.0061669 | 60.0116 | 0.56494 | 0.40016 | 92.9476 | 2.1051 | 0.27857 | 0.14773 | 5.1079 | 0.85865 | 0.26039 | 0 | 100 | 577.5 | 315 | 115.43 | 108.28 | 100.43 | 304.9 | 4 | 95.66 | 42.54 | 4 | 37.75 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.83 | 0 | 38.43 | 55 | 55 | 110.05 | 92.92 | 89.69 | 0 | 100.47 | 2.42 | 94.87 | 43.21 | 115.43 | 12.62 | 108.28 | 110 | 0 | 15706 | 83.19 | 117.01 | 221.07 | 215.03 | 220.39 | 0 | 36.58 | 50.93 | 15018 | 95.66 | 42.54 | 37.75 | 1.15 | 42.54 | 0 | 608 | 429.1 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 311.1 | 0 | 304.9 | 100.43 | 15705 | 15706 | 315
03/26/22 11:00:51.182 | 545.6112 | 1367.8245 | 53.5442 | 43.9978 | 9.5465 | 30.0666 | 51.0217 | 0 | 1798.1128 | 94.0975 | 85.5457 | 8.5517 | 25.5387 | 70.0963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.01 | 462.74 | 459.6 | 463.2 | 410.96 | 440.27 | 417.36 | 314.22 | 0.5759 | -0.44064 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6573563.3751 | 7679490.4138 | 7679490.4138 | 62.4288 | 62.132 | 1.0018 | 0.9979 | 684631.8496 | 896422.9136 | 461.8467 | 0.48645 | 0 | 0 | 30.0666 | 25.5387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017856 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 554.8137 | 1368.0217 | 53.9133 | 44.2077 | 31.0639 | 1787.2466 | 84.312 | 24.6014 | 461.5401 | 0.0061753 | 60.0116 | 0.56511 | 0.39318 | 92.9628 | 2.105 | 0.27756 | 0.14851 | 5.1723 | 0.85201 | 0.25974 | 0 | 100 | 578.7 | 316 | 115.4 | 108.26 | 100.64 | 307.6 | 4 | 95.65 | 42.55 | 4 | 37.76 | 43.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.8 | 0 | 38.44 | 55 | 55 | 110 | 92.9 | 89.65 | 0 | 100.64 | 2.42 | 94.84 | 43.22 | 115.4 | 12.61 | 108.26 | 110 | 0 | 15706 | 83.19 | 117.01 | 221.07 | 215.03 | 220.39 | 0 | 36.53 | 50.82 | 15023 | 95.65 | 42.55 | 37.76 | 1.16 | 42.55 | 0 | 608 | 425.2 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.8 | 311.9 | 0 | 305.7 | 100.66 | 15706 | 15706 | 317
03/26/22 11:00:56.182 | 545.4404 | 1366.3949 | 53.5555 | 44.0033 | 9.5522 | 29.5818 | 51.0101 | 0 | 1792.6421 | 94.1061 | 85.5493 | 8.5568 | 25.3392 | 70.1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.017 | 462.79 | 459.63 | 463.24 | 411.04 | 440.33 | 417.43 | 314.31 | 0.57625 | -0.24733 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6571260.1642 | 7662659.0898 | 7662659.0898 | 62.4288 | 62.1319 | 1.0018 | 0.9979 | 683975.1191 | 893966.9347 | 461.8867 | 0.48858 | 0 | 0 | 29.5818 | 25.3392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017854 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 554.6282 | 1368.0155 | 53.9085 | 44.2062 | 31.0576 | 1787.3011 | 84.3293 | 24.6044 | 461.5442 | 0.006184 | 60.0117 | 0.56528 | 0.38637 | 92.9779 | 2.1074 | 0.27636 | 0.14921 | 5.1979 | 0.84522 | 0.25945 | 0 | 100 | 578.3 | 315 | 115.48 | 108.24 | 100.61 | 307.4 | 4 | 95.68 | 42.56 | 4 | 37.78 | 43.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.83 | 0 | 38.44 | 55 | 55 | 110.05 | 92.92 | 89.65 | 0 | 100.61 | 2.42 | 94.85 | 43.22 | 115.5 | 12.54 | 108.24 | 110 | 0 | 15706 | 83.19 | 117.01 | 221.19 | 215.14 | 220.39 | 0 | 36.52 | 50.74 | 15028 | 95.7 | 42.56 | 37.76 | 1.15 | 42.56 | 0 | 608 | 429.3 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 313.7 | 0 | 307.4 | 100.57 | 15705 | 15706 | 315
03/26/22 11:01:01.182 | 545.6405 | 1366.4672 | 53.5613 | 44.006 | 9.5552 | 29.3125 | 51.0089 | 0 | 1793.184 | 94.1085 | 85.5491 | 8.5594 | 25.962 | 70.1136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0171 | 462.7901 | 459.6301 | 463.2401 | 411.0401 | 440.3301 | 417.4301 | 314.3101 | 0.57604 | -0.28921 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6573425.8032 | 7668040.0681 | 7668040.0681 | 62.4288 | 62.1319 | 1.0018 | 0.9979 | 684011.0418 | 894237.2082 | 461.8868 | 0.48858 | 0 | 0 | 29.3125 | 25.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017847 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 554.4412 | 1367.9872 | 53.9038 | 44.2046 | 31.0446 | 1787.3495 | 84.3464 | 24.6163 | 461.5482 | 0.0061927 | 60.0117 | 0.56545 | 0.3781 | 92.993 | 2.0937 | 0.27504 | 0.1498 | 5.212 | 0.83851 | 0.25909 | 0 | 100 | 578.2 | 313 | 115.43 | 108.24 | 100.47 | 305.3 | 4 | 95.66 | 42.54 | 4 | 37.75 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.78 | 0 | 38.44 | 55 | 55 | 110.03 | 92.91 | 89.6 | 0 | 100.47 | 2.42 | 94.84 | 43.22 | 115.4 | 12.6 | 108.24 | 110 | 0 | 15706 | 83.19 | 117.01 | 221.19 | 215.14 | 220.39 | 0 | 36.43 | 50.58 | 15034 | 95.63 | 42.54 | 37.75 | 1.17 | 42.54 | 0 | 608 | 428.1 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.2 | 313.5 | 0 | 307.2 | 100.56 | 15704 | 15706 | 316
03/26/22 11:01:06.182 | 546.4156 | 1367.9174 | 53.5713 | 44.0113 | 9.56 | 30.0217 | 51.0147 | 0 | 1790.9132 | 94.1105 | 85.5466 | 8.5638 | 25.1741 | 70.1211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.025 | 462.84 | 459.65 | 463.29 | 411.13 | 440.3 | 417.45 | 314.36 | 0.57531 | -0.10339 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6583371.1431 | 7663931.628 | 7663931.628 | 62.4288 | 62.1319 | 1.0018 | 0.9979 | 684661.6527 | 893421.6511 | 461.9267 | 0.49286 | 0 | 0 | 30.0217 | 25.1741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017851 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 554.2746 | 1367.9923 | 53.8992 | 44.203 | 31.0353 | 1787.4001 | 84.3634 | 24.6238 | 461.5524 | 0.0062016 | 60.0118 | 0.56561 | 0.37201 | 93.008 | 2.0921 | 0.27365 | 0.1503 | 5.2082 | 0.83171 | 0.25919 | 0 | 100 | 577.2 | 315 | 115.4 | 108.24 | 100.38 | 306.1 | 4 | 95.65 | 42.54 | 4 | 37.75 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.8 | 0 | 38.43 | 55 | 55 | 110.03 | 92.91 | 89.62 | 0 | 100.47 | 2.42 | 94.84 | 43.21 | 115.4 | 12.59 | 108.24 | 110 | 0 | 15706 | 83.21 | 117.04 | 221.19 | 215.14 | 220.39 | 0 | 36.41 | 50.6 | 15039 | 95.65 | 42.54 | 37.75 | 1.19 | 42.54 | 0 | 608 | 427.5 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 313.7 | 0 | 307.5 | 100.47 | 15706 | 15706 | 316
03/26/22 11:01:11.182 | 545.911 | 1366.0749 | 53.5788 | 44.016 | 9.5627 | 30.4025 | 51.013 | 0 | 1786.5986 | 94.1101 | 85.5432 | 8.5668 | 24.2621 | 70.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0201 | 462.8301 | 459.6301 | 463.2801 | 411.1401 | 440.3001 | 417.4501 | 314.3501 | 0.57583 | 0.074597 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6577621.5903 | 7644557.2953 | 7644557.2953 | 62.4287 | 62.1319 | 1.0018 | 0.9979 | 683813.9367 | 890954.0178 | 461.9134 | 0.49432 | 0 | 0 | 30.4025 | 24.2621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017855 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 554.1199 | 1368.0062 | 53.8947 | 44.2013 | 31.0295 | 1787.4415 | 84.3801 | 24.6254 | 461.5566 | 0.0062108 | 60.0119 | 0.56576 | 0.36729 | 93.0228 | 2.0813 | 0.27227 | 0.15073 | 5.1848 | 0.82493 | 0.25898 | 0 | 100 | 577.7 | 315 | 115.48 | 108.24 | 100.47 | 306 | 4 | 95.68 | 42.54 | 4 | 37.75 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.83 | 0 | 38.43 | 55 | 55 | 110.05 | 92.92 | 89.56 | 0 | 100.4 | 2.42 | 94.85 | 43.21 | 115.48 | 12.55 | 108.24 | 110 | 0 | 15706 | 83.21 | 117.04 | 221.19 | 215.14 | 220.51 | 0 | 36.43 | 50.62 | 15043 | 95.68 | 42.54 | 37.75 | 1.19 | 42.54 | 0 | 608 | 429.1 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 314.4 | 0 | 308.2 | 100.49 | 15706 | 15706 | 317
03/26/22 11:01:16.182 | 544.9403 | 1363.5976 | 53.5852 | 44.0211 | 9.5641 | 30.1816 | 51.0025 | 0 | 1782.124 | 94.1081 | 85.539 | 8.5691 | 24.6561 | 70.1306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0131 | 462.8301 | 459.6001 | 463.2501 | 411.1401 | 440.2701 | 417.4101 | 314.3201 | 0.5768 | 0.050367 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6565963.3721 | 7634723.2208 | 7634723.2208 | 62.4287 | 62.1319 | 1.0018 | 0.9979 | 682511.663 | 889623.8867 | 461.8934 | 0.49651 | 0 | 0 | 30.1816 | 24.6561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017867 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 553.9575 | 1367.9901 | 53.8904 | 44.1997 | 31.0262 | 1787.4507 | 84.3967 | 24.6228 | 461.561 | 0.0062201 | 60.012 | 0.56592 | 0.36238 | 93.0376 | 2.1051 | 0.27086 | 0.15108 | 5.177 | 0.81801 | 0.25838 | 0 | 100 | 577.5 | 315 | 115.48 | 108.26 | 100.43 | 306.9 | 4 | 95.68 | 42.53 | 4 | 37.74 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.41 | 55 | 55 | 110.08 | 92.94 | 89.58 | 0 | 100.43 | 2.42 | 94.89 | 43.2 | 115.48 | 12.57 | 108.26 | 110 | 0 | 15706 | 83.21 | 117.06 | 221.19 | 215.14 | 220.51 | 0 | 36.38 | 50.5 | 15048 | 95.68 | 42.53 | 37.74 | 1.22 | 42.53 | 0 | 608 | 430.4 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 313.2 | 0 | 306.9 | 100.43 | 15705 | 15706 | 315
03/26/22 11:01:21.182 | 545.616 | 1365.1459 | 53.5867 | 44.0226 | 9.5641 | 30.2642 | 50.9953 | 0 | 1783.1872 | 94.1073 | 85.5379 | 8.5694 | 24.8525 | 70.1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.013 | 462.83 | 459.6 | 463.25 | 411.14 | 440.27 | 417.41 | 314.32 | 0.57608 | 0.17708 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6573942.3451 | 7632918.2274 | 7632918.2274 | 62.4287 | 62.132 | 1.0018 | 0.9979 | 683348.561 | 889253.5763 | 461.8933 | 0.49651 | 0 | 0 | 30.2642 | 24.8525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017861 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 553.8042 | 1367.9673 | 53.8862 | 44.198 | 31.0239 | 1787.4021 | 84.4129 | 24.6189 | 461.5654 | 0.0062297 | 60.012 | 0.56607 | 0.36031 | 93.0522 | 2.1136 | 0.26969 | 0.15138 | 5.1758 | 0.81153 | 0.25714 | 0 | 100 | 577.2 | 315 | 115.48 | 108.28 | 100.38 | 304.4 | 4 | 95.68 | 42.53 | 4 | 37.74 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.93 | 0 | 38.41 | 55 | 55 | 110.13 | 92.96 | 89.52 | 0 | 100.37 | 2.42 | 94.9 | 43.2 | 115.48 | 12.6 | 108.28 | 110 | 0 | 15706 | 83.21 | 117.06 | 221.19 | 215.14 | 220.51 | 0 | 36.32 | 50.46 | 15053 | 95.67 | 42.53 | 37.74 | 1.28 | 42.53 | 0 | 608 | 426.1 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.2 | 310.6 | 0 | 304.4 | 100.38 | 15704 | 15706 | 315
03/26/22 11:01:26.182 | 546.7158 | 1367.9329 | 53.5894 | 44.0255 | 9.5639 | 30.6651 | 51.0052 | 0 | 1784.8077 | 94.1054 | 85.5359 | 8.5695 | 24.4842 | 70.0728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.01 | 462.82 | 459.59 | 463.22 | 411.16 | 440.2 | 417.42 | 314.3 | 0.57489 | 0.26839 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6587546.215 | 7639518.7221 | 7639518.7221 | 62.4287 | 62.132 | 1.0018 | 0.9979 | 684743.5032 | 890062.0043 | 461.8767 | 0.49508 | 0 | 0 | 30.6651 | 24.4842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017859 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 553.6661 | 1367.9646 | 53.8821 | 44.1964 | 31.0226 | 1787.342 | 84.4288 | 24.6154 | 461.57 | 0.0062395 | 60.012 | 0.56621 | 0.36013 | 93.0666 | 2.1133 | 0.26867 | 0.15165 | 5.1425 | 0.80518 | 0.25537 | 0 | 100 | 577.7 | 315 | 115.43 | 108.29 | 100.47 | 306.3 | 4 | 95.66 | 42.53 | 4 | 37.74 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.88 | 0 | 38.41 | 55 | 55 | 110.1 | 92.95 | 89.58 | 0 | 100.47 | 2.42 | 94.88 | 43.2 | 115.43 | 12.64 | 108.29 | 110 | 0 | 15706 | 83.21 | 117.06 | 221.19 | 215.14 | 220.51 | 0 | 36.29 | 50.46 | 15058 | 95.66 | 42.53 | 37.74 | 1.34 | 42.53 | 0 | 607 | 429 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 312.7 | 0 | 306.5 | 100.47 | 15704 | 15706 | 315
03/26/22 11:01:31.182 | 546.0685 | 1366.4001 | 53.5931 | 44.0298 | 9.5633 | 30.9065 | 51.0172 | 0 | 1787.125 | 94.1029 | 85.5327 | 8.5702 | 24.2752 | 70.0806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.002 | 462.77 | 459.5 | 463.17 | 411.17 | 440.18 | 417.3 | 314.25 | 0.57548 | 0.033606 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6579960.5485 | 7649825.1835 | 7649825.1835 | 62.4287 | 62.132 | 1.0018 | 0.9979 | 683976.0668 | 891218.1008 | 461.8134 | 0.50092 | 0 | 0 | 30.9065 | 24.2752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017861 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 553.5297 | 1367.9524 | 53.8783 | 44.1948 | 31.0222 | 1787.3111 | 84.4445 | 24.6135 | 461.5745 | 0.0062493 | 60.012 | 0.56635 | 0.35774 | 93.0809 | 2.1154 | 0.26778 | 0.1519 | 5.1224 | 0.79897 | 0.25351 | 0 | 100 | 577.9 | 317 | 115.53 | 108.29 | 100.5 | 308.4 | 4 | 95.7 | 42.55 | 4 | 37.76 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.44 | 55 | 55 | 110.1 | 92.95 | 89.52 | 0 | 100.47 | 2.42 | 94.89 | 43.22 | 115.53 | 12.59 | 108.29 | 110 | 0 | 15706 | 83.21 | 117.06 | 221.19 | 215.25 | 220.51 | 0 | 36.3 | 50.59 | 15063 | 95.71 | 42.55 | 37.76 | 1.32 | 42.55 | 0 | 607 | 430.5 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 313.3 | 0 | 307 | 100.52 | 15706 | 15706 | 317
03/26/22 11:01:36.182 | 545.9594 | 1366.1317 | 53.5946 | 44.0313 | 9.5632 | 31.2186 | 51.012 | 0 | 1785.8244 | 94.1021 | 85.5311 | 8.571 | 24.1228 | 70.0666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.002 | 462.77 | 459.5 | 463.17 | 411.17 | 440.18 | 417.3 | 314.25 | 0.57559 | 0.08315 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6578920.1786 | 7644826.1754 | 7644826.1754 | 62.4287 | 62.132 | 1.0018 | 0.9979 | 683841.6711 | 890569.7622 | 461.8134 | 0.50092 | 0 | 0 | 31.2186 | 24.1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017871 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 553.3978 | 1367.9246 | 53.8746 | 44.1933 | 31.0237 | 1787.2921 | 84.4598 | 24.6119 | 461.5789 | 0.0062586 | 60.012 | 0.56649 | 0.35331 | 93.095 | 2.1061 | 0.26716 | 0.15216 | 5.1215 | 0.79319 | 0.25082 | 0 | 100 | 578.2 | 315 | 115.6 | 108.29 | 100.56 | 307.7 | 4 | 95.73 | 42.56 | 4 | 37.78 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.45 | 55 | 55 | 110.13 | 92.96 | 89.56 | 0 | 100.59 | 2.42 | 94.89 | 43.23 | 115.58 | 12.55 | 108.29 | 110 | 0 | 15706 | 83.21 | 117.06 | 221.31 | 215.25 | 220.51 | 0 | 36.34 | 50.64 | 15068 | 95.75 | 42.56 | 37.78 | 1.27 | 42.56 | 0 | 607 | 430.7 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 313.6 | 0 | 307.4 | 100.57 | 15707 | 15706 | 317
03/26/22 11:01:41.181 | 547.5128 | 1370.178 | 53.5966 | 44.0344 | 9.5621 | 30.2953 | 51.0275 | 0 | 1783.9149 | 94.1002 | 85.5277 | 8.5726 | 25.5556 | 70.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9941 | 462.7301 | 459.4301 | 463.1201 | 411.2601 | 440.2801 | 417.2901 | 314.2801 | 0.57401 | 0.38502 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6596829.4363 | 7639657.7532 | 7639657.7532 | 62.4287 | 62.1321 | 1.0018 | 0.9979 | 685867.0019 | 889617.9955 | 461.7601 | 0.50459 | 0 | 0 | 30.2953 | 25.5556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.01786 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 553.2748 | 1367.9119 | 53.8712 | 44.1918 | 31.0211 | 1787.2501 | 84.4749 | 24.6154 | 461.5831 | 0.0062678 | 60.0119 | 0.56662 | 0.35056 | 93.1089 | 2.1031 | 0.26668 | 0.15243 | 5.1305 | 0.78758 | 0.24759 | 0 | 100 | 578.6 | 316 | 115.58 | 108.29 | 100.63 | 306.6 | 4 | 95.73 | 42.56 | 4 | 37.78 | 43.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.95 | 0 | 38.45 | 55 | 55 | 110.15 | 92.98 | 89.6 | 0 | 100.61 | 2.42 | 94.92 | 43.23 | 115.55 | 12.57 | 108.29 | 110 | 0 | 15706 | 83.23 | 117.06 | 221.31 | 215.25 | 220.63 | 0 | 36.29 | 50.53 | 15073 | 95.72 | 42.56 | 37.78 | 1.23 | 42.56 | 0 | 607 | 428.5 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 311.8 | 0 | 305.6 | 100.49 | 15707 | 15706 | 314
03/26/22 11:01:46.181 | 547.7266 | 1370.725 | 53.5964 | 44.0357 | 9.5607 | 30.1208 | 51.0372 | 0 | 1786.8205 | 94.1001 | 85.5268 | 8.5733 | 25.7448 | 70.1863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9941 | 462.7301 | 459.4301 | 463.1201 | 411.2601 | 440.2801 | 417.2901 | 314.2801 | 0.57379 | 0.27841 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6599173.1033 | 7650211.6028 | 7650211.6028 | 62.4287 | 62.1321 | 1.0018 | 0.9979 | 686202.8491 | 890758.2358 | 461.7601 | 0.50459 | 0 | 0 | 30.1208 | 25.7448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017861 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 553.1742 | 1367.9401 | 53.8678 | 44.1904 | 31.0192 | 1787.2322 | 84.4896 | 24.6174 | 461.5874 | 0.0062336 | 60.0117 | 0.56672 | 0.349 | 93.1225 | 2.1066 | 0.26638 | 0.15272 | 5.1263 | 0.78225 | 0.24391 | 0 | 100 | 578.5 | 316 | 115.45 | 108.29 | 100.61 | 306.9 | 4 | 95.68 | 42.56 | 4 | 37.78 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.85 | 0 | 38.45 | 55 | 55 | 110.1 | 92.95 | 89.56 | 0 | 100.61 | 2.42 | 94.87 | 43.23 | 115.4 | 12.64 | 108.29 | 110 | 0 | 15706 | 83.23 | 117.09 | 221.31 | 215.25 | 220.63 | 0 | 36.25 | 50.55 | 15078 | 95.66 | 42.56 | 37.78 | 1.19 | 42.56 | 0 | 607 | 430.6 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 314 | 0 | 307.8 | 100.57 | 15707 | 15706 | 318
03/26/22 11:01:51.182 | 546.222 | 1367.3497 | 53.5964 | 44.0371 | 9.5593 | 30.1363 | 51.0161 | 0 | 1789.9326 | 94.101 | 85.5261 | 8.5749 | 25.0607 | 70.1384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.991 | 462.75 | 459.42 | 463.12 | 411.34 | 440.36 | 417.3 | 314.33 | 0.57546 | -0.17539 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6581144.7096 | 7666947.3846 | 7666947.3846 | 62.4287 | 62.1321 | 1.0018 | 0.9979 | 684451.2853 | 892619.1967 | 461.7634 | 0.50747 | 0 | 0 | 30.1363 | 25.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017857 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 553.0708 | 1367.9506 | 53.8647 | 44.1892 | 31.0199 | 1787.2307 | 84.5041 | 24.6125 | 461.5915 | 0.006156 | 60.0116 | 0.56683 | 0.34535 | 93.1359 | 2.0989 | 0.26621 | 0.15305 | 5.1255 | 0.77723 | 0.24048 | 0 | 100 | 578 | 315 | 115.4 | 108.29 | 100.59 | 306.4 | 4 | 95.65 | 42.55 | 4 | 37.76 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.85 | 0 | 38.45 | 55 | 55 | 110.1 | 92.95 | 89.52 | 0 | 100.59 | 2.42 | 94.87 | 43.23 | 115.4 | 12.65 | 108.29 | 110 | 0 | 15706 | 83.23 | 117.09 | 221.31 | 215.25 | 220.63 | 0 | 36.28 | 50.66 | 15083 | 95.65 | 42.55 | 37.76 | 1.22 | 42.55 | 0 | 608 | 431.3 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 312.9 | 0 | 306.7 | 100.52 | 15707 | 15706 | 315
03/26/22 11:01:56.181 | 546.3937 | 1368.0465 | 53.5965 | 44.0391 | 9.5575 | 30.7253 | 51.0196 | 0 | 1784.5497 | 94.1033 | 85.5258 | 8.5775 | 24.2457 | 70.0736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 462.77 | 459.44 | 463.12 | 411.46 | 440.39 | 417.28 | 314.38 | 0.57537 | 0.14607 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6583736.1955 | 7645269.5003 | 7645269.5003 | 62.4287 | 62.1321 | 1.0018 | 0.9979 | 684800.0449 | 889934.8358 | 461.7767 | 0.50602 | 0 | 0 | 30.7253 | 24.2457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017868 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 552.966 | 1367.9559 | 53.8617 | 44.188 | 31.0132 | 1787.2124 | 84.5182 | 24.6147 | 461.5955 | 0.0061646 | 60.0114 | 0.56694 | 0.34209 | 93.1491 | 2.0944 | 0.26614 | 0.1534 | 5.1111 | 0.77241 | 0.2375 | 0 | 100 | 577.8 | 315 | 115.48 | 108.29 | 100.49 | 306.6 | 4 | 95.68 | 42.56 | 4 | 37.78 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.45 | 55 | 55 | 110.1 | 92.95 | 89.5 | 0 | 100.49 | 2.42 | 94.89 | 43.23 | 115.48 | 12.61 | 108.29 | 110 | 0 | 15706 | 83.23 | 117.11 | 221.31 | 215.25 | 220.63 | 0 | 36.35 | 50.72 | 15088 | 95.68 | 42.56 | 37.78 | 1.23 | 42.56 | 0 | 608 | 429.3 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 313 | 0 | 306.7 | 100.49 | 15707 | 15706 | 316
03/26/22 11:02:01.182 | 547.0693 | 1369.9148 | 53.5964 | 44.0402 | 9.5562 | 30.5744 | 51.0155 | 0 | 1782.3459 | 94.1048 | 85.5262 | 8.5786 | 24.9233 | 70.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 462.81 | 459.44 | 463.14 | 411.55 | 440.39 | 417.17 | 314.39 | 0.57468 | 0.35106 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6591747.555 | 7637596.5575 | 7637596.5575 | 62.4287 | 62.132 | 1.0018 | 0.9979 | 685735.2611 | 888835.7752 | 461.7967 | 0.51033 | 0 | 0 | 30.5744 | 24.9233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017872 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 552.8619 | 1367.9626 | 53.8587 | 44.1869 | 31.0087 | 1787.168 | 84.5323 | 24.6187 | 461.5995 | 0.006173 | 60.0112 | 0.56705 | 0.3406 | 93.1621 | 2.0977 | 0.26609 | 0.15376 | 5.1169 | 0.76757 | 0.23442 | 0 | 100 | 577.8 | 315 | 115.55 | 108.29 | 100.49 | 305.4 | 4 | 95.72 | 42.55 | 4 | 37.76 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.95 | 0 | 38.45 | 55 | 55 | 110.15 | 92.98 | 89.5 | 0 | 100.49 | 2.42 | 94.9 | 43.23 | 115.53 | 12.59 | 108.29 | 110 | 0 | 15706 | 83.23 | 117.11 | 221.31 | 215.25 | 220.63 | 0 | 36.38 | 50.76 | 15093 | 95.71 | 42.55 | 37.76 | 1.26 | 42.55 | 0 | 608 | 425.4 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 312.8 | 0 | 306.6 | 100.43 | 15704 | 15706 | 315
03/26/22 11:02:06.181 | 546.7993 | 1369.4399 | 53.5964 | 44.0416 | 9.5548 | 30.9704 | 51.0102 | 0 | 1782.831 | 94.1072 | 85.5277 | 8.5796 | 24.3449 | 70.1095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.989 | 462.83 | 459.47 | 463.15 | 411.54 | 440.32 | 417.18 | 314.39 | 0.57496 | 0.28411 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6588846.988 | 7639852.8773 | 7639852.8773 | 62.4287 | 62.132 | 1.0018 | 0.9979 | 685497.5776 | 889077.5039 | 461.8167 | 0.50814 | 0 | 0 | 30.9704 | 24.3449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017873 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 552.7568 | 1367.9712 | 53.8558 | 44.1859 | 31.0061 | 1787.1476 | 84.5462 | 24.6226 | 461.6034 | 0.0061812 | 60.0111 | 0.56716 | 0.33754 | 93.175 | 2.1002 | 0.26607 | 0.15411 | 5.1271 | 0.76285 | 0.23199 | 0 | 100 | 577.4 | 316 | 115.65 | 108.31 | 100.43 | 304.8 | 4 | 95.77 | 42.55 | 4 | 37.76 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.98 | 0 | 38.45 | 55 | 55 | 110.2 | 92.99 | 89.5 | 0 | 100.43 | 2.42 | 94.93 | 43.23 | 115.65 | 12.56 | 108.31 | 110 | 0 | 15706 | 83.23 | 117.13 | 221.31 | 215.36 | 220.63 | 0 | 36.41 | 50.76 | 15098 | 95.76 | 42.55 | 37.76 | 1.26 | 42.55 | 0 | 608 | 427.7 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.4 | 311 | 0 | 304.8 | 100.42 | 15706 | 15706 | 316
03/26/22 11:02:11.181 | 546.3102 | 1368.5677 | 53.5966 | 44.0429 | 9.5537 | 31.8062 | 51.0205 | 0 | 1784.4 | 94.1098 | 85.5297 | 8.5802 | 23.3008 | 70.1157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.989 | 462.83 | 459.47 | 463.15 | 411.54 | 440.32 | 417.18 | 314.39 | 0.57548 | 0.17349 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6583586.2373 | 7643057.7725 | 7643057.7725 | 62.4287 | 62.132 | 1.0018 | 0.9979 | 684947.2948 | 889525.1228 | 461.8167 | 0.50814 | 0 | 0 | 31.8062 | 23.3008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017872 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 552.6469 | 1367.9711 | 53.8529 | 44.185 | 31.0057 | 1787.1349 | 84.56 | 24.6212 | 461.6072 | 0.0061895 | 60.011 | 0.56728 | 0.33374 | 93.1877 | 2.1001 | 0.26604 | 0.15446 | 5.131 | 0.758 | 0.22968 | 0 | 100 | 578.2 | 318 | 115.65 | 108.33 | 100.56 | 307 | 4 | 95.76 | 42.55 | 4 | 37.76 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.03 | 0 | 38.44 | 55 | 55 | 110.23 | 93.01 | 89.52 | 0 | 100.5 | 2.42 | 94.94 | 43.22 | 115.68 | 12.55 | 108.33 | 110 | 0 | 15706 | 83.23 | 117.13 | 221.31 | 215.36 | 220.63 | 0 | 36.37 | 50.66 | 15103 | 95.78 | 42.55 | 37.76 | 1.28 | 42.55 | 0 | 608 | 427.5 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.9 | 313.8 | 0 | 307.5 | 100.5 | 15706 | 15706 | 317
03/26/22 11:02:16.181 | 545.8314 | 1367.52 | 53.5968 | 44.0455 | 9.5513 | 32.0096 | 51.0374 | 0 | 1778.9809 | 94.1152 | 85.535 | 8.5802 | 23.2606 | 70.0922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 462.87 | 459.55 | 463.15 | 411.45 | 440.05 | 417.21 | 314.33 | 0.57587 | 0.36717 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6578106.664 | 7622605.2175 | 7622605.2175 | 62.4287 | 62.1319 | 1.0018 | 0.9979 | 684536.5263 | 887156.4117 | 461.8567 | 0.49943 | 0 | 0 | 32.0096 | 23.2606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017889 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 552.5373 | 1367.9715 | 53.85 | 44.184 | 31.0081 | 1787.1411 | 84.5737 | 24.6185 | 461.6111 | 0.0061979 | 60.0109 | 0.56739 | 0.32894 | 93.2004 | 2.1002 | 0.266 | 0.1548 | 5.1249 | 0.75305 | 0.22758 | 0 | 100 | 578.3 | 316 | 115.7 | 108.33 | 100.57 | 306.5 | 4 | 95.81 | 42.56 | 4 | 37.78 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.08 | 0 | 38.45 | 55 | 55 | 110.28 | 93.04 | 89.56 | 0 | 100.57 | 2.42 | 94.98 | 43.23 | 115.7 | 12.54 | 108.33 | 110 | 0 | 15706 | 83.23 | 117.13 | 221.44 | 215.36 | 220.75 | 0 | 36.32 | 50.52 | 15108 | 95.8 | 42.56 | 37.78 | 1.23 | 42.56 | 0 | 608 | 428.9 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 312.8 | 0 | 306.5 | 100.57 | 15704 | 15706 | 316
03/26/22 11:02:21.181 | 544.9066 | 1365.4608 | 53.5964 | 44.0469 | 9.5495 | 31.6732 | 51.0291 | 0 | 1778.3461 | 94.1179 | 85.5384 | 8.5795 | 23.2166 | 70.0897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 462.87 | 459.55 | 463.15 | 411.45 | 440.05 | 417.21 | 314.33 | 0.57685 | 0.26194 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6566671.2638 | 7619225.199 | 7619225.199 | 62.4287 | 62.1319 | 1.0018 | 0.9979 | 683505.7442 | 886839.3228 | 461.8567 | 0.49943 | 0 | 0 | 31.6732 | 23.2166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017888 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 552.4162 | 1367.9472 | 53.8471 | 44.1831 | 31.0138 | 1787.1183 | 84.5873 | 24.607 | 461.615 | 0.0062063 | 60.0108 | 0.56752 | 0.32385 | 93.213 | 2.1038 | 0.26595 | 0.15513 | 5.1549 | 0.74815 | 0.22575 | 0 | 100 | 577.7 | 315 | 115.7 | 108.35 | 100.47 | 303.9 | 4 | 95.8 | 42.56 | 4 | 37.78 | 43.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.1 | 0 | 38.45 | 55 | 55 | 110.3 | 93.05 | 89.63 | 0 | 100.47 | 2.42 | 94.99 | 43.23 | 115.7 | 12.56 | 108.35 | 110 | 0 | 15706 | 83.23 | 117.13 | 221.44 | 215.36 | 220.75 | 0 | 36.15 | 50.31 | 15113 | 95.8 | 42.56 | 37.78 | 1.21 | 42.56 | 0 | 608 | 424.8 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 312.4 | 0 | 306.2 | 100.43 | 15708 | 15706 | 314
03/26/22 11:02:26.181 | 544.111 | 1363.8815 | 53.5953 | 44.0487 | 9.5466 | 30.9811 | 51.0188 | 0 | 1781.2466 | 94.1221 | 85.544 | 8.5781 | 24.237 | 70.1124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9991 | 462.8801 | 459.5801 | 463.1601 | 411.3901 | 439.9701 | 417.2101 | 314.2901 | 0.57762 | -0.033718 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6556485.9602 | 7631596.7552 | 7631596.7552 | 62.4287 | 62.1318 | 1.0018 | 0.9979 | 682715.2565 | 888284.9535 | 461.8734 | 0.49653 | 0 | 0 | 30.9811 | 24.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017891 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 552.2909 | 1367.9142 | 53.8443 | 44.1822 | 31.0153 | 1787.0947 | 84.6009 | 24.6021 | 461.619 | 0.0062148 | 60.0108 | 0.56765 | 0.31861 | 93.2254 | 2.1208 | 0.26587 | 0.15544 | 5.1721 | 0.74319 | 0.22401 | 0 | 100 | 577.8 | 315 | 115.75 | 108.37 | 100.49 | 306.8 | 4 | 95.82 | 42.55 | 4 | 37.76 | 43.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.13 | 0 | 38.45 | 55 | 55 | 110.33 | 93.07 | 89.67 | 0 | 100.49 | 2.42 | 95 | 43.23 | 115.73 | 12.55 | 108.37 | 110 | 0 | 15706 | 83.23 | 117.13 | 221.44 | 215.36 | 220.75 | 0 | 36.06 | 50.27 | 15118 | 95.82 | 42.55 | 37.78 | 1.22 | 42.55 | 0 | 608 | 429.8 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 313.1 | 0 | 306.8 | 100.49 | 15705 | 15706 | 316
03/26/22 11:02:31.181 | 546.4247 | 1370.2399 | 53.594 | 44.0513 | 9.5427 | 31.0163 | 51.0266 | 0 | 1782.284 | 94.1298 | 85.5549 | 8.5749 | 24.488 | 70.1578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.009 | 462.86 | 459.62 | 463.17 | 411.17 | 439.83 | 417.28 | 314.23 | 0.57507 | 0.30565 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6584407.237 | 7633441.6278 | 7633441.6278 | 62.4287 | 62.1317 | 1.0018 | 0.9979 | 685898.1062 | 888800.6447 | 461.8833 | 0.49002 | 0 | 0 | 31.0163 | 24.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017888 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 552.1822 | 1367.9267 | 53.8414 | 44.1813 | 31.0156 | 1787.0626 | 84.6144 | 24.5986 | 461.6229 | 0.0062233 | 60.0107 | 0.56776 | 0.3167 | 93.2378 | 2.1278 | 0.26575 | 0.15573 | 5.184 | 0.73826 | 0.22219 | 0 | 100 | 577.4 | 317 | 115.75 | 108.37 | 100.42 | 306.6 | 4 | 95.82 | 42.56 | 4 | 37.78 | 43.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.13 | 0 | 38.46 | 55 | 55 | 110.33 | 93.07 | 89.67 | 0 | 100.42 | 2.42 | 95 | 43.25 | 115.75 | 12.55 | 108.37 | 110 | 0 | 15706 | 83.23 | 117.16 | 221.44 | 215.36 | 220.75 | 0 | 36.03 | 50.35 | 15123 | 95.82 | 42.58 | 37.79 | 1.22 | 42.58 | 0 | 608 | 429.1 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 313.6 | 0 | 307.3 | 100.47 | 15705 | 15706 | 313
03/26/22 11:02:36.181 | 546.3646 | 1370.3276 | 53.5937 | 44.0526 | 9.5411 | 31.3803 | 51.0209 | 0 | 1782.4801 | 94.1357 | 85.5635 | 8.5722 | 24.1103 | 70.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.009 | 462.86 | 459.62 | 463.17 | 411.17 | 439.83 | 417.28 | 314.23 | 0.57513 | 0.32396 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6584008.6334 | 7631442.5003 | 7631442.5003 | 62.4287 | 62.1317 | 1.0018 | 0.9979 | 685942.0302 | 888897.1579 | 461.8834 | 0.49002 | 0 | 0 | 31.3803 | 24.1103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.0179 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 552.0687 | 1367.9299 | 53.8385 | 44.1804 | 31.0152 | 1787.0382 | 84.6279 | 24.598 | 461.6272 | 0.0062324 | 60.0107 | 0.56787 | 0.31375 | 93.2502 | 2.131 | 0.26559 | 0.156 | 5.1952 | 0.73326 | 0.21976 | 0 | 100 | 577.7 | 317 | 115.73 | 108.39 | 100.52 | 306.6 | 4 | 95.81 | 42.59 | 4 | 37.8 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.13 | 0 | 38.48 | 55 | 55 | 110.28 | 93.04 | 89.65 | 0 | 100.52 | 2.42 | 95 | 43.26 | 115.75 | 12.57 | 108.39 | 110 | 0 | 15706 | 83.23 | 117.18 | 221.44 | 215.36 | 220.75 | 0 | 36.08 | 50.55 | 15128 | 95.82 | 42.59 | 37.8 | 1.22 | 42.59 | 0 | 608 | 431.6 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.6 | 312.6 | 0 | 306.4 | 100.45 | 15704 | 15706 | 317
03/26/22 11:02:41.181 | 545.2069 | 1367.6232 | 53.5935 | 44.0538 | 9.5397 | 31.1912 | 51.013 | 0 | 1783.1407 | 94.1434 | 85.5749 | 8.5684 | 24.7975 | 70.1508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.013 | 462.85 | 459.66 | 463.19 | 411.09 | 439.86 | 417.46 | 314.28 | 0.57644 | 0.13575 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6569896.1152 | 7631725.7104 | 7631725.7104 | 62.4287 | 62.1316 | 1.0018 | 0.9979 | 684588.3276 | 889224.8947 | 461.9 | 0.48495 | 0 | 0 | 31.1912 | 24.7975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017888 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 551.944 | 1367.9076 | 53.8356 | 44.1795 | 31.0135 | 1787.0449 | 84.6413 | 24.6029 | 461.6315 | 0.0061984 | 60.0107 | 0.568 | 0.30746 | 93.2625 | 2.1129 | 0.26536 | 0.15626 | 5.1894 | 0.72829 | 0.21743 | 0 | 100 | 578.3 | 317 | 115.75 | 108.39 | 100.57 | 306.9 | 4 | 95.81 | 42.59 | 4 | 37.8 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.13 | 0 | 38.48 | 55 | 55 | 110.33 | 93.07 | 89.69 | 0 | 100.57 | 2.42 | 95 | 43.26 | 115.73 | 12.58 | 108.39 | 110 | 0 | 15706 | 83.23 | 117.2 | 221.44 | 215.36 | 220.75 | 0 | 36.16 | 50.72 | 15133 | 95.81 | 42.59 | 37.8 | 1.22 | 42.59 | 0 | 608 | 429.5 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 314.1 | 0 | 307.9 | 100.57 | 15707 | 15706 | 316
03/26/22 11:02:46.181 | 546.3651 | 1370.1315 | 53.5946 | 44.0556 | 9.539 | 29.9455 | 51.0386 | 0 | 1790.4538 | 94.158 | 85.595 | 8.563 | 25.7847 | 70.1921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0231 | 462.8501 | 459.7101 | 463.2301 | 411.0401 | 440.0301 | 417.7701 | 314.4001 | 0.57544 | -0.058852 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6582925.8894 | 7660004.8039 | 7660004.8039 | 62.4287 | 62.1314 | 1.0018 | 0.9979 | 686097.0162 | 892905.3533 | 461.9301 | 0.48059 | 0 | 0 | 29.9455 | 25.7847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017883 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 551.8266 | 1367.9051 | 53.8326 | 44.1786 | 31.0065 | 1787.1058 | 84.6548 | 24.6124 | 461.6358 | 0.0061427 | 60.0107 | 0.56812 | 0.29948 | 93.2748 | 2.1094 | 0.26506 | 0.1565 | 5.1653 | 0.72331 | 0.21516 | 0 | 100 | 578.8 | 315 | 115.7 | 108.39 | 100.61 | 310.1 | 4 | 95.78 | 42.6 | 4 | 37.81 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.08 | 0 | 38.49 | 55 | 55 | 110.28 | 93.04 | 89.77 | 0 | 100.61 | 2.42 | 94.98 | 43.27 | 115.7 | 12.6 | 108.39 | 110 | 0 | 15706 | 83.25 | 117.2 | 221.44 | 215.47 | 220.75 | 0 | 36.25 | 50.86 | 15138 | 95.8 | 42.6 | 37.81 | 1.19 | 42.6 | 0 | 608 | 428.2 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 314 | 0 | 307.8 | 100.73 | 15707 | 15706 | 318
03/26/22 11:02:51.182 | 545.384 | 1368.1135 | 53.5963 | 44.0569 | 9.5394 | 30.7251 | 51.0339 | 0 | 1792.4821 | 94.1677 | 85.606 | 8.5617 | 24.654 | 70.2053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0271 | 462.8601 | 459.7401 | 463.2701 | 411.0001 | 440.1101 | 417.8501 | 314.4501 | 0.57657 | -0.2762 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6571620.4119 | 7665540.4929 | 7665540.4929 | 62.4287 | 62.1312 | 1.0018 | 0.9979 | 684833.634 | 893878.6668 | 461.9568 | 0.47984 | 0 | 0 | 30.7251 | 24.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017881 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 551.7181 | 1367.9222 | 53.8296 | 44.1776 | 31.0001 | 1787.1549 | 84.6681 | 24.6186 | 461.6401 | 0.0060871 | 60.0107 | 0.56823 | 0.29351 | 93.287 | 2.115 | 0.26469 | 0.15673 | 5.1548 | 0.71826 | 0.21326 | 0 | 100 | 578.8 | 317 | 115.68 | 108.39 | 100.66 | 307.6 | 4 | 95.77 | 42.6 | 4 | 37.81 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.03 | 0 | 38.49 | 55 | 55 | 110.28 | 93.04 | 89.71 | 0 | 100.66 | 2.42 | 94.95 | 43.27 | 115.65 | 12.62 | 108.39 | 110 | 0 | 15706 | 83.25 | 117.23 | 221.44 | 215.47 | 220.75 | 0 | 36.33 | 50.98 | 15143 | 95.77 | 42.6 | 37.81 | 1.15 | 42.6 | 0 | 608 | 430.1 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 313.7 | 0 | 307.4 | 100.61 | 15704 | 15706 | 315
03/26/22 11:02:56.180 | 545.5192 | 1368.3974 | 53.5976 | 44.0579 | 9.5397 | 31.2882 | 51.0419 | 0 | 1790.8357 | 94.1736 | 85.612 | 8.5616 | 24.0277 | 70.1974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.027 | 462.86 | 459.74 | 463.27 | 411 | 440.11 | 417.85 | 314.45 | 0.57642 | -0.1433 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6573744.3851 | 7657657.2191 | 7657657.2191 | 62.4287 | 62.1312 | 1.0018 | 0.9979 | 684975.6687 | 893056.7571 | 461.9567 | 0.47984 | 0 | 0 | 31.2882 | 24.0277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017888 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 551.6092 | 1367.9429 | 53.8266 | 44.1767 | 31.0029 | 1787.2076 | 84.6815 | 24.6131 | 461.6445 | 0.0060966 | 60.0107 | 0.56833 | 0.28762 | 93.2992 | 2.1012 | 0.26422 | 0.15693 | 5.1436 | 0.71325 | 0.21154 | 0 | 100 | 578.5 | 315 | 115.68 | 108.37 | 100.66 | 308.1 | 4 | 95.78 | 42.59 | 4 | 37.8 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.05 | 0 | 38.49 | 55 | 55 | 110.25 | 93.03 | 89.77 | 0 | 100.66 | 2.42 | 94.97 | 43.27 | 115.73 | 12.57 | 108.37 | 110 | 0 | 15706 | 83.27 | 117.25 | 221.44 | 215.47 | 220.88 | 0 | 36.48 | 51.1 | 15148 | 95.81 | 42.59 | 37.8 | 1.17 | 42.59 | 0 | 608 | 429.7 | 460.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 314.2 | 0 | 308 | 100.61 | 15708 | 15706 | 317
03/26/22 11:03:01.180 | 545.357 | 1367.8813 | 53.6011 | 44.0606 | 9.5405 | 31.6203 | 51.0227 | 0 | 1783.2078 | 94.1855 | 85.6234 | 8.5621 | 23.5348 | 70.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.022 | 462.83 | 459.76 | 463.32 | 410.91 | 440.32 | 417.99 | 314.52 | 0.57672 | 0.26665 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6572079.704 | 7624907.3805 | 7624907.3805 | 62.4287 | 62.1311 | 1.0018 | 0.9979 | 684717.1706 | 889251.1603 | 461.97 | 0.47839 | 0 | 0 | 31.6203 | 23.5348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017894 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 551.5036 | 1367.9704 | 53.8235 | 44.1757 | 31.0022 | 1787.1987 | 84.6948 | 24.6111 | 461.6489 | 0.006041 | 60.0107 | 0.56844 | 0.28535 | 93.3113 | 2.0863 | 0.26362 | 0.15709 | 5.1461 | 0.70832 | 0.20972 | 0 | 100 | 577.6 | 316 | 115.73 | 108.35 | 100.45 | 306.8 | 4 | 95.81 | 42.59 | 4 | 37.8 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.13 | 0 | 38.48 | 55 | 55 | 110.3 | 93.05 | 89.71 | 0 | 100.45 | 2.42 | 95 | 43.26 | 115.75 | 12.53 | 108.35 | 110 | 0 | 15706 | 83.27 | 117.28 | 221.56 | 215.47 | 220.88 | 0 | 36.51 | 50.96 | 15153 | 95.82 | 42.59 | 37.8 | 1.17 | 42.59 | 0 | 608 | 428.4 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.4 | 313.8 | 0 | 307.5 | 100.59 | 15706 | 15706 | 317
03/26/22 11:03:06.182 | 544.1528 | 1364.826 | 53.6041 | 44.0633 | 9.5408 | 31.9612 | 51.018 | 0 | 1783.4555 | 94.193 | 85.631 | 8.562 | 23.1111 | 70.1686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.016 | 462.82 | 459.73 | 463.32 | 410.91 | 440.45 | 418.01 | 314.53 | 0.57802 | 0.074946 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6557865.3462 | 7625334.7236 | 7625334.7236 | 62.4286 | 62.131 | 1.0018 | 0.9979 | 683187.6604 | 889373.5582 | 461.9567 | 0.48201 | 0 | 0 | 31.9612 | 23.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017886 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 551.387 | 1367.9665 | 53.8204 | 44.1746 | 31.0053 | 1787.1679 | 84.708 | 24.6052 | 461.6533 | 0.0060073 | 60.0107 | 0.56856 | 0.28236 | 93.3233 | 2.088 | 0.26291 | 0.15722 | 5.1626 | 0.70337 | 0.20794 | 0 | 100 | 577.8 | 317 | 115.75 | 108.37 | 100.49 | 308.4 | 4 | 95.82 | 42.59 | 4 | 37.8 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.15 | 0 | 38.48 | 55 | 55 | 110.33 | 93.07 | 89.73 | 0 | 100.49 | 2.42 | 95.02 | 43.26 | 115.78 | 12.55 | 108.37 | 110 | 0 | 15706 | 83.27 | 117.3 | 221.56 | 215.47 | 220.88 | 0 | 36.41 | 50.78 | 15158 | 95.82 | 42.59 | 37.79 | 1.17 | 42.59 | 0 | 608 | 430.9 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 312.3 | 0 | 306.1 | 100.49 | 15708 | 15706 | 315
03/26/22 11:03:11.181 | 543.9195 | 1364.2118 | 53.6066 | 44.0656 | 9.541 | 30.1947 | 51.0302 | 0 | 1785.7006 | 94.1984 | 85.6367 | 8.5616 | 23.2061 | 70.1789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.016 | 462.82 | 459.73 | 463.32 | 410.91 | 440.45 | 418.01 | 314.53 | 0.57827 | -0.1052 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6553504.4163 | 7634752.8301 | 7634752.8301 | 62.4286 | 62.1309 | 1.0018 | 0.9979 | 682880.1221 | 890492.2573 | 461.9567 | 0.48201 | 0 | 0 | 30.1947 | 23.2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017891 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 551.263 | 1367.9501 | 53.8173 | 44.1736 | 30.9993 | 1787.1696 | 84.7212 | 24.5988 | 461.6577 | 0.0059951 | 60.0107 | 0.56868 | 0.27665 | 93.3354 | 2.1059 | 0.2621 | 0.15731 | 5.1621 | 0.69836 | 0.20594 | 0 | 100 | 578.3 | 317 | 115.8 | 108.39 | 100.57 | 305.1 | 4 | 95.85 | 42.59 | 4 | 37.8 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.18 | 0 | 38.48 | 55 | 55 | 110.35 | 93.08 | 89.71 | 0 | 100.57 | 2.42 | 95.03 | 43.26 | 115.8 | 12.55 | 108.39 | 110 | 0 | 15706 | 83.29 | 117.3 | 221.56 | 215.47 | 220.88 | 0 | 36.36 | 50.7 | 15163 | 95.85 | 42.59 | 37.8 | 1.18 | 42.59 | 0 | 608 | 427.7 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 311.8 | 0 | 305.5 | 100.49 | 15705 | 15706 | 316
03/26/22 11:03:16.181 | 544.6118 | 1365.7601 | 53.6135 | 44.0712 | 9.5423 | 14.1409 | 50.9854 | 0 | 1787.5224 | 94.2097 | 85.6487 | 8.561 | 25.4646 | 70.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.013 | 462.83 | 459.71 | 463.36 | 410.95 | 440.65 | 417.97 | 314.56 | 0.57759 | -0.30778 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6547752.7774 | 7644533.6097 | 7644533.6097 | 62.4286 | 62.1308 | 1.0018 | 0.9979 | 683654.8535 | 891398.9709 | 461.9667 | 0.48849 | 0 | 0 | 14.1409 | 25.4646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017885 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 551.1432 | 1367.944 | 53.8141 | 44.1725 | 30.9364 | 1787.1742 | 84.7343 | 24.5952 | 461.6621 | 0.005918 | 60.0108 | 0.5688 | 0.27057 | 93.3473 | 2.1124 | 0.26113 | 0.15735 | 5.1603 | 0.69336 | 0.20392 | 0 | 100 | 578.7 | 316 | 115.85 | 108.39 | 100.64 | 306.6 | 4 | 95.87 | 42.6 | 4 | 37.81 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.2 | 0 | 38.49 | 55 | 55 | 110.4 | 93.1 | 89.77 | 0 | 100.64 | 2.42 | 95.04 | 43.27 | 115.85 | 12.52 | 108.39 | 110 | 0 | 15706 | 83.29 | 117.3 | 221.56 | 215.47 | 220.88 | 0 | 36.35 | 50.68 | 15168 | 95.87 | 42.6 | 37.81 | 1.17 | 42.6 | 0 | 608 | 428.5 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.8 | 314.5 | 0 | 308.2 | 100.66 | 15706 | 15706 | 316
03/26/22 11:03:21.180 | 544.0557 | 1364.1293 | 53.6163 | 44.0733 | 9.5431 | 9.4589 | 50.9786 | 0 | 1785.4631 | 94.2135 | 85.6525 | 8.561 | 25.3879 | 70.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 462.8301 | 459.6901 | 463.3601 | 410.9801 | 440.6901 | 417.9201 | 314.5601 | 0.57818 | -0.36235 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6537826.4644 | 7638778.2845 | 7638778.2845 | 62.4286 | 62.1307 | 1.0018 | 0.9979 | 682915.8968 | 890719.0855 | 461.9601 | 0.49138 | 0 | 0 | 9.4589 | 25.3879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01624 | 0.017894 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 551.0145 | 1367.9141 | 53.8109 | 44.1713 | 30.8132 | 1787.1474 | 84.7473 | 24.6029 | 461.6664 | 0.0059054 | 60.0108 | 0.56893 | 0.26409 | 93.3592 | 2.128 | 0.26 | 0.15732 | 5.1566 | 0.6884 | 0.20208 | 0 | 100 | 578.2 | 316 | 115.78 | 108.41 | 100.56 | 306.7 | 4 | 95.83 | 42.59 | 4 | 37.8 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.15 | 0 | 38.49 | 55 | 55 | 110.35 | 93.08 | 89.71 | 0 | 100.56 | 2.42 | 95.02 | 43.27 | 115.78 | 12.58 | 108.41 | 110 | 0 | 15706 | 83.29 | 117.3 | 221.56 | 215.47 | 220.88 | 0 | 36.31 | 50.61 | 15173 | 95.83 | 42.59 | 37.8 | 1.18 | 42.59 | 0 | 608 | 430.1 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 312.2 | 0 | 306 | 100.64 | 15706 | 15706 | 315
03/26/22 11:03:26.181 | 544.7863 | 1365.8634 | 53.6222 | 44.0775 | 9.5447 | 4.0569 | 50.9604 | 0 | 1785.8812 | 94.2205 | 85.6582 | 8.5623 | 24.2324 | 70.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.012 | 462.83 | 459.69 | 463.36 | 410.98 | 440.69 | 417.92 | 314.56 | 0.5774 | -0.30063 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6540996.0186 | 7637244.4779 | 7637244.4779 | 62.4286 | 62.1307 | 1.0018 | 0.9979 | 683706.1446 | 890579.1393 | 461.96 | 0.49138 | 0 | 0 | 4.0569 | 24.2324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017888 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 550.8807 | 1367.8711 | 53.8077 | 44.1701 | 30.663 | 1787.1202 | 84.7603 | 24.6066 | 461.6706 | 0.005828 | 60.0108 | 0.56906 | 0.25667 | 93.3709 | 2.1296 | 0.25872 | 0.15722 | 5.1583 | 0.68344 | 0.20021 | 0 | 100 | 578.9 | 317 | 115.75 | 108.41 | 100.68 | 308.4 | 4 | 95.83 | 42.6 | 4 | 37.81 | 43.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.13 | 0 | 38.49 | 55 | 55 | 110.33 | 93.07 | 89.79 | 0 | 100.68 | 2.42 | 95 | 43.27 | 115.75 | 12.59 | 108.41 | 110 | 0 | 15706 | 83.29 | 117.3 | 221.56 | 215.58 | 220.88 | 0 | 36.27 | 50.59 | 15178 | 95.82 | 42.61 | 37.82 | 1.12 | 42.61 | 0 | 608 | 429.9 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 313.7 | 0 | 307.4 | 100.61 | 15706 | 15706 | 317
03/26/22 11:03:31.181 | 545.517 | 1367.5355 | 53.6259 | 44.0801 | 9.5458 | 6.8188 | 50.9439 | 0 | 1788.1623 | 94.224 | 85.6604 | 8.5636 | 23.8843 | 70.0979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0141 | 462.8101 | 459.6401 | 463.3301 | 411.0501 | 440.8201 | 417.9201 | 314.5801 | 0.57666 | -0.29179 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6552196.8424 | 7647802.5956 | 7647802.5956 | 62.4286 | 62.1306 | 1.0018 | 0.9979 | 684543.0044 | 891716.3585 | 461.9267 | 0.49503 | 0 | 0 | 6.8188 | 23.8843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017886 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 550.7509 | 1367.8381 | 53.8044 | 44.1689 | 30.5093 | 1787.0993 | 84.7731 | 24.6077 | 461.6746 | 0.0058365 | 60.0107 | 0.56919 | 0.24949 | 93.3826 | 2.1055 | 0.25731 | 0.15707 | 5.153 | 0.67838 | 0.19887 | 0 | 100 | 578.9 | 317 | 115.73 | 108.41 | 100.73 | 308 | 4 | 95.81 | 42.63 | 4 | 37.84 | 43.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.13 | 0 | 38.51 | 55 | 55 | 110.33 | 93.07 | 89.75 | 0 | 100.73 | 2.42 | 95 | 43.3 | 115.73 | 12.6 | 108.41 | 110 | 0 | 15706 | 83.32 | 117.33 | 221.56 | 215.58 | 220.88 | 0 | 36.27 | 50.66 | 15183 | 95.81 | 42.63 | 37.84 | 1.11 | 42.63 | 0 | 608 | 425.2 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 314.6 | 0 | 308.4 | 100.64 | 15705 | 15706 | 315
03/26/22 11:03:36.182 | 544.4656 | 1364.2841 | 53.6303 | 44.083 | 9.5472 | 22.8761 | 51.0052 | 0 | 1790.0668 | 94.2275 | 85.6621 | 8.5654 | 24.9956 | 70.2235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.013 | 462.81 | 459.63 | 463.31 | 411.11 | 440.87 | 417.97 | 314.61 | 0.57783 | -0.43693 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6551702.5884 | 7658482.8004 | 7658482.8004 | 62.4286 | 62.1306 | 1.0018 | 0.9979 | 683142.6414 | 892663.2664 | 461.9167 | 0.49504 | 0 | 0 | 22.8761 | 24.9956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016246 | 0.017884 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 550.621 | 1367.806 | 53.8012 | 44.1676 | 30.4353 | 1787.0964 | 84.7859 | 24.6104 | 461.6783 | 0.0057796 | 60.0107 | 0.56931 | 0.24204 | 93.3943 | 2.0984 | 0.25575 | 0.15686 | 5.1514 | 0.67324 | 0.19719 | 0 | 100 | 579.2 | 316 | 115.73 | 108.39 | 100.73 | 308.1 | 4 | 95.81 | 42.63 | 4 | 37.84 | 43.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.1 | 0 | 38.53 | 55 | 55 | 110.33 | 93.07 | 89.71 | 0 | 100.73 | 2.42 | 94.99 | 43.31 | 115.73 | 12.58 | 108.39 | 110 | 0 | 15706 | 83.32 | 117.33 | 221.56 | 215.58 | 221 | 0 | 36.32 | 50.82 | 15188 | 95.81 | 42.63 | 37.84 | 1.11 | 42.63 | 0 | 608 | 430.3 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.8 | 310.6 | 0 | 304.3 | 100.66 | 15706 | 15706 | 315
03/26/22 11:03:41.180 | 544.4499 | 1364.537 | 53.6327 | 44.0846 | 9.5481 | 29.1726 | 51.0407 | 0 | 1791.3364 | 94.2291 | 85.6629 | 8.5662 | 25.18 | 70.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.013 | 462.81 | 459.63 | 463.31 | 411.11 | 440.87 | 417.97 | 314.61 | 0.57785 | -0.42686 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6558979.8336 | 7665122.9534 | 7665122.9534 | 62.4286 | 62.1306 | 1.0018 | 0.9979 | 683041.7358 | 893298.7996 | 461.9167 | 0.49504 | 0 | 0 | 29.1726 | 25.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017869 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 550.4921 | 1367.7738 | 53.7978 | 44.1663 | 30.4279 | 1787.1132 | 84.7987 | 24.6102 | 461.6819 | 0.0057439 | 60.0107 | 0.56944 | 0.23454 | 93.4059 | 2.1038 | 0.25402 | 0.15658 | 5.1603 | 0.66801 | 0.19563 | 0 | 100 | 578.5 | 314 | 115.65 | 108.39 | 100.64 | 305.8 | 4 | 95.77 | 42.63 | 4 | 37.84 | 43.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.05 | 0 | 38.53 | 55 | 55 | 110.3 | 93.05 | 89.77 | 0 | 100.64 | 2.42 | 94.97 | 43.31 | 115.7 | 12.6 | 108.39 | 110 | 0 | 15706 | 83.34 | 117.37 | 221.56 | 215.58 | 221 | 0 | 36.44 | 50.95 | 15193 | 95.8 | 42.61 | 37.84 | 1.16 | 42.61 | 0 | 608 | 428.2 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 312.1 | 0 | 305.8 | 100.61 | 15705 | 15706 | 314
03/26/22 11:03:46.180 | 546.1911 | 1368.5781 | 53.6394 | 44.089 | 9.5503 | 32.1306 | 51.0599 | 0 | 1795.3413 | 94.2328 | 85.6649 | 8.5679 | 23.8405 | 70.2346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9961 | 462.8301 | 459.6501 | 463.3301 | 411.1901 | 440.9601 | 418.1101 | 314.7001 | 0.57617 | -0.3406 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6582551.6749 | 7682268.6772 | 7682268.6772 | 62.4286 | 62.1306 | 1.0018 | 0.9979 | 685064.2854 | 895295.6913 | 461.9367 | 0.49502 | 0 | 0 | 32.1306 | 23.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017869 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 550.379 | 1367.7794 | 53.7945 | 44.165 | 30.4381 | 1787.1469 | 84.8113 | 24.6007 | 461.6854 | 0.0057515 | 60.0106 | 0.56955 | 0.22897 | 93.4173 | 2.1046 | 0.25207 | 0.1562 | 5.1942 | 0.66271 | 0.19444 | 0 | 100 | 578.7 | 316 | 115.7 | 108.39 | 100.64 | 307.1 | 4 | 95.8 | 42.61 | 4 | 37.82 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.03 | 0 | 38.51 | 55 | 55 | 110.25 | 93.03 | 89.71 | 0 | 100.64 | 2.42 | 94.95 | 43.3 | 115.68 | 12.6 | 108.39 | 110 | 0 | 15706 | 83.34 | 117.37 | 221.68 | 215.58 | 221 | 0 | 36.51 | 50.98 | 15198 | 95.8 | 42.61 | 37.82 | 1.2 | 42.61 | 0 | 608 | 430.4 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.8 | 311.8 | 0 | 305.5 | 100.66 | 15707 | 15706 | 318
03/26/22 11:03:51.180 | 546.0213 | 1367.9174 | 53.6435 | 44.0915 | 9.552 | 31.4537 | 51.0415 | 0 | 1791.2435 | 94.2347 | 85.6652 | 8.5695 | 24.7726 | 70.2429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9961 | 462.8301 | 459.6501 | 463.3301 | 411.1901 | 440.9601 | 418.1101 | 314.7001 | 0.57635 | -0.17653 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6579904.7359 | 7667228.1251 | 7667228.1251 | 62.4285 | 62.1305 | 1.0018 | 0.9979 | 684733.4029 | 893252.1301 | 461.9367 | 0.49502 | 0 | 0 | 31.4537 | 24.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017869 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 550.2654 | 1367.7844 | 53.7911 | 44.1636 | 30.4429 | 1787.1488 | 84.8239 | 24.5967 | 461.6888 | 0.0057588 | 60.0104 | 0.56966 | 0.22518 | 93.4287 | 2.1039 | 0.24991 | 0.15574 | 5.1956 | 0.65729 | 0.1935 | 0 | 100 | 578.4 | 315 | 115.7 | 108.39 | 100.7 | 306.3 | 4 | 95.8 | 42.63 | 4 | 37.84 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.1 | 0 | 38.53 | 55 | 55 | 110.33 | 93.07 | 89.63 | 0 | 100.7 | 2.42 | 94.99 | 43.31 | 115.73 | 12.58 | 108.39 | 110 | 0 | 15706 | 83.36 | 117.4 | 221.68 | 215.58 | 221 | 0 | 36.55 | 50.96 | 15203 | 95.81 | 42.63 | 37.84 | 1.2 | 42.63 | 0 | 608 | 427 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.6 | 313.2 | 0 | 306.9 | 100.63 | 15706 | 15706 | 316
03/26/22 11:03:56.180 | 546.6474 | 1368.8567 | 53.6468 | 44.0934 | 9.5534 | 29.8496 | 51.0349 | 0 | 1791.9092 | 94.236 | 85.6649 | 8.5711 | 24.6423 | 70.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.987 | 462.83 | 459.66 | 463.32 | 411.21 | 440.95 | 418.17 | 314.72 | 0.57573 | -0.13072 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6587184.2694 | 7671073.9605 | 7671073.9605 | 62.4285 | 62.1305 | 1.0018 | 0.9979 | 685441.1466 | 893563.5652 | 461.9367 | 0.49285 | 0 | 0 | 29.8496 | 24.6423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016243 | 0.017875 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 550.1569 | 1367.8008 | 53.7876 | 44.1622 | 30.4399 | 1787.1371 | 84.8364 | 24.5917 | 461.692 | 0.0057657 | 60.0103 | 0.56976 | 0.22289 | 93.44 | 2.1006 | 0.24755 | 0.1552 | 5.1824 | 0.65168 | 0.1928 | 0 | 100 | 578.8 | 316 | 115.65 | 108.39 | 100.66 | 307.7 | 4 | 95.77 | 42.61 | 4 | 37.82 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.05 | 0 | 38.51 | 55 | 55 | 110.28 | 93.04 | 89.63 | 0 | 100.66 | 2.42 | 94.97 | 43.3 | 115.68 | 12.61 | 108.39 | 110 | 0 | 15706 | 83.36 | 117.4 | 221.68 | 215.58 | 221 | 0 | 36.54 | 50.91 | 15208 | 95.78 | 42.61 | 37.82 | 1.26 | 42.61 | 0 | 607 | 429 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 312.9 | 0 | 306.7 | 100.61 | 15704 | 15706 | 315
03/26/22 11:04:01.181 | 545.158 | 1365.2698 | 53.652 | 44.0966 | 9.5554 | 18.3453 | 51.006 | 0 | 1785.4167 | 94.2369 | 85.6631 | 8.5738 | 23.7682 | 70.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.987 | 462.83 | 459.66 | 463.32 | 411.21 | 440.95 | 418.17 | 314.72 | 0.5773 | -0.1717 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6557991.389 | 7644975.2201 | 7644975.2201 | 62.4285 | 62.1305 | 1.0018 | 0.9979 | 683407.7494 | 890346.7845 | 461.9367 | 0.49285 | 0 | 0 | 18.3453 | 23.7682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016248 | 0.017881 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 550.0437 | 1367.8051 | 53.7841 | 44.1608 | 30.3739 | 1787.0839 | 84.8489 | 24.5816 | 461.6952 | 0.0057726 | 60.0101 | 0.56987 | 0.22149 | 93.4513 | 2.0947 | 0.24505 | 0.1546 | 5.1505 | 0.64582 | 0.19204 | 0 | 100 | 578.7 | 315 | 115.75 | 108.39 | 100.64 | 306.5 | 4 | 95.82 | 42.61 | 4 | 37.82 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.1 | 0 | 38.51 | 55 | 55 | 110.3 | 93.05 | 89.63 | 0 | 100.64 | 2.42 | 94.99 | 43.3 | 115.78 | 12.57 | 108.39 | 110 | 0 | 15706 | 83.36 | 117.4 | 221.68 | 215.69 | 221 | 0 | 36.58 | 50.93 | 15213 | 95.82 | 42.61 | 37.82 | 1.24 | 42.61 | 0 | 608 | 430.8 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 313.6 | 0 | 307.3 | 100.64 | 15706 | 15706 | 316
03/26/22 11:04:06.180 | 544.8869 | 1364.6144 | 53.6552 | 44.0988 | 9.5564 | 13.8142 | 50.9879 | 0 | 1782.1033 | 94.2367 | 85.6611 | 8.5756 | 24.2731 | 70.1405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.979 | 462.84 | 459.68 | 463.34 | 411.14 | 440.97 | 418.2 | 314.72 | 0.57759 | -0.11128 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6550806.087 | 7633164.6282 | 7633164.6282 | 62.4285 | 62.1306 | 1.0018 | 0.9979 | 683004.6242 | 888756.4771 | 461.9534 | 0.49211 | 0 | 0 | 13.8142 | 24.2731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016246 | 0.01788 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.9259 | 1367.7993 | 53.7806 | 44.1592 | 30.2775 | 1787.0074 | 84.8613 | 24.5808 | 461.6986 | 0.0057799 | 60.0099 | 0.56999 | 0.22036 | 93.4625 | 2.1021 | 0.24224 | 0.15385 | 5.1212 | 0.63981 | 0.19121 | 0 | 100 | 578.6 | 315 | 115.83 | 108.41 | 100.63 | 306.2 | 4 | 95.86 | 42.63 | 4 | 37.84 | 43.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.18 | 0 | 38.51 | 55 | 55 | 110.35 | 93.08 | 89.67 | 0 | 100.63 | 2.42 | 95.03 | 43.3 | 115.8 | 12.57 | 108.41 | 110 | 0 | 15706 | 83.38 | 117.4 | 221.68 | 215.69 | 221 | 0 | 36.58 | 50.87 | 15218 | 95.85 | 42.63 | 37.84 | 1.19 | 42.63 | 0 | 608 | 429.2 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 314.4 | 0 | 308.2 | 100.61 | 15705 | 15706 | 317
03/26/22 11:04:11.181 | 545.4752 | 1365.853 | 53.6605 | 44.1036 | 9.5569 | 13.985 | 50.9804 | 0 | 1784.3071 | 94.2341 | 85.6568 | 8.5774 | 23.8341 | 70.1776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9761 | 462.8301 | 459.6901 | 463.3501 | 411.0701 | 440.9401 | 418.1601 | 314.6801 | 0.57689 | -0.15261 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6557977.5827 | 7643468.2177 | 7643468.2177 | 62.4285 | 62.1306 | 1.0018 | 0.9979 | 683699.3099 | 889794.3824 | 461.9567 | 0.49067 | 0 | 0 | 13.985 | 23.8341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016246 | 0.017883 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.8136 | 1367.8027 | 53.777 | 44.1577 | 30.1775 | 1786.965 | 84.8736 | 24.5803 | 461.7022 | 0.0057876 | 60.0097 | 0.5701 | 0.21805 | 93.4736 | 2.0975 | 0.23926 | 0.15299 | 5.1067 | 0.63359 | 0.18997 | 0 | 100 | 578.5 | 317 | 115.8 | 108.43 | 100.61 | 308.3 | 4 | 95.85 | 42.61 | 4 | 37.82 | 43.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.18 | 0 | 38.51 | 55 | 55 | 110.35 | 93.08 | 89.71 | 0 | 100.61 | 2.42 | 95.03 | 43.3 | 115.83 | 12.57 | 108.43 | 110 | 0 | 15706 | 83.38 | 117.4 | 221.68 | 215.69 | 221 | 0 | 36.53 | 50.76 | 15222 | 95.85 | 42.61 | 37.82 | 1.18 | 42.61 | 0 | 608 | 430.1 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 312.4 | 0 | 306.1 | 100.57 | 15708 | 15706 | 315
03/26/22 11:04:16.180 | 545.6646 | 1366.4053 | 53.662 | 44.1056 | 9.5564 | 13.907 | 50.9856 | 0 | 1786.418 | 94.2328 | 85.6555 | 8.5773 | 24.6919 | 70.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.976 | 462.83 | 459.69 | 463.35 | 411.07 | 440.94 | 418.16 | 314.68 | 0.57669 | -0.25475 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6560186.6882 | 7653390.8878 | 7653390.8878 | 62.4285 | 62.1306 | 1.0018 | 0.9979 | 683975.6733 | 890847.2053 | 461.9567 | 0.49067 | 0 | 0 | 13.907 | 24.6919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016245 | 0.017876 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.7056 | 1367.8055 | 53.7735 | 44.1561 | 30.0794 | 1786.9828 | 84.8858 | 24.5834 | 461.706 | 0.0057958 | 60.0095 | 0.57021 | 0.2124 | 93.4847 | 2.0952 | 0.2362 | 0.152 | 5.0991 | 0.6273 | 0.18821 | 0 | 100 | 578.7 | 317 | 115.88 | 108.43 | 100.64 | 309.1 | 4 | 95.88 | 42.61 | 4 | 37.82 | 43.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.25 | 0 | 38.51 | 55 | 55 | 110.43 | 93.12 | 89.73 | 0 | 100.64 | 2.42 | 95.07 | 43.3 | 115.88 | 12.55 | 108.43 | 110 | 0 | 15706 | 83.38 | 117.4 | 221.68 | 215.69 | 221.12 | 0 | 36.51 | 50.74 | 15227 | 95.88 | 42.61 | 37.82 | 1.18 | 42.61 | 0 | 608 | 427.6 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.7 | 315.4 | 0 | 309.1 | 100.64 | 15709 | 15706 | 317
03/26/22 11:04:21.180 | 545.4306 | 1366.1111 | 53.6631 | 44.1092 | 9.5539 | 13.8103 | 50.9945 | 0 | 1793.0447 | 94.2307 | 85.6563 | 8.5744 | 25.8697 | 70.1871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9851 | 462.8301 | 459.6901 | 463.3801 | 411.0201 | 440.9601 | 418.0401 | 314.6501 | 0.57688 | -0.61002 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6557265.4871 | 7677622.237 | 7677622.237 | 62.4285 | 62.1306 | 1.0018 | 0.9979 | 683833.5277 | 893747.6678 | 461.9668 | 0.49282 | 0 | 0 | 13.8103 | 25.8697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016248 | 0.017862 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.597 | 1367.7983 | 53.77 | 44.1544 | 29.9802 | 1787.0418 | 84.8979 | 24.5948 | 461.7098 | 0.0058041 | 60.0093 | 0.57032 | 0.20417 | 93.4958 | 2.0988 | 0.23312 | 0.15092 | 5.0982 | 0.62087 | 0.18612 | 0 | 100 | 578.9 | 317 | 115.78 | 108.45 | 100.64 | 306.6 | 4 | 95.83 | 42.61 | 4 | 37.82 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.2 | 0 | 38.5 | 55 | 55 | 110.4 | 93.09 | 89.75 | 0 | 100.64 | 2.42 | 95.04 | 43.28 | 115.78 | 12.62 | 108.45 | 110 | 0 | 15706 | 83.38 | 117.4 | 221.68 | 215.69 | 221.12 | 0 | 36.51 | 50.68 | 15233 | 95.83 | 42.61 | 37.82 | 1.2 | 42.61 | 0 | 608 | 428.9 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.4 | 312.3 | 0 | 306 | 100.59 | 15707 | 15706 | 315
03/26/22 11:04:26.180 | 546.7834 | 1369.9767 | 53.6629 | 44.1119 | 9.551 | 19.0538 | 51.0215 | 0 | 1791.7751 | 94.2307 | 85.6595 | 8.5712 | 24.3031 | 70.2169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.985 | 462.83 | 459.69 | 463.38 | 411.02 | 440.96 | 418.04 | 314.65 | 0.57546 | -0.24344 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6578175.1173 | 7670455.1307 | 7670455.1307 | 62.4285 | 62.1306 | 1.0018 | 0.9979 | 685763.3522 | 893518.0769 | 461.9667 | 0.49282 | 0 | 0 | 19.0538 | 24.3031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017868 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.4954 | 1367.7946 | 53.7666 | 44.1528 | 29.897 | 1787.1171 | 84.9099 | 24.5954 | 461.7138 | 0.0058126 | 60.0091 | 0.57043 | 0.1951 | 93.5067 | 2.0985 | 0.23015 | 0.14974 | 5.0945 | 0.61455 | 0.18397 | 0 | 100 | 578.8 | 317 | 115.75 | 108.45 | 100.64 | 307.2 | 4 | 95.82 | 42.63 | 4 | 37.84 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.15 | 0 | 38.53 | 55 | 55 | 110.35 | 93.08 | 89.77 | 0 | 100.64 | 2.42 | 95.02 | 43.3 | 115.75 | 12.63 | 108.45 | 110 | 0 | 15706 | 83.38 | 117.4 | 221.81 | 215.69 | 221.12 | 0 | 36.45 | 50.62 | 15238 | 95.82 | 42.63 | 37.84 | 1.2 | 42.63 | 0 | 608 | 431.6 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 314.6 | 0 | 308.3 | 100.68 | 15706 | 15706 | 317
03/26/22 11:04:31.179 | 547.5104 | 1371.4063 | 53.6628 | 44.1144 | 9.5485 | 23.7702 | 51.0304 | 0 | 1784.9522 | 94.2326 | 85.6638 | 8.5687 | 23.8586 | 70.2705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9901 | 462.8101 | 459.6901 | 463.3901 | 410.9701 | 441.0601 | 418.0201 | 314.6501 | 0.57469 | 0.28268 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6590846.5443 | 7642841.0312 | 7642841.0312 | 62.4285 | 62.1306 | 1.0018 | 0.9979 | 686825.1336 | 890573.2815 | 461.9634 | 0.4921 | 0 | 0 | 23.7702 | 23.8586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016242 | 0.017876 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.4157 | 1367.8285 | 53.7633 | 44.1511 | 29.8561 | 1787.1325 | 84.9217 | 24.5889 | 461.7177 | 0.0058211 | 60.009 | 0.57051 | 0.19214 | 93.5176 | 2.1185 | 0.22741 | 0.1485 | 5.0865 | 0.60849 | 0.18171 | 0 | 100 | 579 | 317 | 115.88 | 108.45 | 100.7 | 308.8 | 4 | 95.88 | 42.65 | 4 | 37.86 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.23 | 0 | 38.54 | 55 | 55 | 110.43 | 93.12 | 89.79 | 0 | 100.7 | 2.42 | 95.06 | 43.32 | 115.88 | 12.57 | 108.45 | 110 | 0 | 15706 | 83.38 | 117.42 | 221.81 | 215.8 | 221.12 | 0 | 36.42 | 50.62 | 15243 | 95.88 | 42.65 | 37.86 | 1.16 | 42.65 | 0 | 608 | 427.9 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579 | 315.1 | 0 | 308.8 | 100.7 | 15706 | 15706 | 317
03/26/22 11:04:36.180 | 547.008 | 1370.9986 | 53.6627 | 44.1149 | 9.5478 | 23.6725 | 51.0324 | 0 | 1783.1717 | 94.2335 | 85.6654 | 8.5681 | 23.9898 | 70.2697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.99 | 462.81 | 459.69 | 463.39 | 410.97 | 441.06 | 418.02 | 314.65 | 0.57522 | 0.36682 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6584952.5478 | 7630540.7104 | 7630540.7104 | 62.4285 | 62.1306 | 1.0018 | 0.9979 | 686274.8843 | 889226.8931 | 461.9633 | 0.4921 | 0 | 0 | 23.6725 | 23.9898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01624 | 0.017881 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.3362 | 1367.8499 | 53.7602 | 44.1495 | 29.817 | 1787.1246 | 84.9334 | 24.582 | 461.7217 | 0.0058295 | 60.0088 | 0.5706 | 0.19008 | 93.5284 | 2.131 | 0.22474 | 0.14724 | 5.0916 | 0.60238 | 0.17927 | 0 | 100 | 578.2 | 316 | 115.9 | 108.45 | 100.56 | 307.5 | 4 | 95.9 | 42.64 | 4 | 37.85 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.25 | 0 | 38.53 | 55 | 55 | 110.48 | 93.14 | 89.79 | 0 | 100.56 | 2.42 | 95.07 | 43.31 | 115.93 | 12.54 | 108.45 | 110 | 0 | 15706 | 83.36 | 117.45 | 221.81 | 215.8 | 221.12 | 0 | 36.41 | 50.64 | 15248 | 95.91 | 42.63 | 37.84 | 1.19 | 42.63 | 0 | 607 | 431.5 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 312.4 | 0 | 306.2 | 100.57 | 15706 | 15706 | 318
03/26/22 11:04:41.179 | 546.4827 | 1369.9715 | 53.6616 | 44.1159 | 9.5458 | 23.2415 | 51.025 | 0 | 1782.9653 | 94.2362 | 85.6696 | 8.5665 | 25.1325 | 70.2594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9911 | 462.7801 | 459.6701 | 463.3801 | 410.9501 | 441.1101 | 418.0501 | 314.6501 | 0.57577 | 0.29228 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6578253.8281 | 7629551.4484 | 7629551.4484 | 62.4285 | 62.1305 | 1.0018 | 0.9979 | 685760.8299 | 889123.3169 | 461.9434 | 0.49212 | 0 | 0 | 23.2415 | 25.1325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017876 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.2642 | 1367.8576 | 53.7572 | 44.1479 | 29.7737 | 1787.0978 | 84.9447 | 24.5839 | 461.7256 | 0.005838 | 60.0087 | 0.57069 | 0.18805 | 93.5391 | 2.1361 | 0.22259 | 0.14605 | 5.1007 | 0.59694 | 0.17625 | 0 | 100 | 578.5 | 315 | 115.95 | 108.45 | 100.61 | 305.5 | 4 | 95.92 | 42.61 | 4 | 37.82 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.28 | 0 | 38.53 | 55 | 55 | 110.45 | 93.13 | 89.79 | 0 | 100.61 | 2.42 | 95.08 | 43.31 | 115.93 | 12.53 | 108.45 | 110 | 0 | 15706 | 83.36 | 117.45 | 221.81 | 215.8 | 221.12 | 0 | 36.43 | 50.72 | 15253 | 95.92 | 42.61 | 37.82 | 1.2 | 42.61 | 0 | 607 | 428.2 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5 | 314.2 | 0 | 308 | 100.61 | 15706 | 15706 | 316
03/26/22 11:04:46.180 | 546.8876 | 1372.4746 | 53.6596 | 44.1176 | 9.542 | 23.0899 | 51.0378 | 0 | 1787.8785 | 94.2429 | 85.6791 | 8.5638 | 25.365 | 70.2664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 462.75 | 459.66 | 463.37 | 410.95 | 441.21 | 418.17 | 314.68 | 0.5754 | 0.085711 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6582918.0798 | 7650022.495 | 7650022.495 | 62.4285 | 62.1304 | 1.0018 | 0.9979 | 686515.2688 | 891718.898 | 461.9267 | 0.4907 | 0 | 0 | 23.0899 | 25.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017876 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.1974 | 1367.8708 | 53.7545 | 44.1464 | 29.7292 | 1787.1012 | 84.9558 | 24.5879 | 461.7296 | 0.0058466 | 60.0086 | 0.57077 | 0.18464 | 93.5496 | 2.1512 | 0.22067 | 0.14489 | 5.1013 | 0.59174 | 0.17257 | 0 | 100 | 578.9 | 317 | 115.85 | 108.45 | 100.68 | 307.3 | 4 | 95.88 | 42.63 | 4 | 37.84 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.2 | 0 | 38.54 | 55 | 55 | 110.43 | 93.12 | 89.81 | 0 | 100.68 | 2.42 | 95.04 | 43.32 | 115.83 | 12.59 | 108.45 | 110 | 0 | 15706 | 83.36 | 117.45 | 221.81 | 215.8 | 221.24 | 0 | 36.45 | 50.72 | 15258 | 95.86 | 42.64 | 37.85 | 1.19 | 42.64 | 0 | 608 | 428.7 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 314.5 | 0 | 308.2 | 100.73 | 15706 | 15706 | 317
03/26/22 11:04:51.180 | 547.7682 | 1373.9609 | 53.6593 | 44.1188 | 9.5405 | 23.652 | 51.0426 | 0 | 1787.7237 | 94.2487 | 85.6856 | 8.5631 | 24.3022 | 70.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9971 | 462.7501 | 459.6601 | 463.3701 | 410.9501 | 441.2101 | 418.1701 | 314.6801 | 0.57448 | 0.28717 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6594101.5983 | 7645845.8571 | 7645845.8571 | 62.4285 | 62.1304 | 1.0018 | 0.9979 | 687757.8995 | 891493.8349 | 461.9267 | 0.4907 | 0 | 0 | 23.652 | 24.3022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017879 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.1427 | 1367.9006 | 53.7518 | 44.1449 | 29.6878 | 1787.1045 | 84.9669 | 24.5871 | 461.7335 | 0.0058551 | 60.0084 | 0.57085 | 0.18224 | 93.5602 | 2.1979 | 0.21889 | 0.14377 | 5.1015 | 0.58665 | 0.16875 | 0 | 100 | 578.9 | 316 | 115.83 | 108.45 | 100.68 | 308.4 | 4 | 95.86 | 42.65 | 4 | 37.86 | 43.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.23 | 0 | 38.55 | 55 | 55 | 110.45 | 93.13 | 89.83 | 0 | 100.68 | 2.42 | 95.06 | 43.33 | 115.83 | 12.59 | 108.45 | 110 | 0 | 15706 | 83.36 | 117.45 | 221.81 | 215.8 | 221.24 | 0 | 36.46 | 50.77 | 15263 | 95.86 | 42.65 | 37.86 | 1.18 | 42.65 | 0 | 608 | 428 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.1 | 314.6 | 0 | 308.4 | 100.71 | 15707 | 15706 | 316
03/26/22 11:04:56.180 | 546.7817 | 1371.6591 | 53.6596 | 44.1203 | 9.5393 | 23.87 | 51.0461 | 0 | 1788.2191 | 94.2576 | 85.6934 | 8.5642 | 23.8576 | 70.2821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0031 | 462.7401 | 459.6801 | 463.3801 | 410.9501 | 441.2701 | 418.2701 | 314.7201 | 0.57559 | 0.10184 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6582420.8132 | 7648496.5604 | 7648496.5604 | 62.4285 | 62.1303 | 1.0018 | 0.9979 | 686605.6866 | 891739.754 | 461.9334 | 0.4878 | 0 | 0 | 23.87 | 23.8576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017873 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.1045 | 1367.9371 | 53.7495 | 44.1435 | 29.6477 | 1787.1211 | 84.9774 | 24.5821 | 461.7376 | 0.0058639 | 60.0083 | 0.5709 | 0.17942 | 93.5704 | 2.2273 | 0.2177 | 0.14286 | 5.0952 | 0.58243 | 0.16466 | 0 | 100 | 578.9 | 316 | 115.88 | 108.45 | 100.68 | 307.4 | 4 | 95.87 | 42.65 | 4 | 37.86 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.23 | 0 | 38.55 | 54 | 54 | 110.48 | 93.13 | 89.79 | 0 | 100.68 | 2.42 | 95.06 | 43.33 | 115.88 | 12.58 | 108.45 | 110 | 0 | 15706 | 83.36 | 117.45 | 221.81 | 215.8 | 221.24 | 0 | 36.47 | 50.77 | 15268 | 95.87 | 42.65 | 37.86 | 1.24 | 42.65 | 0 | 608 | 428.3 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.9 | 313.1 | 0 | 306.8 | 100.68 | 15704 | 15706 | 317
03/26/22 11:05:01.179 | 545.7138 | 1369.058 | 53.6601 | 44.1214 | 9.5387 | 23.6471 | 51.0477 | 0 | 1787.094 | 94.263 | 85.6977 | 8.5652 | 24.4863 | 70.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0081 | 462.7401 | 459.7101 | 463.3801 | 410.8601 | 441.2701 | 418.3701 | 314.7001 | 0.57668 | -0.026968 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6569370.3313 | 7645300.8449 | 7645300.8449 | 62.4285 | 62.1302 | 1.0018 | 0.9979 | 685303.6252 | 891178.0511 | 461.9434 | 0.48346 | 0 | 0 | 23.6471 | 24.4863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017876 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 549.0602 | 1367.948 | 53.7474 | 44.1423 | 29.6065 | 1787.1222 | 84.9878 | 24.581 | 461.7417 | 0.0058726 | 60.0082 | 0.57097 | 0.17553 | 93.5805 | 2.2308 | 0.21671 | 0.14204 | 5.0953 | 0.57851 | 0.16036 | 0 | 100 | 578.3 | 317 | 115.9 | 108.47 | 100.63 | 307.8 | 4 | 95.9 | 42.63 | 4 | 37.84 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.28 | 0 | 38.53 | 53 | 53 | 110.6 | 93.21 | 89.73 | 0 | 100.63 | 2.42 | 95.08 | 43.31 | 115.93 | 12.56 | 108.47 | 110 | 0 | 15706 | 83.36 | 117.45 | 221.81 | 215.8 | 221.24 | 0 | 36.48 | 50.73 | 15273 | 95.91 | 42.63 | 37.84 | 1.26 | 42.63 | 0 | 608 | 430.1 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.3 | 313.6 | 0 | 307.4 | 100.57 | 15706 | 15706 | 316
03/26/22 11:05:06.179 | 544.1321 | 1365.1511 | 53.6621 | 44.1238 | 9.5383 | 23.519 | 51.043 | 0 | 1782.4853 | 94.2716 | 85.705 | 8.5666 | 24.2002 | 70.3424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 462.71 | 459.7 | 463.36 | 410.76 | 441.16 | 418.41 | 314.64 | 0.57824 | -0.032231 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6550217.5162 | 7626475.9633 | 7626475.9633 | 62.4285 | 62.1301 | 1.0018 | 0.9979 | 683347.8843 | 888878.7055 | 461.9234 | 0.48132 | 0 | 0 | 23.519 | 24.2002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017883 | 0.010636 | 0.004553 | 0.011584 | 0.0119 | 549.0264 | 1367.9621 | 53.7456 | 44.1411 | 29.5603 | 1787.1173 | 84.9978 | 24.5848 | 461.7456 | 0.0058811 | 60.0081 | 0.57102 | 0.17234 | 93.5904 | 2.2201 | 0.21598 | 0.14139 | 5.0959 | 0.57508 | 0.15653 | 0 | 100 | 578.6 | 316 | 115.95 | 108.49 | 100.63 | 306.3 | 4 | 95.92 | 42.63 | 4 | 37.84 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.35 | 0 | 38.53 | 53 | 53 | 110.78 | 93.28 | 89.71 | 0 | 100.63 | 2.42 | 95.12 | 43.31 | 115.95 | 12.57 | 108.49 | 110 | 0 | 15706 | 83.38 | 117.45 | 221.93 | 215.8 | 221.24 | 0 | 36.39 | 50.6 | 15278 | 95.92 | 42.63 | 37.84 | 1.24 | 42.63 | 0 | 608 | 431 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 313.5 | 0 | 307.2 | 100.47 | 15706 | 15706 | 317
03/26/22 11:05:11.179 | 543.7817 | 1364.5369 | 53.664 | 44.1256 | 9.5385 | 23.3841 | 51.0419 | 0 | 1780.8647 | 94.2765 | 85.709 | 8.5675 | 24.9981 | 70.3383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.994 | 462.71 | 459.71 | 463.36 | 410.69 | 441.09 | 418.39 | 314.59 | 0.57852 | -0.026572 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6545878.7821 | 7621499.7427 | 7621499.7427 | 62.4285 | 62.1301 | 1.0018 | 0.9979 | 682898.2938 | 888126.7525 | 461.9267 | 0.47987 | 0 | 0 | 23.3841 | 24.9981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.01789 | 0.010636 | 0.004553 | 0.011584 | 0.0119 | 548.9832 | 1367.9571 | 53.7438 | 44.1401 | 29.5153 | 1787.0826 | 85.0077 | 24.5868 | 461.7495 | 0.0058462 | 60.0079 | 0.57109 | 0.16922 | 93.6001 | 2.2275 | 0.21537 | 0.14084 | 5.1164 | 0.57189 | 0.15206 | 0 | 100 | 578 | 315 | 115.95 | 108.51 | 100.61 | 308.4 | 4 | 95.92 | 42.63 | 4 | 37.84 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.4 | 0 | 38.51 | 53 | 53 | 110.75 | 93.28 | 89.65 | 0 | 100.61 | 2.43 | 95.14 | 43.3 | 115.95 | 12.6 | 108.51 | 110 | 0 | 15706 | 83.38 | 117.45 | 221.93 | 215.8 | 221.24 | 0 | 36.36 | 50.54 | 15282 | 95.91 | 42.63 | 37.84 | 1.24 | 42.63 | 0 | 607 | 429.4 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 313.6 | 0 | 307.4 | 100.49 | 15706 | 15706 | 317
03/26/22 11:05:16.180 | 544.0379 | 1365.2027 | 53.6662 | 44.1278 | 9.5384 | 24.2197 | 51.045 | 0 | 1779.8016 | 94.2826 | 85.7153 | 8.5673 | 25.068 | 70.3193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.99 | 462.74 | 459.74 | 463.38 | 410.59 | 440.95 | 418.31 | 314.53 | 0.57814 | 0.092291 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6549453.3803 | 7615846.6198 | 7615846.6198 | 62.4285 | 62.13 | 1.0018 | 0.9979 | 683218.5508 | 887433.5436 | 461.9534 | 0.47912 | 0 | 0 | 24.2197 | 25.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017894 | 0.010636 | 0.004553 | 0.011584 | 0.0119 | 548.9311 | 1367.9276 | 53.7422 | 44.1392 | 29.4753 | 1787.035 | 85.0175 | 24.5856 | 461.7533 | 0.0057462 | 60.0078 | 0.57116 | 0.16541 | 93.6097 | 2.2373 | 0.21483 | 0.14037 | 5.1423 | 0.56886 | 0.14769 | 0 | 100 | 577.9 | 317 | 116 | 108.53 | 100.49 | 308.1 | 4 | 95.95 | 42.61 | 4 | 37.82 | 43.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.45 | 0 | 38.5 | 53 | 53 | 110.85 | 93.34 | 89.62 | 0 | 100.49 | 2.43 | 95.17 | 43.28 | 115.98 | 12.6 | 108.53 | 110 | 0 | 15706 | 83.38 | 117.45 | 221.93 | 215.91 | 221.24 | 0 | 36.26 | 50.43 | 15287 | 95.93 | 42.61 | 37.82 | 1.29 | 42.61 | 0 | 608 | 430.9 | 460.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.6 | 314.1 | 0 | 307.8 | 100.45 | 15706 | 15706 | 316
03/26/22 11:05:21.179 | 544.6983 | 1366.5652 | 53.6671 | 44.1292 | 9.538 | 26.1866 | 51.0523 | 0 | 1783.022 | 94.2866 | 85.7204 | 8.5662 | 24.8034 | 70.2755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9901 | 462.7401 | 459.7401 | 463.3801 | 410.5901 | 440.9501 | 418.3101 | 314.5301 | 0.57744 | 0.11537 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6558869.0727 | 7623289.2459 | 7623289.2459 | 62.4285 | 62.13 | 1.0018 | 0.9979 | 684076.1991 | 888421.0339 | 461.9534 | 0.47912 | 0 | 0 | 26.1866 | 24.8034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017885 | 0.010636 | 0.004553 | 0.011584 | 0.0119 | 548.8791 | 1367.8953 | 53.7407 | 44.1384 | 29.4537 | 1786.9815 | 85.027 | 24.5776 | 461.757 | 0.0056674 | 60.0077 | 0.57123 | 0.16268 | 93.6191 | 2.2145 | 0.21442 | 0.14001 | 5.1336 | 0.56615 | 0.1443 | 0 | 100 | 577.5 | 317 | 115.95 | 108.57 | 100.43 | 308.6 | 4 | 95.92 | 42.6 | 4 | 37.81 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.38 | 0 | 38.5 | 53 | 53 | 110.83 | 93.32 | 89.58 | 0 | 100.43 | 2.43 | 95.14 | 43.28 | 115.95 | 12.65 | 108.57 | 110 | 0 | 15706 | 83.38 | 117.45 | 221.93 | 215.91 | 221.24 | 0 | 36.14 | 50.29 | 15292 | 95.92 | 42.6 | 37.81 | 1.43 | 42.6 | 0 | 608 | 430.3 | 460.4 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 314.9 | 0 | 308.6 | 100.52 | 15705 | 15706 | 316
03/26/22 11:05:26.179 | 545.0906 | 1367.6233 | 53.6693 | 44.1315 | 9.5378 | 29.1845 | 51.0595 | 0 | 1787.1405 | 94.2958 | 85.731 | 8.5648 | 23.9076 | 70.3271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.99 | 462.75 | 459.76 | 463.39 | 410.5 | 440.86 | 418.23 | 314.47 | 0.57691 | -0.060887 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6566735.956 | 7644404.7533 | 7644404.7533 | 62.4285 | 62.1298 | 1.0018 | 0.9979 | 684585.0404 | 891196.2367 | 461.9667 | 0.47767 | 0 | 0 | 29.1845 | 23.9076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017891 | 0.010636 | 0.004553 | 0.011584 | 0.0119 | 548.8309 | 1367.8742 | 53.7393 | 44.1377 | 29.4477 | 1786.9268 | 85.0365 | 24.567 | 461.7606 | 0.0056749 | 60.0075 | 0.57129 | 0.16018 | 93.6284 | 2.1988 | 0.21404 | 0.13969 | 5.0787 | 0.56356 | 0.1415 | 0 | 100 | 577.8 | 316 | 115.93 | 108.59 | 100.5 | 304.8 | 4 | 95.91 | 42.61 | 4 | 37.82 | 44.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.35 | 0 | 38.5 | 53 | 53 | 110.78 | 93.3 | 89.39 | 0 | 100.5 | 2.43 | 95.12 | 43.28 | 115.93 | 12.69 | 108.59 | 110 | 0 | 15706 | 83.38 | 117.45 | 221.93 | 215.91 | 221.24 | 0 | 36.02 | 50.23 | 15297 | 95.9 | 42.61 | 37.81 | 1.51 | 42.61 | 0 | 608 | 427.7 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.8 | 311 | 0 | 304.8 | 100.49 | 15708 | 15706 | 316
03/26/22 11:05:31.179 | 545.1156 | 1367.4839 | 53.6713 | 44.132 | 9.5393 | 29.1221 | 51.0646 | 0 | 1787.0218 | 94.3012 | 85.7355 | 8.5656 | 24.4583 | 70.3552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9901 | 462.7501 | 459.7601 | 463.3901 | 410.5001 | 440.8601 | 418.2301 | 314.4701 | 0.57689 | -0.068973 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6566979.5709 | 7645266.8675 | 7645266.8675 | 62.4285 | 62.1298 | 1.0018 | 0.9979 | 684515.197 | 891136.3696 | 461.9667 | 0.47767 | 0 | 0 | 29.1221 | 24.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017881 | 0.010636 | 0.004553 | 0.011584 | 0.0119 | 548.7874 | 1367.8614 | 53.7379 | 44.137 | 29.4379 | 1786.8865 | 85.0458 | 24.5645 | 461.7641 | 0.0055528 | 60.0074 | 0.57136 | 0.15814 | 93.6377 | 2.1943 | 0.21371 | 0.13942 | 5.0487 | 0.56108 | 0.13855 | 0 | 100 | 578 | 316 | 116 | 108.59 | 100.52 | 305.6 | 4 | 95.95 | 42.63 | 4 | 37.84 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.4 | 0 | 38.51 | 53 | 53 | 110.85 | 93.34 | 89.23 | 0 | 100.52 | 2.43 | 95.14 | 43.3 | 116 | 12.64 | 108.59 | 110 | 0 | 15706 | 83.38 | 117.45 | 221.93 | 215.91 | 221.36 | 0 | 35.95 | 50.23 | 15302 | 95.95 | 42.63 | 37.84 | 1.54 | 42.63 | 0 | 608 | 426 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 312 | 0 | 305.7 | 100.52 | 15708 | 15706 | 317
03/26/22 11:05:36.179 | 545.4353 | 1367.9226 | 53.6739 | 44.1321 | 9.5418 | 28.8774 | 51.0797 | 0 | 1790.7532 | 94.3069 | 85.7397 | 8.5672 | 24.7835 | 70.3865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.993 | 462.75 | 459.77 | 463.39 | 410.24 | 440.61 | 418.03 | 314.3 | 0.57624 | -0.25333 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6570609.0012 | 7663012.9631 | 7663012.9631 | 62.4284 | 62.1297 | 1.0018 | 0.9979 | 684734.6743 | 892996.5022 | 461.97 | 0.47622 | 0 | 0 | 28.8774 | 24.7835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017886 | 0.010636 | 0.004553 | 0.011584 | 0.0119 | 548.7455 | 1367.8475 | 53.7367 | 44.1363 | 29.4262 | 1786.8923 | 85.0551 | 24.564 | 461.7672 | 0.0055593 | 60.0073 | 0.57141 | 0.15354 | 93.6467 | 2.1859 | 0.2134 | 0.13918 | 5.0526 | 0.55869 | 0.13702 | 0 | 100 | 577.4 | 317 | 116.03 | 108.59 | 100.42 | 306.5 | 4 | 95.95 | 42.64 | 4 | 37.85 | 44.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.35 | 0 | 38.53 | 53 | 53 | 110.83 | 93.32 | 89.11 | 0 | 100.42 | 2.42 | 95.12 | 43.31 | 116.03 | 12.64 | 108.59 | 110 | 0 | 15706 | 83.38 | 117.45 | 221.93 | 215.91 | 221.36 | 0 | 35.82 | 50.11 | 15307 | 95.95 | 42.64 | 37.85 | 1.65 | 42.64 | 0 | 608 | 427.3 | 460.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.4 | 314.6 | 0 | 308.4 | 100.42 | 15705 | 15706 | 317
03/26/22 11:05:41.180 | 547.2829 | 1372.2682 | 53.6772 | 44.1308 | 9.5464 | 29.3129 | 51.0729 | 0 | 1786.3302 | 94.3157 | 85.7457 | 8.5701 | 24.4882 | 70.3585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.999 | 462.7 | 459.72 | 463.35 | 410.11 | 440.38 | 417.84 | 314.17 | 0.57405 | 0.23819 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6593090.2595 | 7647051.1322 | 7647051.1322 | 62.4284 | 62.1297 | 1.0018 | 0.9979 | 686739.2635 | 890874.9689 | 461.9234 | 0.47699 | 0 | 0 | 29.3129 | 24.4882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017888 | 0.010636 | 0.004553 | 0.011584 | 0.0119 | 548.7156 | 1367.8624 | 53.7354 | 44.1357 | 29.415 | 1786.8824 | 85.0643 | 24.5662 | 461.7699 | 0.0055651 | 60.0071 | 0.57146 | 0.15171 | 93.6558 | 2.2045 | 0.21312 | 0.13897 | 5.0516 | 0.55635 | 0.13572 | 0 | 100 | 577.4 | 315 | 116 | 108.59 | 100.42 | 305.4 | 4 | 95.95 | 42.63 | 4 | 37.84 | 44.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.35 | 0 | 38.51 | 53 | 53 | 110.85 | 93.34 | 88.99 | 0 | 100.42 | 2.43 | 95.12 | 43.3 | 115.98 | 12.66 | 108.59 | 110 | 0 | 15706 | 83.38 | 117.42 | 221.93 | 215.91 | 221.36 | 0 | 35.64 | 49.99 | 15312 | 95.93 | 42.63 | 37.84 | 1.7 | 42.63 | 0 | 607 | 430.7 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5 | 312.3 | 0 | 306.1 | 100.43 | 15703 | 15706 | 315
03/26/22 11:05:46.179 | 546.8941 | 1370.6166 | 53.6786 | 44.1301 | 9.5485 | 29.741 | 51.0655 | 0 | 1783.8426 | 94.3204 | 85.7488 | 8.5716 | 24.2936 | 70.3721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9991 | 462.7001 | 459.7201 | 463.3501 | 410.1101 | 440.3801 | 417.8401 | 314.1701 | 0.57446 | 0.31612 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6588925.2968 | 7636738.0291 | 7636738.0291 | 62.4284 | 62.1296 | 1.0018 | 0.9979 | 686083.0063 | 889549.0138 | 461.9234 | 0.47699 | 0 | 0 | 29.741 | 24.2936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017897 | 0.010636 | 0.004553 | 0.011584 | 0.0119 | 548.6885 | 1367.8801 | 53.7342 | 44.1351 | 29.4074 | 1786.8602 | 85.0735 | 24.5672 | 461.7722 | 0.0055701 | 60.007 | 0.5715 | 0.15106 | 93.6648 | 2.2138 | 0.21282 | 0.13876 | 5.0561 | 0.55391 | 0.1348 | 0 | 100 | 577.3 | 318 | 115.95 | 108.57 | 100.4 | 307 | 4 | 95.93 | 42.63 | 4 | 37.84 | 44.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.38 | 0 | 38.51 | 53 | 53 | 110.85 | 93.34 | 88.89 | 0 | 100.45 | 2.43 | 95.13 | 43.3 | 115.95 | 12.66 | 108.57 | 110 | 0 | 15706 | 83.38 | 117.4 | 221.93 | 215.91 | 221.36 | 0 | 35.49 | 49.95 | 15317 | 95.91 | 42.63 | 37.84 | 1.68 | 42.63 | 0 | 607 | 426.5 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 311.9 | 0 | 305.7 | 100.35 | 15705 | 15706 | 317
03/26/22 11:05:51.179 | 545.482 | 1366.6736 | 53.6802 | 44.1289 | 9.5513 | 29.9559 | 51.0698 | 0 | 1780.7615 | 94.3267 | 85.7519 | 8.5748 | 23.3832 | 70.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 462.73 | 459.7 | 463.36 | 409.97 | 440.07 | 417.48 | 314.02 | 0.57567 | 0.24235 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6572092.4135 | 7625309.4774 | 7625309.4774 | 62.4284 | 62.1296 | 1.0018 | 0.9979 | 684109.1917 | 888012.093 | 461.93 | 0.48276 | 0 | 0 | 29.9559 | 23.3832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016237 | 0.017903 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.6587 | 1367.8905 | 53.7331 | 44.1346 | 29.3985 | 1786.8432 | 85.0826 | 24.5672 | 461.774 | 0.005574 | 60.0069 | 0.57154 | 0.14988 | 93.6737 | 2.2098 | 0.21253 | 0.13856 | 5.0685 | 0.55141 | 0.13466 | 0 | 100 | 577.1 | 317 | 116 | 108.57 | 100.37 | 306.7 | 4 | 95.93 | 42.63 | 4 | 37.84 | 44.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.38 | 0 | 38.5 | 53 | 53 | 110.9 | 93.36 | 88.8 | 0 | 100.37 | 2.43 | 95.13 | 43.28 | 116 | 12.62 | 108.57 | 110 | 0 | 15706 | 83.38 | 117.37 | 221.93 | 215.91 | 221.36 | 0 | 35.33 | 49.85 | 15322 | 95.95 | 42.63 | 37.84 | 1.78 | 42.63 | 0 | 607 | 429.3 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 311.4 | 0 | 305.2 | 100.4 | 15706 | 15706 | 315
03/26/22 11:05:56.179 | 545.4004 | 1366.2659 | 53.6807 | 44.1279 | 9.5528 | 29.8479 | 51.0673 | 0 | 1777.9745 | 94.3298 | 85.7528 | 8.577 | 23.3858 | 70.3927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0001 | 462.7301 | 459.7001 | 463.3601 | 409.9701 | 440.0701 | 417.4801 | 314.0201 | 0.57576 | 0.35535 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6571010.7483 | 7615382.2216 | 7615382.2216 | 62.4284 | 62.1295 | 1.0018 | 0.9979 | 683905.0964 | 886622.2086 | 461.9301 | 0.48276 | 0 | 0 | 29.8479 | 23.3858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017912 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.6231 | 1367.883 | 53.7319 | 44.134 | 29.3888 | 1786.8454 | 85.0917 | 24.5631 | 461.7755 | 0.0055772 | 60.0068 | 0.57158 | 0.14693 | 93.6826 | 2.213 | 0.21223 | 0.13836 | 5.0647 | 0.54886 | 0.13489 | 0 | 100 | 576.6 | 318 | 116 | 108.57 | 100.35 | 307.8 | 4 | 95.95 | 42.61 | 4 | 37.82 | 44.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.45 | 0 | 38.5 | 53 | 53 | 110.93 | 93.37 | 88.74 | 0 | 100.35 | 2.43 | 95.17 | 43.28 | 116 | 12.62 | 108.57 | 110 | 0 | 15706 | 83.38 | 117.37 | 221.93 | 215.91 | 221.36 | 0 | 35.16 | 49.79 | 15328 | 95.95 | 42.61 | 37.82 | 1.97 | 42.61 | 0 | 607 | 427 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 314.1 | 0 | 307.8 | 100.35 | 15706 | 15706 | 316
03/26/22 11:06:01.179 | 545.9595 | 1367.4839 | 53.6808 | 44.1268 | 9.554 | 29.2375 | 51.0677 | 0 | 1778.8622 | 94.3324 | 85.7534 | 8.579 | 24.551 | 70.4014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0001 | 462.7301 | 459.7001 | 463.3601 | 409.9701 | 440.0701 | 417.4801 | 314.0201 | 0.57517 | 0.34632 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6577206.7372 | 7622243.6821 | 7622243.6821 | 62.4284 | 62.1295 | 1.0018 | 0.9979 | 684514.7866 | 887064.778 | 461.9301 | 0.48276 | 0 | 0 | 29.2375 | 24.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017898 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.5851 | 1367.8685 | 53.7307 | 44.1334 | 29.3738 | 1786.8426 | 85.1008 | 24.5692 | 461.777 | 0.0055805 | 60.0068 | 0.57163 | 0.14349 | 93.6915 | 2.2069 | 0.21194 | 0.13815 | 5.0691 | 0.54623 | 0.1351 | 0 | 100 | 577.1 | 314 | 116.08 | 108.59 | 100.26 | 306.5 | 4 | 96 | 42.61 | 4 | 37.82 | 44.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.48 | 0 | 38.5 | 53 | 53 | 110.98 | 93.4 | 88.66 | 0 | 100.26 | 2.43 | 95.18 | 43.28 | 116.1 | 12.59 | 108.59 | 110 | 0 | 15706 | 83.38 | 117.35 | 221.93 | 216.02 | 221.36 | 0 | 35 | 49.75 | 15333 | 96 | 42.61 | 37.82 | 2.05 | 42.61 | 0 | 607 | 429.5 | 460.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 312.8 | 0 | 306.5 | 100.37 | 15705 | 15706 | 314
03/26/22 11:06:06.179 | 545.9736 | 1367.0039 | 53.6815 | 44.1238 | 9.5576 | 28.4582 | 51.0729 | 0 | 1790.5519 | 94.3377 | 85.7547 | 8.5831 | 25.8106 | 70.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0001 | 462.6701 | 459.5901 | 463.2601 | 410.0101 | 439.6701 | 417.1201 | 313.8601 | 0.57486 | -0.38895 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6576683.1149 | 7677421.1507 | 7677421.1507 | 62.4284 | 62.1295 | 1.0018 | 0.9979 | 684274.4851 | 892893.8605 | 461.8401 | 0.48718 | 0 | 0 | 28.4582 | 25.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016241 | 0.017888 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.5539 | 1367.8675 | 53.7296 | 44.1328 | 29.3609 | 1786.8953 | 85.1098 | 24.5759 | 461.7777 | 0.0055819 | 60.0067 | 0.57167 | 0.13791 | 93.7003 | 2.2069 | 0.21163 | 0.13794 | 5.0433 | 0.54354 | 0.13536 | 0 | 100 | 577 | 317 | 116 | 108.61 | 100.49 | 305.7 | 4 | 95.95 | 42.63 | 4 | 37.84 | 44.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.38 | 0 | 38.51 | 53 | 53 | 110.9 | 93.36 | 88.64 | 0 | 100.37 | 2.43 | 95.14 | 43.3 | 116 | 12.66 | 108.61 | 110 | 0 | 15706 | 83.38 | 117.33 | 221.93 | 216.02 | 221.36 | 0 | 34.86 | 49.79 | 15337 | 95.95 | 42.63 | 37.84 | 2.09 | 42.63 | 0 | 607 | 430.5 | 460 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 311.9 | 0 | 305.7 | 100.35 | 15709 | 15706 | 317
03/26/22 11:06:11.178 | 545.0297 | 1364.315 | 53.6822 | 44.1223 | 9.5599 | 28.8382 | 51.0696 | 0 | 1795.8987 | 94.3399 | 85.7539 | 8.586 | 25.1164 | 70.3804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.999 | 462.65 | 459.55 | 463.23 | 410.02 | 439.59 | 417.07 | 313.84 | 0.57582 | -0.85571 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6565639.6205 | 7702201.4642 | 7702201.4642 | 62.4284 | 62.1295 | 1.0018 | 0.9979 | 682928.4938 | 895560.2648 | 461.81 | 0.48938 | 0 | 0 | 28.8382 | 25.1164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016245 | 0.017881 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.5206 | 1367.8586 | 53.7284 | 44.1321 | 29.35 | 1786.9729 | 85.1187 | 24.5791 | 461.7779 | 0.0055824 | 60.0066 | 0.57171 | 0.13052 | 93.7091 | 2.2181 | 0.21131 | 0.13772 | 5.0739 | 0.54076 | 0.13543 | 0 | 100 | 577.5 | 316 | 115.9 | 108.61 | 100.43 | 306.4 | 4 | 95.91 | 42.61 | 4 | 37.82 | 44.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.3 | 0 | 38.5 | 53 | 53 | 110.78 | 93.3 | 88.64 | 0 | 100.4 | 2.42 | 95.09 | 43.28 | 115.9 | 12.71 | 108.61 | 110 | 0 | 15706 | 83.36 | 117.33 | 221.93 | 216.02 | 221.36 | 0 | 34.75 | 49.82 | 15342 | 95.9 | 42.61 | 37.82 | 2.07 | 42.61 | 0 | 607 | 429.7 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.2 | 312.7 | 0 | 306.5 | 100.38 | 15707 | 15706 | 313
03/26/22 11:06:16.179 | 544.9648 | 1364.2841 | 53.6832 | 44.1209 | 9.5623 | 29.5658 | 51.0607 | 0 | 1794.2833 | 94.3415 | 85.7525 | 8.5891 | 23.8682 | 70.3816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9991 | 462.6501 | 459.5501 | 463.2301 | 410.0201 | 439.5901 | 417.0701 | 313.8401 | 0.57589 | -0.81657 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6565301.0743 | 7698777.6938 | 7698777.6938 | 62.4285 | 62.1295 | 1.0018 | 0.9979 | 682708.8764 | 895035.4191 | 461.8101 | 0.48938 | 0 | 0 | 29.5658 | 23.8682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016242 | 0.017885 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.4874 | 1367.8497 | 53.7272 | 44.1315 | 29.3422 | 1787.0306 | 85.1276 | 24.5737 | 461.778 | 0.0055826 | 60.0065 | 0.57176 | 0.12407 | 93.7179 | 2.2292 | 0.21098 | 0.13749 | 5.0978 | 0.5379 | 0.13545 | 0 | 100 | 577.7 | 317 | 115.95 | 108.61 | 100.47 | 307.8 | 4 | 95.92 | 42.61 | 4 | 37.82 | 44.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.35 | 0 | 38.51 | 53 | 53 | 110.88 | 93.35 | 88.64 | 0 | 100.47 | 2.43 | 95.12 | 43.28 | 115.95 | 12.69 | 108.61 | 110 | 0 | 15706 | 83.36 | 117.33 | 221.93 | 216.02 | 221.36 | 0 | 34.62 | 49.84 | 15347 | 95.92 | 42.61 | 37.82 | 1.91 | 42.61 | 0 | 607 | 428.5 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 313.7 | 0 | 307.4 | 100.47 | 15707 | 15706 | 318
03/26/22 11:06:21.179 | 547.7018 | 1370.2296 | 53.6845 | 44.1192 | 9.5653 | 28.9967 | 51.0801 | 0 | 1785.9173 | 94.342 | 85.7497 | 8.5924 | 25.0376 | 70.3989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 462.63 | 459.52 | 463.21 | 410.05 | 439.59 | 417.05 | 313.84 | 0.57301 | 0.050535 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6597954.4327 | 7664945.976 | 7664945.976 | 62.4285 | 62.1295 | 1.0018 | 0.9979 | 685888.9923 | 890583.5017 | 461.7867 | 0.49085 | 0 | 0 | 28.9967 | 25.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017893 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.4704 | 1367.8732 | 53.7261 | 44.1308 | 29.3341 | 1787.0268 | 85.1365 | 24.5678 | 461.778 | 0.0055828 | 60.0064 | 0.57178 | 0.12327 | 93.7266 | 2.2318 | 0.21063 | 0.13724 | 5.0983 | 0.53497 | 0.13545 | 0 | 100 | 577.9 | 315 | 115.98 | 108.61 | 100.47 | 306.5 | 4 | 95.93 | 42.63 | 4 | 37.84 | 44.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.4 | 0 | 38.51 | 53 | 53 | 110.93 | 93.37 | 88.6 | 0 | 100.47 | 2.43 | 95.16 | 43.3 | 115.98 | 12.68 | 108.61 | 110 | 0 | 15706 | 83.34 | 117.33 | 221.93 | 216.02 | 221.36 | 0 | 34.53 | 49.94 | 15353 | 95.93 | 42.63 | 37.84 | 1.86 | 42.63 | 0 | 607 | 427.2 | 459.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.9 | 312.8 | 0 | 306.5 | 100.5 | 15708 | 15706 | 315
03/26/22 11:06:26.179 | 548.0205 | 1370.9676 | 53.6846 | 44.1184 | 9.5662 | 29.0854 | 51.0793 | 0 | 1785.9896 | 94.3413 | 85.7478 | 8.5935 | 25.0052 | 70.3907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 462.62 | 459.52 | 463.17 | 410.03 | 439.5 | 417.01 | 313.81 | 0.57262 | 0.11783 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6601844.9148 | 7663573.5016 | 7663573.5016 | 62.4285 | 62.1295 | 1.0018 | 0.9979 | 686232.5696 | 890334.082 | 461.77 | 0.48726 | 0 | 0 | 29.0854 | 25.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017876 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.4499 | 1367.8886 | 53.7249 | 44.1301 | 29.3257 | 1786.9686 | 85.1452 | 24.5649 | 461.7783 | 0.0055833 | 60.0064 | 0.57181 | 0.12529 | 93.7351 | 2.2436 | 0.21027 | 0.13698 | 5.0495 | 0.53205 | 0.1354 | 0 | 100 | 576.4 | 317 | 116.03 | 108.61 | 100.33 | 306.6 | 4 | 95.96 | 42.6 | 4 | 37.81 | 44.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.4 | 0 | 38.49 | 53 | 53 | 110.93 | 93.39 | 88.5 | 0 | 100.33 | 2.43 | 95.14 | 43.27 | 116.03 | 12.65 | 108.61 | 110 | 0 | 15706 | 83.32 | 117.33 | 222.05 | 216.02 | 221.36 | 0 | 34.47 | 50 | 15357 | 95.96 | 42.6 | 37.81 | 1.77 | 42.6 | 0 | 607 | 427.6 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 312.8 | 0 | 306.6 | 100.24 | 15709 | 15706 | 317
03/26/22 11:06:31.178 | 548.113 | 1370.7611 | 53.6842 | 44.1176 | 9.5666 | 28.9771 | 51.0671 | 0 | 1791.8112 | 94.3401 | 85.7457 | 8.5944 | 25.1345 | 70.3717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 462.62 | 459.52 | 463.17 | 410.03 | 439.5 | 417.01 | 313.81 | 0.57253 | -0.19834 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6602948.8982 | 7688947.4484 | 7688947.4484 | 62.4285 | 62.1295 | 1.0018 | 0.9979 | 686315.2539 | 893178.261 | 461.77 | 0.48726 | 0 | 0 | 28.9771 | 25.1345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017877 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.4313 | 1367.9065 | 53.7237 | 44.1293 | 29.3138 | 1786.9324 | 85.1538 | 24.5659 | 461.7785 | 0.0055837 | 60.0063 | 0.57183 | 0.12626 | 93.7437 | 2.2536 | 0.20989 | 0.1367 | 4.9906 | 0.52906 | 0.13535 | 0 | 100 | 577.3 | 316 | 115.9 | 108.59 | 100.4 | 307.3 | 4 | 95.9 | 42.6 | 4 | 37.81 | 44.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.3 | 0 | 38.49 | 53 | 53 | 110.83 | 93.32 | 88.4 | 0 | 100.4 | 2.43 | 95.09 | 43.27 | 115.88 | 12.71 | 108.59 | 110 | 0 | 15706 | 83.32 | 117.33 | 222.05 | 216.02 | 221.36 | 0 | 34.43 | 50.12 | 15362 | 95.88 | 42.6 | 37.81 | 1.73 | 42.6 | 0 | 607 | 428.9 | 459.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 313.6 | 0 | 307.3 | 100.4 | 15704 | 15706 | 316
03/26/22 11:06:36.178 | 547.5019 | 1369.4348 | 53.684 | 44.1166 | 9.5674 | 28.7613 | 51.0659 | 0 | 1795.4755 | 94.339 | 85.7431 | 8.596 | 25.6734 | 70.3754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.999 | 462.56 | 459.48 | 463.12 | 410.16 | 439.51 | 417.13 | 313.87 | 0.57328 | -0.5675 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6595334.1174 | 7709932.4923 | 7709932.4923 | 62.4285 | 62.1295 | 1.0018 | 0.9979 | 685491.1738 | 895350.8468 | 461.72 | 0.48514 | 0 | 0 | 28.7613 | 25.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017865 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.4095 | 1367.9177 | 53.7225 | 44.1286 | 29.2977 | 1786.9425 | 85.1624 | 24.5739 | 461.7785 | 0.0055838 | 60.0063 | 0.57186 | 0.12362 | 93.7521 | 2.2562 | 0.2095 | 0.1364 | 5.0061 | 0.52602 | 0.13534 | 0 | 100 | 577.3 | 316 | 115.88 | 108.57 | 100.37 | 304.5 | 4 | 95.88 | 42.61 | 4 | 37.82 | 44.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.23 | 0 | 38.5 | 53 | 53 | 110.73 | 93.27 | 88.38 | 0 | 100.37 | 2.42 | 95.06 | 43.28 | 115.85 | 12.7 | 108.57 | 110 | 0 | 15706 | 83.32 | 117.33 | 222.05 | 216.02 | 221.36 | 0 | 34.37 | 50.16 | 15367 | 95.87 | 42.61 | 37.81 | 1.68 | 42.61 | 0 | 607 | 428.9 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 313.2 | 0 | 306.9 | 100.47 | 15704 | 15706 | 318
03/26/22 11:06:41.179 | 548.7876 | 1372.3559 | 53.6844 | 44.115 | 9.5694 | 29.5423 | 51.0514 | 0 | 1793.2098 | 94.338 | 85.7395 | 8.5985 | 24.0003 | 70.3605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 462.44 | 459.41 | 463 | 410.28 | 439.62 | 417.45 | 313.94 | 0.57206 | -0.23312 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6611504.1958 | 7700539.9967 | 7700539.9967 | 62.4285 | 62.1296 | 1.0018 | 0.9979 | 686953.3708 | 894221.5706 | 461.6167 | 0.47803 | 0 | 0 | 29.5423 | 24.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.01787 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.3989 | 1367.9567 | 53.7213 | 44.1278 | 29.2864 | 1786.9785 | 85.1709 | 24.5758 | 461.7786 | 0.0055839 | 60.0063 | 0.57188 | 0.12125 | 93.7605 | 2.2717 | 0.20906 | 0.13608 | 5.0334 | 0.52298 | 0.13531 | 0 | 100 | 577.1 | 316 | 115.88 | 108.55 | 100.37 | 306.9 | 4 | 95.88 | 42.6 | 4 | 37.81 | 44.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.23 | 0 | 38.5 | 53 | 53 | 110.75 | 93.27 | 88.4 | 0 | 100.37 | 2.42 | 95.06 | 43.28 | 115.85 | 12.68 | 108.55 | 110 | 0 | 15706 | 83.32 | 117.33 | 222.05 | 216.02 | 221.36 | 0 | 34.34 | 50.24 | 15372 | 95.87 | 42.61 | 37.82 | 1.62 | 42.61 | 0 | 607 | 427.7 | 459.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.2 | 311.6 | 0 | 305.4 | 100.38 | 15706 | 15706 | 314
03/26/22 11:06:46.179 | 548.3116 | 1370.1418 | 53.6851 | 44.1138 | 9.5713 | 29.0891 | 51.0552 | 0 | 1791.517 | 94.3365 | 85.7359 | 8.6006 | 24.6142 | 70.3606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 462.44 | 459.41 | 463 | 410.28 | 439.62 | 417.45 | 313.94 | 0.57256 | -0.24566 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6605353.9809 | 7695443.2586 | 7695443.2586 | 62.4285 | 62.1296 | 1.0018 | 0.9979 | 686253.2402 | 893390.6831 | 461.6167 | 0.47803 | 0 | 0 | 29.0891 | 24.6142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017867 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.3838 | 1367.9791 | 53.72 | 44.1271 | 29.2724 | 1787.0181 | 85.1793 | 24.5802 | 461.7782 | 0.0055832 | 60.0062 | 0.5719 | 0.11781 | 93.7688 | 2.2732 | 0.20861 | 0.13575 | 5.0409 | 0.51984 | 0.13564 | 0 | 100 | 577.8 | 317 | 115.9 | 108.53 | 100.49 | 305.1 | 4 | 95.9 | 42.61 | 4 | 37.82 | 44.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.25 | 0 | 38.5 | 53 | 53 | 110.8 | 93.31 | 88.4 | 0 | 100.49 | 2.42 | 95.07 | 43.28 | 115.9 | 12.63 | 108.53 | 110 | 0 | 15706 | 83.32 | 117.33 | 222.05 | 216.02 | 221.36 | 0 | 34.26 | 50.18 | 15377 | 95.9 | 42.61 | 37.82 | 1.52 | 42.61 | 0 | 606 | 430.9 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.7 | 313.3 | 0 | 307 | 100.47 | 15708 | 15706 | 318
03/26/22 11:06:51.178 | 547.4803 | 1368.2632 | 53.6866 | 44.1114 | 9.5752 | 29.8026 | 51.0611 | 0 | 1790.1132 | 94.3313 | 85.7244 | 8.6069 | 23.8709 | 70.3919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 462.3901 | 459.3901 | 462.9701 | 410.2701 | 439.6501 | 417.6301 | 313.9601 | 0.57346 | -0.35606 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6595967.9272 | 7694592.4389 | 7694592.4389 | 62.4285 | 62.1297 | 1.0018 | 0.9979 | 684904.6226 | 892679.647 | 461.5834 | 0.47518 | 0 | 0 | 29.8026 | 23.8709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017866 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.3618 | 1367.9884 | 53.7188 | 44.1262 | 29.2613 | 1787.0688 | 85.1876 | 24.582 | 461.7778 | 0.0055823 | 60.0062 | 0.57193 | 0.11264 | 93.777 | 2.2691 | 0.20811 | 0.13538 | 5.0382 | 0.51663 | 0.13607 | 0 | 100 | 577.3 | 317 | 115.75 | 108.53 | 100.38 | 307.7 | 4 | 95.82 | 42.6 | 4 | 37.81 | 44.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.18 | 0 | 38.49 | 53 | 53 | 110.78 | 93.3 | 88.36 | 0 | 100.38 | 2.42 | 95.03 | 43.27 | 115.75 | 12.71 | 108.53 | 110 | 0 | 15706 | 83.32 | 117.33 | 222.05 | 216.02 | 221.36 | 0 | 34.14 | 50.21 | 15382 | 95.82 | 42.6 | 37.81 | 1.45 | 42.6 | 0 | 607 | 430.7 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.6 | 312.6 | 0 | 306.4 | 100.45 | 15705 | 15706 | 315
03/26/22 11:06:56.179 | 547.6714 | 1368.5316 | 53.687 | 44.1104 | 9.5766 | 30.1766 | 51.0601 | 0 | 1786.5263 | 94.3274 | 85.7162 | 8.6112 | 23.0765 | 70.3911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 462.3901 | 459.3901 | 462.9701 | 410.2701 | 439.6501 | 417.6301 | 313.9601 | 0.57326 | -0.15895 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6598595.9361 | 7682072.3604 | 7682072.3604 | 62.4285 | 62.1297 | 1.0018 | 0.9979 | 685038.9422 | 890892.1822 | 461.5834 | 0.47518 | 0 | 0 | 30.1766 | 23.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017878 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.3378 | 1367.9865 | 53.7175 | 44.1254 | 29.2571 | 1787.0489 | 85.1957 | 24.5695 | 461.7771 | 0.0055808 | 60.0062 | 0.57196 | 0.11076 | 93.7851 | 2.2685 | 0.20755 | 0.13497 | 5.0332 | 0.5133 | 0.13673 | 0 | 100 | 576.8 | 315 | 115.78 | 108.51 | 100.37 | 305.2 | 4 | 95.83 | 42.58 | 4 | 37.79 | 43.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.25 | 0 | 38.48 | 53 | 53 | 110.78 | 93.3 | 88.28 | 0 | 100.37 | 2.43 | 95.07 | 43.26 | 115.85 | 12.65 | 108.51 | 110 | 0 | 15706 | 83.32 | 117.33 | 222.05 | 216.02 | 221.36 | 0 | 34.19 | 50.41 | 15387 | 95.86 | 42.56 | 37.78 | 1.43 | 42.56 | 0 | 607 | 427.6 | 459.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.3 | 312.7 | 0 | 306.5 | 100.4 | 15707 | 15706 | 316
03/26/22 11:07:01.179 | 547.2411 | 1367.2878 | 53.6871 | 44.1093 | 9.5778 | 29.3566 | 51.0655 | 0 | 1783.6723 | 94.3218 | 85.7067 | 8.6151 | 24.127 | 70.4068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.004 | 462.39 | 459.39 | 462.97 | 410.27 | 439.65 | 417.63 | 313.96 | 0.57371 | -0.13724 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6592687.3009 | 7674488.6424 | 7674488.6424 | 62.4285 | 62.1298 | 1.0018 | 0.9979 | 684416.3289 | 889470.3617 | 461.5833 | 0.47518 | 0 | 0 | 29.3566 | 24.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017885 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.306 | 1367.9715 | 53.7161 | 44.1245 | 29.2464 | 1786.9808 | 85.2038 | 24.5696 | 461.7765 | 0.0055794 | 60.0062 | 0.572 | 0.11022 | 93.7931 | 2.2641 | 0.20694 | 0.13453 | 4.9951 | 0.50983 | 0.13738 | 0 | 100 | 577.1 | 317 | 115.88 | 108.51 | 100.37 | 305 | 4 | 95.9 | 42.58 | 4 | 37.79 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.3 | 0 | 38.46 | 53 | 53 | 110.83 | 93.32 | 88.19 | 0 | 100.37 | 2.43 | 95.09 | 43.26 | 115.9 | 12.61 | 108.51 | 110 | 0 | 15706 | 83.32 | 117.35 | 222.05 | 216.02 | 221.36 | 0 | 34.31 | 50.62 | 15392 | 95.9 | 42.58 | 37.79 | 1.38 | 42.58 | 0 | 607 | 426 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.5 | 312.3 | 0 | 306.1 | 100.26 | 15707 | 15706 | 316
03/26/22 11:07:06.178 | 547.0569 | 1366.8027 | 53.6855 | 44.1075 | 9.578 | 29.9699 | 51.0913 | 0 | 1777.7526 | 94.3103 | 85.6923 | 8.618 | 23.3885 | 70.4423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0051 | 462.2701 | 459.3401 | 462.9001 | 410.0801 | 439.5601 | 417.7901 | 313.8601 | 0.57372 | 0.14782 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6591006.1702 | 7650725.1183 | 7650725.1183 | 62.4285 | 62.13 | 1.0018 | 0.9979 | 684173.5686 | 886520.5165 | 461.5034 | 0.46876 | 0 | 0 | 29.9699 | 23.3885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017894 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.2769 | 1367.9649 | 53.7147 | 44.1235 | 29.2388 | 1786.8838 | 85.2118 | 24.5658 | 461.7753 | 0.0055768 | 60.0061 | 0.57204 | 0.11176 | 93.8011 | 2.2658 | 0.2063 | 0.13407 | 5.004 | 0.50616 | 0.13841 | 0 | 100 | 576.6 | 317 | 115.93 | 108.51 | 100.28 | 307.4 | 4 | 95.91 | 42.58 | 4 | 37.79 | 43.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.33 | 0 | 38.46 | 53 | 53 | 110.88 | 93.35 | 88.13 | 0 | 100.28 | 2.43 | 95.11 | 43.25 | 115.93 | 12.6 | 108.51 | 110 | 0 | 15706 | 83.34 | 117.35 | 222.05 | 216.02 | 221.36 | 0 | 34.32 | 50.62 | 15397 | 95.91 | 42.56 | 37.78 | 1.37 | 42.56 | 0 | 607 | 427.8 | 459.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.5 | 313.7 | 0 | 307.4 | 100.26 | 15707 | 15706 | 317
03/26/22 11:07:11.178 | 546.7484 | 1366.2814 | 53.6839 | 44.1063 | 9.5775 | 29.6563 | 51.0717 | 0 | 1777.0714 | 94.3054 | 85.6864 | 8.619 | 23.7841 | 70.4183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.005 | 462.27 | 459.34 | 462.9 | 410.08 | 439.56 | 417.79 | 313.86 | 0.57405 | 0.11508 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6587053.6522 | 7649180.1566 | 7649180.1566 | 62.4285 | 62.13 | 1.0018 | 0.9979 | 683809.3556 | 886217.4514 | 461.5034 | 0.46876 | 0 | 0 | 29.6563 | 23.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.01789 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.2512 | 1367.9714 | 53.7133 | 44.1226 | 29.23 | 1786.8445 | 85.2197 | 24.5643 | 461.7739 | 0.0055738 | 60.0061 | 0.57207 | 0.1107 | 93.8089 | 2.2592 | 0.20559 | 0.13358 | 5.0532 | 0.50237 | 0.13988 | 0 | 100 | 576.3 | 318 | 115.93 | 108.51 | 100.23 | 306.3 | 4 | 95.91 | 42.56 | 4 | 37.78 | 43.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.33 | 0 | 38.46 | 53 | 53 | 110.85 | 93.34 | 88.17 | 0 | 100.23 | 2.43 | 95.11 | 43.25 | 115.9 | 12.61 | 108.51 | 110 | 0 | 15706 | 83.34 | 117.35 | 222.05 | 216.02 | 221.36 | 0 | 34.29 | 50.52 | 15402 | 95.9 | 42.56 | 37.78 | 1.35 | 42.56 | 0 | 607 | 430.9 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 312.8 | 0 | 306.6 | 100.24 | 15706 | 15706 | 316
03/26/22 11:07:16.179 | 547.9112 | 1369.1354 | 53.6802 | 44.1036 | 9.5766 | 29.4026 | 51.0663 | 0 | 1778.8674 | 94.2978 | 85.6761 | 8.6217 | 24.087 | 70.4051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9991 | 462.2201 | 459.3001 | 462.8601 | 410.0601 | 439.5701 | 417.7701 | 313.8101 | 0.57274 | 0.15596 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6600804.0634 | 7659612.8512 | 7659612.8512 | 62.4285 | 62.1301 | 1.0018 | 0.9979 | 685341.5034 | 887078.8513 | 461.4601 | 0.46808 | 0 | 0 | 29.4026 | 24.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017896 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.2323 | 1367.9961 | 53.7118 | 44.1216 | 29.2182 | 1786.8149 | 85.2275 | 24.5659 | 461.7723 | 0.0055704 | 60.006 | 0.5721 | 0.10984 | 93.8167 | 2.2473 | 0.20486 | 0.13307 | 5.0843 | 0.49839 | 0.1418 | 0 | 100 | 577.1 | 317 | 115.95 | 108.53 | 100.37 | 306.5 | 4 | 95.92 | 42.56 | 4 | 37.78 | 43.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.4 | 0 | 38.45 | 53 | 53 | 110.93 | 93.37 | 88.21 | 0 | 100.37 | 2.43 | 95.14 | 43.23 | 116 | 12.6 | 108.53 | 110 | 0 | 15706 | 83.34 | 117.35 | 222.05 | 216.02 | 221.36 | 0 | 34.2 | 50.45 | 15407 | 95.93 | 42.56 | 37.78 | 1.35 | 42.56 | 0 | 607 | 428.1 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 310.9 | 0 | 304.7 | 100.28 | 15708 | 15706 | 316
03/26/22 11:07:21.178 | 548.3574 | 1369.6567 | 53.6757 | 44.1005 | 9.5753 | 29.1343 | 51.0754 | 0 | 1781.1641 | 94.2919 | 85.6691 | 8.6228 | 25.2367 | 70.3754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 462.19 | 459.26 | 462.84 | 409.99 | 439.55 | 417.67 | 313.74 | 0.57215 | 0.070026 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6606069.208 | 7671220.3283 | 7671220.3283 | 62.4285 | 62.1302 | 1.0018 | 0.9979 | 685961.6573 | 888204.3514 | 461.43 | 0.47028 | 0 | 0 | 29.1343 | 25.2367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.01789 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.211 | 1368.0144 | 53.7102 | 44.1206 | 29.2046 | 1786.8401 | 85.2352 | 24.5754 | 461.7706 | 0.0055667 | 60.0059 | 0.57213 | 0.10566 | 93.8245 | 2.2474 | 0.20408 | 0.13254 | 5.0444 | 0.49431 | 0.14406 | 0 | 100 | 576.5 | 315 | 115.93 | 108.57 | 100.26 | 306.1 | 4 | 95.91 | 42.55 | 4 | 37.76 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.35 | 0 | 38.45 | 53 | 53 | 110.85 | 93.34 | 88.21 | 0 | 100.26 | 2.43 | 95.12 | 43.23 | 115.9 | 12.67 | 108.57 | 110 | 0 | 15706 | 83.34 | 117.35 | 222.05 | 216.02 | 221.36 | 0 | 34.17 | 50.47 | 15412 | 95.9 | 42.55 | 37.76 | 1.34 | 42.55 | 0 | 607 | 426.6 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 312 | 0 | 305.7 | 100.24 | 15706 | 15706 | 314
03/26/22 11:07:26.178 | 546.8173 | 1367.0297 | 53.6681 | 44.0959 | 9.5722 | 28.709 | 51.0735 | 0 | 1789.5507 | 94.2862 | 85.6636 | 8.6226 | 25.4213 | 70.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.997 | 462.23 | 459.3 | 462.89 | 409.85 | 439.48 | 417.54 | 313.67 | 0.57363 | -0.65992 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6587028.1506 | 7708013.6587 | 7708013.6587 | 62.4285 | 62.1303 | 1.0018 | 0.9979 | 684287.9974 | 892408.2162 | 461.4733 | 0.47096 | 0 | 0 | 28.709 | 25.4213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017882 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.1839 | 1368.025 | 53.7087 | 44.1196 | 29.1926 | 1786.888 | 85.2429 | 24.581 | 461.7691 | 0.0055636 | 60.0058 | 0.57217 | 0.099427 | 93.8321 | 2.2508 | 0.20327 | 0.132 | 4.9828 | 0.49014 | 0.14574 | 0 | 100 | 576.8 | 316 | 115.78 | 108.57 | 100.28 | 306.2 | 4 | 95.83 | 42.55 | 4 | 37.76 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.25 | 0 | 38.44 | 53 | 53 | 110.78 | 93.3 | 88.17 | 0 | 100.28 | 2.43 | 95.07 | 43.22 | 115.78 | 12.74 | 108.57 | 110 | 0 | 15706 | 83.34 | 117.35 | 222.05 | 216.02 | 221.36 | 0 | 34.2 | 50.62 | 15417 | 95.83 | 42.55 | 37.76 | 1.36 | 42.55 | 0 | 607 | 430.2 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 311.3 | 0 | 305.1 | 100.24 | 15706 | 15706 | 316
03/26/22 11:07:31.179 | 545.938 | 1365.1098 | 53.6634 | 44.0932 | 9.5702 | 29.8275 | 51.0768 | 0 | 1790.0513 | 94.2842 | 85.6616 | 8.6225 | 24.1828 | 70.4221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9971 | 462.2301 | 459.3001 | 462.8901 | 409.8501 | 439.4801 | 417.5401 | 313.6701 | 0.57455 | -0.79414 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6577422.0589 | 7708683.9488 | 7708683.9488 | 62.4285 | 62.1303 | 1.0018 | 0.9979 | 683327.1542 | 892658.1457 | 461.4734 | 0.47096 | 0 | 0 | 29.8275 | 24.1828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017892 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.1451 | 1368.0122 | 53.7071 | 44.1185 | 29.1898 | 1786.9154 | 85.2506 | 24.571 | 461.7677 | 0.0055604 | 60.0056 | 0.57222 | 0.092323 | 93.8397 | 2.2608 | 0.20244 | 0.13146 | 4.9866 | 0.48591 | 0.14738 | 0 | 100 | 577.1 | 318 | 115.83 | 108.55 | 100.35 | 307.9 | 4 | 95.87 | 42.56 | 4 | 37.78 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.25 | 0 | 38.45 | 53 | 53 | 110.75 | 93.28 | 88.13 | 0 | 100.35 | 2.43 | 95.07 | 43.23 | 115.85 | 12.68 | 108.55 | 110 | 0 | 15706 | 83.34 | 117.35 | 222.05 | 216.02 | 221.36 | 0 | 34.26 | 50.68 | 15422 | 95.87 | 42.56 | 37.78 | 1.38 | 42.56 | 0 | 607 | 429 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 312.5 | 0 | 306.3 | 100.35 | 15708 | 15706 | 317
03/26/22 11:07:36.178 | 547.0809 | 1368.2942 | 53.6577 | 44.0898 | 9.5679 | 29.5105 | 51.0758 | 0 | 1785.8089 | 94.2828 | 85.6604 | 8.6224 | 24.7469 | 70.4187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.003 | 462.19 | 459.26 | 462.91 | 409.8 | 439.6 | 417.43 | 313.65 | 0.57332 | -0.38884 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6590919.4563 | 7690950.9948 | 7690950.9948 | 62.4285 | 62.1303 | 1.0018 | 0.9979 | 684921.3824 | 890542.7473 | 461.4533 | 0.47531 | 0 | 0 | 29.5105 | 24.7469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017894 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.1038 | 1367.9982 | 53.7054 | 44.1175 | 29.1782 | 1786.8952 | 85.258 | 24.5741 | 461.7666 | 0.0055582 | 60.0056 | 0.57228 | 0.087987 | 93.8471 | 2.2511 | 0.2016 | 0.13094 | 4.9817 | 0.48173 | 0.14881 | 0 | 100 | 577.3 | 317 | 115.88 | 108.53 | 100.33 | 307.1 | 4 | 95.88 | 42.56 | 4 | 37.78 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.28 | 0 | 38.46 | 53 | 53 | 110.83 | 93.32 | 88.11 | 0 | 100.33 | 2.43 | 95.08 | 43.25 | 115.9 | 12.63 | 108.53 | 110 | 0 | 15706 | 83.34 | 117.37 | 222.05 | 216.02 | 221.36 | 0 | 34.31 | 50.78 | 15427 | 95.9 | 42.56 | 37.78 | 1.38 | 42.56 | 0 | 607 | 430.2 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 312.5 | 0 | 306.3 | 100.28 | 15707 | 15706 | 316
03/26/22 11:07:41.178 | 547.1824 | 1368.8412 | 53.6523 | 44.0862 | 9.5661 | 29.8884 | 51.0671 | 0 | 1782.3872 | 94.2821 | 85.6603 | 8.6218 | 24.0047 | 70.4274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.003 | 462.19 | 459.26 | 462.91 | 409.8 | 439.6 | 417.43 | 313.65 | 0.57321 | -0.20295 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6592499.9259 | 7678284.6686 | 7678284.6686 | 62.4285 | 62.1303 | 1.0018 | 0.9979 | 685156.6634 | 889214.7552 | 461.4533 | 0.47531 | 0 | 0 | 29.8884 | 24.0047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017902 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.0612 | 1367.9845 | 53.7037 | 44.1165 | 29.1706 | 1786.8591 | 85.2655 | 24.5724 | 461.7655 | 0.0055557 | 60.0056 | 0.57233 | 0.084346 | 93.8545 | 2.2384 | 0.20075 | 0.13044 | 4.9907 | 0.47746 | 0.15041 | 0 | 100 | 576.7 | 315 | 115.85 | 108.53 | 100.3 | 306.1 | 4 | 95.87 | 42.56 | 4 | 37.78 | 43.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.25 | 0 | 38.45 | 53 | 53 | 110.8 | 93.31 | 88.19 | 0 | 100.3 | 2.43 | 95.07 | 43.23 | 115.85 | 12.66 | 108.53 | 110 | 0 | 15706 | 83.34 | 117.37 | 222.05 | 216.02 | 221.36 | 0 | 34.41 | 50.96 | 15432 | 95.87 | 42.56 | 37.78 | 1.37 | 42.56 | 0 | 607 | 429.8 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 311.4 | 0 | 305.2 | 100.24 | 15704 | 15706 | 315
03/26/22 11:07:46.178 | 547.5559 | 1370.1005 | 53.6432 | 44.0796 | 9.5636 | 30.3199 | 51.0778 | 0 | 1782.3872 | 94.2818 | 85.6613 | 8.6204 | 23.6199 | 70.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.005 | 462.2 | 459.23 | 462.91 | 409.85 | 439.64 | 417.35 | 313.65 | 0.57282 | -0.072827 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6597365.955 | 7673169.9702 | 7673169.9702 | 62.4286 | 62.1303 | 1.0018 | 0.9979 | 685826.1991 | 888836.28 | 461.4467 | 0.48037 | 0 | 0 | 30.3199 | 23.6199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017902 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 548.0141 | 1367.9632 | 53.702 | 44.1154 | 29.1652 | 1786.816 | 85.2729 | 24.5691 | 461.7644 | 0.0055535 | 60.0056 | 0.57239 | 0.080824 | 93.8618 | 2.2165 | 0.19988 | 0.12994 | 5.0045 | 0.47314 | 0.15201 | 0 | 100 | 576.4 | 315 | 115.98 | 108.53 | 100.19 | 308.2 | 4 | 95.93 | 42.56 | 4 | 37.78 | 43.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.3 | 0 | 38.45 | 53 | 53 | 110.85 | 93.34 | 88.15 | 0 | 100.19 | 2.43 | 95.09 | 43.23 | 115.98 | 12.6 | 108.53 | 110 | 0 | 15706 | 83.34 | 117.37 | 222.05 | 216.02 | 221.36 | 0 | 34.56 | 51.14 | 15437 | 95.93 | 42.56 | 37.78 | 1.35 | 42.56 | 0 | 607 | 426.8 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 312.2 | 0 | 305.9 | 100.24 | 15707 | 15706 | 317
03/26/22 11:07:51.178 | 547.7107 | 1370.6321 | 53.6391 | 44.0765 | 9.5625 | 30.0989 | 51.0909 | 0 | 1782.124 | 94.2823 | 85.6625 | 8.6198 | 24.1373 | 70.3998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0051 | 462.2001 | 459.2301 | 462.9101 | 409.8501 | 439.6401 | 417.3501 | 313.6501 | 0.57266 | -0.036279 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6599039.3041 | 7672039.8891 | 7672039.8891 | 62.4286 | 62.1303 | 1.0018 | 0.9979 | 686092.4808 | 888704.856 | 461.4467 | 0.48037 | 0 | 0 | 30.0989 | 24.1373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017913 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.9736 | 1367.9666 | 53.7002 | 44.1144 | 29.1588 | 1786.778 | 85.2802 | 24.567 | 461.7636 | 0.0055517 | 60.0056 | 0.57245 | 0.078458 | 93.869 | 2.2201 | 0.199 | 0.12949 | 5.0141 | 0.46888 | 0.15334 | 0 | 100 | 576.4 | 315 | 115.93 | 108.53 | 100.24 | 306.1 | 4 | 95.91 | 42.56 | 4 | 37.78 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.33 | 0 | 38.45 | 53 | 53 | 110.85 | 93.34 | 88.09 | 0 | 100.24 | 2.43 | 95.11 | 43.23 | 115.93 | 12.62 | 108.53 | 110 | 0 | 15706 | 83.34 | 117.37 | 222.05 | 216.02 | 221.36 | 0 | 34.68 | 51.13 | 15442 | 95.91 | 42.56 | 37.78 | 1.45 | 42.56 | 0 | 607 | 428.5 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 312 | 0 | 305.8 | 100.21 | 15707 | 15706 | 316
03/26/22 11:07:56.178 | 546.9276 | 1368.8309 | 53.6344 | 44.0729 | 9.5614 | 29.6023 | 51.076 | 0 | 1782.5369 | 94.2833 | 85.6643 | 8.619 | 24.8789 | 70.4435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 462.21 | 459.22 | 462.91 | 409.87 | 439.62 | 417.3 | 313.64 | 0.57346 | -0.1906 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6589170.6613 | 7674001.3741 | 7674001.3741 | 62.4286 | 62.1303 | 1.0018 | 0.9979 | 685191.0863 | 888910.4911 | 461.4467 | 0.48254 | 0 | 0 | 29.6023 | 24.8789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017899 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.9301 | 1367.9658 | 53.6984 | 44.1133 | 29.153 | 1786.748 | 85.2875 | 24.5639 | 461.7628 | 0.0055499 | 60.0057 | 0.57251 | 0.075356 | 93.8762 | 2.2198 | 0.19811 | 0.12905 | 5.0233 | 0.46457 | 0.15465 | 0 | 100 | 576.4 | 318 | 115.9 | 108.53 | 100.4 | 305.2 | 4 | 95.9 | 42.56 | 4 | 37.78 | 44.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.33 | 0 | 38.46 | 53 | 53 | 110.83 | 93.32 | 88.13 | 0 | 100.4 | 2.43 | 95.11 | 43.25 | 115.9 | 12.63 | 108.53 | 110 | 0 | 15706 | 83.34 | 117.37 | 222.05 | 216.02 | 221.36 | 0 | 34.62 | 50.89 | 15447 | 95.9 | 42.56 | 37.78 | 1.54 | 42.56 | 0 | 607 | 429.8 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 310.9 | 0 | 304.7 | 100.28 | 15707 | 15706 | 315
03/26/22 11:08:01.178 | 545.1438 | 1364.6092 | 53.6277 | 44.068 | 9.5597 | 29.6645 | 51.0745 | 0 | 1787.3263 | 94.285 | 85.6676 | 8.6174 | 24.8237 | 70.4332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.002 | 462.23 | 459.22 | 462.9 | 409.93 | 439.59 | 417.21 | 313.63 | 0.57532 | -0.71981 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6567739.721 | 7693100.7797 | 7693100.7797 | 62.4286 | 62.1303 | 1.0018 | 0.9979 | 683078.1182 | 891298.3512 | 461.45 | 0.48326 | 0 | 0 | 29.6645 | 24.8237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017903 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.8813 | 1367.9577 | 53.6965 | 44.1123 | 29.1454 | 1786.7037 | 85.2947 | 24.5653 | 461.7619 | 0.0055481 | 60.0057 | 0.57257 | 0.072441 | 93.8832 | 2.2293 | 0.19719 | 0.12864 | 4.9825 | 0.46034 | 0.15595 | 0 | 100 | 576.1 | 316 | 115.9 | 108.53 | 100.16 | 307.1 | 4 | 95.9 | 42.55 | 4 | 37.76 | 44.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.28 | 0 | 38.44 | 53 | 53 | 110.8 | 93.31 | 88.19 | 0 | 100.16 | 2.43 | 95.08 | 43.22 | 115.9 | 12.63 | 108.53 | 110 | 0 | 15706 | 83.34 | 117.37 | 222.05 | 216.02 | 221.36 | 0 | 34.47 | 50.51 | 15452 | 95.9 | 42.55 | 37.76 | 1.57 | 42.55 | 0 | 607 | 428.8 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 312.5 | 0 | 306.3 | 100.14 | 15704 | 15706 | 313
03/26/22 11:08:06.178 | 545.1433 | 1364.9705 | 53.6255 | 44.0662 | 9.5593 | 29.3803 | 51.0752 | 0 | 1786.4799 | 94.2855 | 85.6688 | 8.6168 | 25.3568 | 70.4241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0021 | 462.2301 | 459.2201 | 462.9001 | 409.9301 | 439.5901 | 417.2101 | 313.6301 | 0.57532 | -0.66858 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6567624.5732 | 7689009.8381 | 7689009.8381 | 62.4286 | 62.1302 | 1.0018 | 0.9979 | 683104.033 | 890837.5272 | 461.4501 | 0.48326 | 0 | 0 | 29.3803 | 25.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017899 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.8344 | 1367.9588 | 53.6947 | 44.1112 | 29.1358 | 1786.6686 | 85.3019 | 24.5702 | 461.7613 | 0.0055467 | 60.0058 | 0.57263 | 0.069629 | 93.8901 | 2.2279 | 0.19625 | 0.12824 | 4.9615 | 0.45606 | 0.157 | 0 | 100 | 576.4 | 316 | 115.8 | 108.53 | 100.3 | 306.7 | 4 | 95.85 | 42.56 | 4 | 37.78 | 44.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.2 | 0 | 38.44 | 53 | 53 | 110.78 | 93.3 | 88.17 | 0 | 100.3 | 2.43 | 95.04 | 43.22 | 115.8 | 12.68 | 108.51 | 110 | 0 | 15706 | 83.34 | 117.35 | 222.05 | 216.02 | 221.36 | 0 | 34.25 | 50.21 | 15457 | 95.83 | 42.56 | 37.78 | 1.56 | 42.56 | 0 | 607 | 430.2 | 459.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 312.3 | 0 | 306.1 | 100.21 | 15707 | 15706 | 316
03/26/22 11:08:11.178 | 546.5565 | 1368.191 | 53.6221 | 44.0627 | 9.5594 | 28.7444 | 51.0795 | 0 | 1793.0188 | 94.286 | 85.6692 | 8.6168 | 26.2826 | 70.4481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0031 | 462.2401 | 459.2101 | 462.8801 | 409.9701 | 439.5101 | 417.1701 | 313.6001 | 0.57377 | -0.84193 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6583950.7182 | 7718711.6388 | 7718711.6388 | 62.4286 | 62.1302 | 1.0018 | 0.9979 | 684871.2766 | 894136.8656 | 461.4434 | 0.48399 | 0 | 0 | 28.7444 | 26.2826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017875 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.7844 | 1367.9485 | 53.6928 | 44.1102 | 29.1214 | 1786.711 | 85.3089 | 24.5815 | 461.7607 | 0.0055454 | 60.0059 | 0.57269 | 0.062142 | 93.897 | 2.2225 | 0.19526 | 0.12784 | 4.983 | 0.45175 | 0.15803 | 0 | 100 | 576.7 | 316 | 115.7 | 108.51 | 100.3 | 305.2 | 4 | 95.8 | 42.55 | 4 | 37.76 | 44.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.13 | 0 | 38.45 | 53 | 53 | 110.65 | 93.23 | 88.09 | 0 | 100.3 | 2.42 | 95 | 43.23 | 115.68 | 12.73 | 108.51 | 110 | 0 | 15706 | 83.34 | 117.33 | 222.05 | 216.02 | 221.36 | 0 | 34.01 | 49.98 | 15462 | 95.78 | 42.55 | 37.76 | 1.59 | 42.55 | 0 | 607 | 426.1 | 459.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 310.4 | 0 | 304.2 | 100.21 | 15708 | 15706 | 316
03/26/22 11:08:16.177 | 546.4602 | 1367.4994 | 53.62 | 44.0597 | 9.5603 | 29.4292 | 51.0686 | 0 | 1801.9732 | 94.2847 | 85.6675 | 8.6172 | 25.2407 | 70.4662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0061 | 462.2701 | 459.2201 | 462.8701 | 410.0001 | 439.3901 | 417.1001 | 313.5701 | 0.57382 | -1.3028 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6583244.6719 | 7753550.0601 | 7753550.0601 | 62.4286 | 62.1302 | 1.0018 | 0.9979 | 684695.6661 | 898229.1935 | 461.4534 | 0.48398 | 0 | 0 | 29.4292 | 25.2407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017864 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.7219 | 1367.9127 | 53.6908 | 44.1091 | 29.115 | 1786.8167 | 85.316 | 24.5808 | 461.7601 | 0.0055441 | 60.006 | 0.57277 | 0.049523 | 93.9038 | 2.1767 | 0.19424 | 0.12743 | 5.1031 | 0.44743 | 0.15896 | 0 | 100 | 576.5 | 317 | 115.6 | 108.49 | 100.28 | 305.8 | 4 | 95.75 | 42.54 | 4 | 37.75 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.05 | 0 | 38.43 | 53 | 53 | 110.65 | 93.23 | 88.09 | 0 | 100.28 | 2.42 | 94.97 | 43.21 | 115.63 | 12.73 | 108.49 | 110 | 0 | 15706 | 83.34 | 117.33 | 222.05 | 216.02 | 221.36 | 0 | 33.89 | 50.01 | 15467 | 95.76 | 42.54 | 37.75 | 1.63 | 42.54 | 0 | 607 | 430.2 | 459.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 312.6 | 0 | 306.4 | 100.35 | 15707 | 15706 | 316
03/26/22 11:08:21.177 | 547.2467 | 1369.7805 | 53.6174 | 44.0571 | 9.5603 | 28.3936 | 51.0878 | 0 | 1800.3681 | 94.2795 | 85.6627 | 8.6168 | 26.1396 | 70.4406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 462.3301 | 459.2701 | 462.8501 | 410.0401 | 439.0101 | 416.9901 | 313.4901 | 0.57285 | -1.1481 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6591953.8107 | 7750231.0144 | 7750231.0144 | 62.4286 | 62.1303 | 1.0018 | 0.9979 | 685667.1613 | 897802.7586 | 461.4834 | 0.47961 | 0 | 0 | 28.3936 | 26.1396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017862 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.6618 | 1367.8856 | 53.6889 | 44.108 | 29.1049 | 1786.9145 | 85.3229 | 24.5824 | 461.7595 | 0.0055429 | 60.0061 | 0.57284 | 0.037585 | 93.9106 | 2.1366 | 0.19318 | 0.12702 | 5.2279 | 0.44304 | 0.1598 | 0 | 100 | 575.9 | 317 | 115.7 | 108.47 | 100.16 | 307.7 | 4 | 95.81 | 42.54 | 4 | 37.75 | 44.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.08 | 0 | 38.43 | 53 | 53 | 110.63 | 93.22 | 88.13 | 0 | 100.16 | 2.42 | 94.98 | 43.21 | 115.7 | 12.66 | 108.45 | 110 | 0 | 15706 | 83.32 | 117.33 | 222.05 | 216.02 | 221.36 | 0 | 33.9 | 50.15 | 15472 | 95.8 | 42.54 | 37.75 | 1.63 | 42.54 | 0 | 607 | 428.5 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 313.1 | 0 | 306.9 | 100.19 | 15707 | 15706 | 315
03/26/22 11:08:26.177 | 546.0617 | 1366.9472 | 53.6153 | 44.0559 | 9.5594 | 29.342 | 51.0814 | 0 | 1794.8046 | 94.275 | 85.6588 | 8.6163 | 25.3383 | 70.4757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 462.3301 | 459.2701 | 462.8501 | 410.0401 | 439.0101 | 416.9901 | 313.4901 | 0.57409 | -0.99779 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6578514.9833 | 7724882.2683 | 7724882.2683 | 62.4286 | 62.1304 | 1.0018 | 0.9979 | 684248.9553 | 895028.9284 | 461.4834 | 0.47961 | 0 | 0 | 29.342 | 25.3383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.01787 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.6046 | 1367.8669 | 53.6869 | 44.1069 | 29.0985 | 1786.954 | 85.3298 | 24.5803 | 461.759 | 0.0055418 | 60.0063 | 0.57291 | 0.029582 | 93.9172 | 2.13 | 0.19209 | 0.1266 | 5.2606 | 0.43857 | 0.16056 | 0 | 100 | 575.5 | 318 | 115.63 | 108.45 | 100.09 | 303.3 | 4 | 95.76 | 42.51 | 4 | 37.73 | 44.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.03 | 0 | 38.4 | 53 | 53 | 110.55 | 93.18 | 88.03 | 0 | 100.09 | 2.42 | 94.95 | 43.18 | 115.63 | 12.69 | 108.45 | 110 | 0 | 15706 | 83.32 | 117.33 | 222.05 | 216.02 | 221.36 | 0 | 33.89 | 50.35 | 15477 | 95.76 | 42.51 | 37.73 | 1.63 | 42.51 | 0 | 607 | 428.8 | 459.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.6 | 311.5 | 0 | 305.3 | 100.1 | 15703 | 15706 | 316
03/26/22 11:08:31.177 | 546.3848 | 1367.9536 | 53.6125 | 44.0545 | 9.558 | 29.7238 | 51.0913 | 0 | 1790.361 | 94.2693 | 85.6533 | 8.616 | 24.3264 | 70.4935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0111 | 462.3201 | 459.2801 | 462.8201 | 410.0101 | 438.7401 | 416.9201 | 313.4001 | 0.57359 | -0.6762 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6582747.165 | 7704340.1521 | 7704340.1521 | 62.4286 | 62.1304 | 1.0018 | 0.9979 | 684752.8487 | 892813.8255 | 461.4734 | 0.47529 | 0 | 0 | 29.7238 | 24.3264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017869 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.5546 | 1367.8668 | 53.6849 | 44.1058 | 29.0912 | 1786.9627 | 85.3366 | 24.5768 | 461.7585 | 0.0055406 | 60.0064 | 0.57297 | 0.024514 | 93.9237 | 2.13 | 0.19096 | 0.12616 | 5.2655 | 0.43401 | 0.16132 | 0 | 100 | 576.3 | 315 | 115.6 | 108.45 | 100.24 | 307 | 4 | 95.75 | 42.51 | 4 | 37.73 | 44.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.03 | 0 | 38.41 | 53 | 53 | 110.58 | 93.19 | 88.03 | 0 | 100.24 | 2.42 | 94.95 | 43.2 | 115.63 | 12.71 | 108.45 | 110 | 0 | 15706 | 83.32 | 117.35 | 222.05 | 216.02 | 221.36 | 0 | 34.15 | 50.84 | 15482 | 95.75 | 42.53 | 37.74 | 1.62 | 42.53 | 0 | 607 | 426.1 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.4 | 313.4 | 0 | 307.2 | 100.07 | 15705 | 15706 | 315
03/26/22 11:08:36.178 | 547.1664 | 1370.5702 | 53.61 | 44.053 | 9.557 | 28.9921 | 51.0892 | 0 | 1787.1973 | 94.2629 | 85.6467 | 8.6162 | 25.2517 | 70.4898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.011 | 462.32 | 459.28 | 462.82 | 410.01 | 438.74 | 416.92 | 313.4 | 0.57277 | -0.41792 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6591522.5537 | 7692970.7494 | 7692970.7494 | 62.4286 | 62.1305 | 1.0018 | 0.9979 | 685791.4711 | 891357.8605 | 461.4734 | 0.47529 | 0 | 0 | 28.9921 | 25.2517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.01787 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.5106 | 1367.8856 | 53.6829 | 44.1046 | 29.0765 | 1786.9658 | 85.3433 | 24.5835 | 461.7577 | 0.005539 | 60.0066 | 0.57303 | 0.020452 | 93.9302 | 2.1389 | 0.1898 | 0.1257 | 5.2655 | 0.42937 | 0.16236 | 0 | 100 | 575.2 | 317 | 115.68 | 108.45 | 100.12 | 306.6 | 4 | 95.78 | 42.53 | 4 | 37.74 | 44.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.03 | 0 | 38.41 | 53 | 53 | 110.58 | 93.21 | 88.05 | 0 | 100.12 | 2.42 | 94.95 | 43.2 | 115.65 | 12.68 | 108.45 | 110 | 0 | 15706 | 83.32 | 117.37 | 222.05 | 216.02 | 221.36 | 0 | 34.4 | 51.21 | 15487 | 95.77 | 42.53 | 37.74 | 1.6 | 42.53 | 0 | 607 | 429 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.9 | 312.3 | 0 | 306.1 | 100.16 | 15705 | 15706 | 316
03/26/22 11:08:41.177 | 547.872 | 1372.0049 | 53.6051 | 44.0494 | 9.5557 | 30.0796 | 51.0758 | 0 | 1785.0451 | 94.2498 | 85.6313 | 8.6185 | 23.925 | 70.4712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 462.25 | 459.24 | 462.72 | 410.07 | 438.54 | 416.96 | 313.34 | 0.57192 | -0.17085 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6600984.4146 | 7683260.3125 | 7683260.3125 | 62.4287 | 62.1307 | 1.0018 | 0.9979 | 686781.1616 | 890166.2173 | 461.4034 | 0.46886 | 0 | 0 | 30.0796 | 23.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017878 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.4676 | 1367.9045 | 53.6808 | 44.1035 | 29.0657 | 1786.9849 | 85.3499 | 24.5871 | 461.7566 | 0.0055366 | 60.0067 | 0.57308 | 0.01587 | 93.9366 | 2.1538 | 0.1886 | 0.12522 | 5.2612 | 0.42459 | 0.16381 | 0 | 100 | 575 | 315 | 115.58 | 108.43 | 100.1 | 304.2 | 4 | 95.73 | 42.5 | 4 | 37.71 | 44.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.98 | 0 | 38.39 | 53 | 53 | 110.5 | 93.16 | 87.97 | 0 | 100.1 | 2.42 | 94.93 | 43.17 | 115.58 | 12.7 | 108.43 | 110 | 0 | 15706 | 83.32 | 117.37 | 222.05 | 216.02 | 221.36 | 0 | 34.69 | 51.51 | 15492 | 95.73 | 42.5 | 37.71 | 1.65 | 42.5 | 0 | 607 | 428.8 | 459.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574.8 | 310.9 | 0 | 304.7 | 99.97 | 15707 | 15706 | 314
03/26/22 11:08:46.177 | 547.4921 | 1371.1018 | 53.6029 | 44.0475 | 9.5554 | 29.3411 | 51.0774 | 0 | 1783.0943 | 94.2432 | 85.6229 | 8.6203 | 24.9199 | 70.4691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 462.25 | 459.24 | 462.72 | 410.07 | 438.54 | 416.96 | 313.34 | 0.57232 | -0.16578 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6595757.4433 | 7677635.2341 | 7677635.2341 | 62.4287 | 62.1307 | 1.0018 | 0.9979 | 686329.1528 | 889194.6065 | 461.4033 | 0.46886 | 0 | 0 | 29.3411 | 24.9199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017869 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.4168 | 1367.9056 | 53.6787 | 44.1023 | 29.0574 | 1786.9782 | 85.3564 | 24.5867 | 461.7553 | 0.0055338 | 60.0068 | 0.57314 | 0.011524 | 93.9428 | 2.1554 | 0.18736 | 0.12473 | 5.2654 | 0.41972 | 0.16569 | 0 | 100 | 576.4 | 317 | 115.58 | 108.41 | 100.14 | 307.4 | 4 | 95.73 | 42.5 | 4 | 37.71 | 44.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114 | 0 | 38.39 | 53 | 53 | 110.5 | 93.16 | 87.93 | 0 | 100.14 | 2.42 | 94.94 | 43.17 | 115.58 | 12.68 | 108.41 | 110 | 0 | 15707 | 83.32 | 117.37 | 222.05 | 216.02 | 221.36 | 0 | 34.9 | 51.35 | 15497 | 95.73 | 42.5 | 37.71 | 1.63 | 42.5 | 0 | 606 | 430.2 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 313.6 | 0 | 307.4 | 100.24 | 15706 | 15707 | 317
03/26/22 11:08:51.178 | 546.5891 | 1368.8412 | 53.6003 | 44.0449 | 9.5553 | 29.6103 | 51.057 | 0 | 1787.4553 | 94.2338 | 85.6108 | 8.623 | 24.6758 | 70.4951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0131 | 462.2001 | 459.2001 | 462.6701 | 410.0701 | 438.5201 | 416.9801 | 313.3101 | 0.57321 | -0.57625 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6585115.3704 | 7698510.429 | 7698510.429 | 62.4287 | 62.1309 | 1.0018 | 0.9979 | 685197.7278 | 891371.1778 | 461.3567 | 0.46746 | 0 | 0 | 29.6103 | 24.6758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017878 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.3675 | 1367.9139 | 53.6766 | 44.1011 | 29.0484 | 1786.9785 | 85.3628 | 24.5864 | 461.7536 | 0.0055301 | 60.0069 | 0.5732 | 0.006647 | 93.949 | 2.1562 | 0.18608 | 0.12421 | 5.2654 | 0.41469 | 0.16821 | 0 | 100 | 575.8 | 316 | 115.53 | 108.39 | 100.1 | 307.1 | 4 | 95.71 | 42.5 | 4 | 37.71 | 44.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.95 | 0 | 38.39 | 53 | 53 | 110.48 | 93.13 | 87.97 | 0 | 100.1 | 2.42 | 94.92 | 43.17 | 115.55 | 12.67 | 108.39 | 110 | 0 | 15707 | 83.32 | 117.37 | 221.93 | 216.02 | 221.36 | 0 | 34.61 | 50.54 | 15502 | 95.72 | 42.5 | 37.71 | 1.55 | 42.5 | 0 | 606 | 430.1 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 312.9 | 0 | 306.7 | 100.21 | 15705 | 15707 | 315
03/26/22 11:08:56.178 | 545.6469 | 1366.3485 | 53.5963 | 44.04 | 9.5563 | 29.724 | 51.0923 | 0 | 1785.1277 | 94.2166 | 85.5889 | 8.6277 | 23.9123 | 70.4592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.012 | 462.14 | 459.14 | 462.61 | 410.02 | 438.53 | 417 | 313.27 | 0.57413 | -0.64042 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6573861.5571 | 7691886.145 | 7691886.145 | 62.4287 | 62.1311 | 1.0018 | 0.9979 | 683950.1049 | 890213.7139 | 461.2967 | 0.46752 | 0 | 0 | 29.724 | 23.9123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017875 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.3134 | 1367.9046 | 53.6745 | 44.0998 | 29.0396 | 1786.9715 | 85.3691 | 24.5833 | 461.7514 | 0.0056555 | 60.0071 | 0.57327 | 0.0014816 | 93.955 | 2.1593 | 0.18475 | 0.12368 | 5.2671 | 0.40953 | 0.17154 | 0 | 100 | 576.4 | 317 | 115.58 | 108.37 | 100.24 | 305.8 | 4 | 95.73 | 42.49 | 4 | 37.7 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.98 | 0 | 38.38 | 53 | 53 | 110.53 | 93.17 | 87.95 | 0 | 100.24 | 2.42 | 94.93 | 43.16 | 115.58 | 12.64 | 108.37 | 110 | 0 | 15707 | 83.32 | 117.35 | 221.93 | 216.02 | 221.36 | 0 | 34.12 | 49.9 | 15507 | 95.73 | 42.49 | 37.7 | 1.54 | 42.49 | 0 | 606 | 428.4 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 312.8 | 0 | 306.6 | 100.19 | 15708 | 15707 | 317
03/26/22 11:09:01.177 | 545.232 | 1364.8518 | 53.594 | 44.0373 | 9.5567 | 29.6104 | 51.088 | 0 | 1784.2091 | 94.2078 | 85.5782 | 8.6296 | 24.2488 | 70.4704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 462.1401 | 459.1401 | 462.6101 | 410.0201 | 438.5301 | 417.0001 | 313.2701 | 0.57456 | -0.67802 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6568785.7184 | 7689668.3037 | 7689668.3037 | 62.4287 | 62.1311 | 1.0018 | 0.9979 | 683405.0699 | 889772.1592 | 461.2968 | 0.46752 | 0 | 0 | 29.6104 | 24.2488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017885 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.2554 | 1367.8852 | 53.6723 | 44.0985 | 29.0351 | 1786.9689 | 85.3752 | 24.5754 | 461.7493 | 0.0056509 | 60.0072 | 0.57334 | -0.0043449 | 93.9609 | 2.171 | 0.18335 | 0.12312 | 5.2683 | 0.40428 | 0.17478 | 0 | 100 | 575.2 | 316 | 115.58 | 108.35 | 100.03 | 305.3 | 4 | 95.73 | 42.48 | 4 | 37.7 | 43.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114 | 0 | 38.36 | 53 | 53 | 110.55 | 93.18 | 87.85 | 0 | 100.03 | 2.43 | 94.94 | 43.15 | 115.58 | 12.62 | 108.35 | 110 | 0 | 15707 | 83.32 | 117.33 | 221.93 | 216.02 | 221.36 | 0 | 33.83 | 49.68 | 15511 | 95.73 | 42.48 | 37.69 | 1.5 | 42.48 | 0 | 606 | 429.9 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.1 | 312.8 | 0 | 306.6 | 100.02 | 15704 | 15707 | 317
03/26/22 11:09:06.178 | 545.2168 | 1365.1563 | 53.5887 | 44.0317 | 9.557 | 30.1229 | 51.081 | 0 | 1780.4777 | 94.1904 | 85.559 | 8.6315 | 23.9128 | 70.4671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0051 | 462.0101 | 459.0101 | 462.5001 | 410.0201 | 438.6701 | 416.9901 | 313.2101 | 0.57447 | -0.48911 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6569027.785 | 7675193.2548 | 7675193.2548 | 62.4287 | 62.1314 | 1.0018 | 0.9979 | 683353.674 | 887899.2498 | 461.1734 | 0.46909 | 0 | 0 | 30.1229 | 23.9128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017887 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.1948 | 1367.8622 | 53.67 | 44.0972 | 29.0264 | 1786.9194 | 85.3812 | 24.5761 | 461.7468 | 0.0059268 | 60.0073 | 0.57341 | -0.0080696 | 93.9667 | 2.1779 | 0.18187 | 0.12252 | 5.2873 | 0.39894 | 0.17976 | 0 | 100 | 575.7 | 317 | 115.58 | 108.37 | 100.12 | 306.8 | 4 | 95.73 | 42.48 | 4 | 37.69 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.03 | 0 | 38.36 | 53 | 53 | 110.55 | 93.18 | 87.89 | 0 | 100.12 | 2.43 | 94.95 | 43.15 | 115.6 | 12.63 | 108.37 | 110 | 0 | 15707 | 83.32 | 117.3 | 221.93 | 216.02 | 221.36 | 0 | 33.69 | 49.72 | 15517 | 95.75 | 42.48 | 37.69 | 1.48 | 42.48 | 0 | 606 | 429.9 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.3 | 312 | 0 | 305.7 | 100.05 | 15705 | 15707 | 316
03/26/22 11:09:11.178 | 545.445 | 1367.1846 | 53.5826 | 44.0259 | 9.5566 | 29.0652 | 51.0777 | 0 | 1782.7175 | 94.1759 | 85.5441 | 8.6318 | 25.2804 | 70.4865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.999 | 461.96 | 458.96 | 462.44 | 410.03 | 438.72 | 417 | 313.18 | 0.57417 | -0.54713 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6570860.3785 | 7681386.769 | 7681386.769 | 62.4287 | 62.1315 | 1.0018 | 0.9979 | 683658.7051 | 888400.2322 | 461.12 | 0.46842 | 0 | 0 | 29.0652 | 25.2804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017884 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.1382 | 1367.86 | 53.6677 | 44.0958 | 29.0113 | 1786.9016 | 85.3871 | 24.5856 | 461.7441 | 0.0060295 | 60.0074 | 0.57347 | -0.012254 | 93.9723 | 2.1784 | 0.18032 | 0.1219 | 5.2961 | 0.39345 | 0.18541 | 0 | 100 | 575.3 | 315 | 115.65 | 108.39 | 100.05 | 305.7 | 4 | 95.77 | 42.46 | 4 | 37.68 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.03 | 0 | 38.35 | 53 | 53 | 110.55 | 93.18 | 87.93 | 0 | 100.05 | 2.43 | 94.95 | 43.14 | 115.63 | 12.63 | 108.39 | 110 | 0 | 15709 | 83.32 | 117.3 | 221.93 | 215.91 | 221.36 | 0 | 33.59 | 49.82 | 15522 | 95.76 | 42.46 | 37.68 | 1.43 | 42.46 | 0 | 606 | 429.2 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.6 | 311.2 | 0 | 305 | 100.03 | 15708 | 15709 | 317
03/26/22 11:09:16.177 | 546.0441 | 1367.3084 | 53.5747 | 44.0183 | 9.5564 | 29.1354 | 51.0789 | 0 | 1792.5337 | 94.1627 | 85.5309 | 8.6318 | 25.3803 | 70.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 461.89 | 458.89 | 462.37 | 410.12 | 438.92 | 417.09 | 313.22 | 0.57362 | -1.0717 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6578129.2186 | 7729206.436 | 7729206.436 | 62.4287 | 62.1317 | 1.0018 | 0.9979 | 684431.5547 | 893915.64 | 461.05 | 0.4685 | 0 | 0 | 29.1354 | 25.3803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016239 | 0.017866 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.0891 | 1367.8681 | 53.6654 | 44.0944 | 28.9968 | 1786.9299 | 85.3929 | 24.5931 | 461.7413 | 0.0061102 | 60.0075 | 0.57353 | -0.018203 | 93.9778 | 2.1756 | 0.17869 | 0.12123 | 5.2776 | 0.38786 | 0.19162 | 0 | 100 | 575.9 | 315 | 115.5 | 108.39 | 100.12 | 305.4 | 4 | 95.7 | 42.45 | 4 | 37.66 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.93 | 0 | 38.34 | 53 | 53 | 110.43 | 93.12 | 87.91 | 0 | 100.12 | 2.43 | 94.9 | 43.12 | 115.5 | 12.7 | 108.39 | 110 | 0 | 15709 | 83.29 | 117.3 | 221.93 | 215.91 | 221.36 | 0 | 33.69 | 50.26 | 15527 | 95.7 | 42.45 | 37.66 | 1.42 | 42.45 | 0 | 606 | 429 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 311.6 | 0 | 305.4 | 100.21 | 15707 | 15709 | 316
03/26/22 11:09:21.177 | 545.8005 | 1366.6891 | 53.5702 | 44.0137 | 9.5565 | 29.4966 | 51.0688 | 0 | 1792.8331 | 94.1569 | 85.5254 | 8.6315 | 25.0735 | 70.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 461.89 | 458.89 | 462.37 | 410.12 | 438.92 | 417.09 | 313.22 | 0.57387 | -1.1142 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6575511.9695 | 7729915.4943 | 7729915.4943 | 62.4288 | 62.1318 | 1.0018 | 0.9979 | 684121.7419 | 894065.7445 | 461.05 | 0.4685 | 0 | 0 | 29.4966 | 25.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017872 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 547.0319 | 1367.8548 | 53.663 | 44.0929 | 28.9864 | 1786.9993 | 85.3986 | 24.5974 | 461.7386 | 0.0061692 | 60.0076 | 0.57359 | -0.027987 | 93.9832 | 2.1755 | 0.177 | 0.12053 | 5.2726 | 0.3822 | 0.19793 | 0 | 100 | 575.8 | 317 | 115.5 | 108.39 | 100.12 | 305.2 | 4 | 95.7 | 42.45 | 4 | 37.66 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.34 | 53 | 53 | 110.43 | 93.12 | 87.89 | 0 | 100.12 | 2.42 | 94.89 | 43.12 | 115.55 | 12.67 | 108.39 | 110 | 0 | 15709 | 83.29 | 117.33 | 221.93 | 215.91 | 221.36 | 0 | 34 | 50.8 | 15531 | 95.71 | 42.45 | 37.66 | 1.42 | 42.45 | 0 | 606 | 431 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 311.4 | 0 | 305.2 | 100.14 | 15706 | 15709 | 317
03/26/22 11:09:26.177 | 546.7479 | 1369.0116 | 53.5649 | 44.0081 | 9.5568 | 29.9231 | 51.0725 | 0 | 1787.8682 | 94.1507 | 85.5199 | 8.6308 | 24.1613 | 70.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.991 | 461.86 | 458.86 | 462.36 | 410.1 | 439.03 | 417.12 | 313.23 | 0.5729 | -0.66084 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6587300.517 | 7706847.7008 | 7706847.7008 | 62.4288 | 62.1318 | 1.0018 | 0.9979 | 685284.5186 | 891590.6267 | 461.0267 | 0.46997 | 0 | 0 | 29.9231 | 24.1613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017878 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.9759 | 1367.8437 | 53.6605 | 44.0913 | 28.9773 | 1787.0344 | 85.4042 | 24.5976 | 461.7357 | 0.0062278 | 60.0076 | 0.57366 | -0.035644 | 93.9886 | 2.1651 | 0.17524 | 0.1198 | 5.2642 | 0.37648 | 0.20442 | 0 | 100 | 575.4 | 316 | 115.53 | 108.39 | 100.07 | 306.6 | 4 | 95.71 | 42.45 | 4 | 37.66 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.93 | 0 | 38.34 | 53 | 53 | 110.48 | 93.14 | 87.91 | 0 | 100.07 | 2.43 | 94.9 | 43.12 | 115.53 | 12.68 | 108.39 | 110 | 0 | 15709 | 83.27 | 117.35 | 221.93 | 215.91 | 221.24 | 0 | 34.36 | 51.32 | 15536 | 95.71 | 42.45 | 37.66 | 1.42 | 42.45 | 0 | 606 | 428.5 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.4 | 312.7 | 0 | 306.5 | 100.07 | 15709 | 15709 | 317
03/26/22 11:09:31.177 | 547.2897 | 1370.5134 | 53.5602 | 44.0026 | 9.5576 | 30.393 | 51.082 | 0 | 1784.9574 | 94.1451 | 85.515 | 8.6302 | 23.5823 | 70.4633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9911 | 461.8601 | 458.8601 | 462.3601 | 410.1001 | 439.0301 | 417.1201 | 313.2301 | 0.57233 | -0.42284 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6594254.8751 | 7695510.7772 | 7695510.7772 | 62.4288 | 62.1319 | 1.0018 | 0.9979 | 685917.6198 | 890425.3209 | 461.0267 | 0.46997 | 0 | 0 | 30.393 | 23.5823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017884 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.924 | 1367.8423 | 53.658 | 44.0897 | 28.9685 | 1787.042 | 85.4097 | 24.5955 | 461.7328 | 0.0062217 | 60.0076 | 0.57372 | -0.04132 | 93.9939 | 2.1634 | 0.17342 | 0.11903 | 5.2601 | 0.37069 | 0.21067 | 0 | 100 | 575.8 | 315 | 115.55 | 108.39 | 100.14 | 305.6 | 4 | 95.71 | 42.45 | 4 | 37.66 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.93 | 0 | 38.34 | 53 | 53 | 110.48 | 93.14 | 87.93 | 0 | 100.16 | 2.43 | 94.9 | 43.12 | 115.55 | 12.67 | 108.39 | 110 | 0 | 15709 | 83.25 | 117.37 | 221.93 | 215.91 | 221.24 | 0 | 34.69 | 51.52 | 15541 | 95.72 | 42.45 | 37.66 | 1.42 | 42.45 | 0 | 606 | 430.4 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 311.8 | 0 | 305.6 | 100.14 | 15711 | 15709 | 315
03/26/22 11:09:36.177 | 547.8638 | 1371.494 | 53.552 | 43.993 | 9.559 | 29.7876 | 51.0754 | 0 | 1781.4324 | 94.136 | 85.5069 | 8.629 | 24.2754 | 70.4452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.987 | 461.83 | 458.8 | 462.37 | 410.11 | 439.16 | 416.97 | 313.21 | 0.57169 | -0.10826 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6600618.7845 | 7677642.2692 | 7677642.2692 | 62.4288 | 62.132 | 1.0018 | 0.9979 | 686527.7135 | 888383.0944 | 461 | 0.47722 | 0 | 0 | 29.7876 | 24.2754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.01789 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.8808 | 1367.8603 | 53.6555 | 44.0881 | 28.9656 | 1787.0019 | 85.4151 | 24.5878 | 461.7299 | 0.0063021 | 60.0076 | 0.57377 | -0.042623 | 93.9991 | 2.1761 | 0.17152 | 0.11822 | 5.2623 | 0.36487 | 0.217 | 0 | 100 | 575.7 | 316 | 115.53 | 108.39 | 100.12 | 304 | 4 | 95.71 | 42.44 | 4 | 37.65 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.93 | 0 | 38.34 | 53 | 53 | 110.45 | 93.13 | 87.93 | 0 | 100.12 | 2.43 | 94.9 | 43.12 | 115.5 | 12.7 | 108.39 | 110 | 0 | 15709 | 83.25 | 117.37 | 221.93 | 215.91 | 221.24 | 0 | 34.62 | 51 | 15546 | 95.7 | 42.44 | 37.65 | 1.51 | 42.44 | 0 | 606 | 428.2 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.4 | 311.3 | 0 | 305.1 | 100.07 | 15708 | 15709 | 315
03/26/22 11:09:41.177 | 547.2752 | 1370.0025 | 53.5471 | 43.988 | 9.5591 | 29.79 | 51.0783 | 0 | 1781.5872 | 94.1317 | 85.5035 | 8.6283 | 23.7431 | 70.4848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9871 | 461.8301 | 458.8001 | 462.3701 | 410.1101 | 439.1601 | 416.9701 | 313.2101 | 0.57231 | -0.19266 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6593529.3222 | 7677022.4261 | 7677022.4261 | 62.4288 | 62.132 | 1.0018 | 0.9979 | 685781.3016 | 888460.819 | 461.0001 | 0.47722 | 0 | 0 | 29.79 | 23.7431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017891 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.8391 | 1367.8785 | 53.6529 | 44.0863 | 28.9596 | 1786.9217 | 85.4205 | 24.5797 | 461.7269 | 0.0063388 | 60.0075 | 0.57382 | -0.041407 | 94.0042 | 2.1802 | 0.16955 | 0.11738 | 5.2339 | 0.35902 | 0.22332 | 0 | 100 | 575.6 | 316 | 115.48 | 108.39 | 99.98 | 305.8 | 4 | 95.68 | 42.43 | 4 | 37.64 | 43.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.33 | 53 | 53 | 110.43 | 93.12 | 87.93 | 0 | 99.98 | 2.43 | 94.89 | 43.11 | 115.48 | 12.71 | 108.39 | 110 | 0 | 15713 | 83.25 | 117.35 | 221.93 | 215.91 | 221.24 | 0 | 34.27 | 50.22 | 15552 | 95.68 | 42.43 | 37.64 | 1.56 | 42.43 | 0 | 606 | 429.1 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.3 | 313.2 | 0 | 306.9 | 100.05 | 15709 | 15713 | 317
03/26/22 11:09:46.177 | 545.0923 | 1364.5937 | 53.5415 | 43.9828 | 9.5587 | 29.6505 | 51.0904 | 0 | 1785.4735 | 94.1276 | 85.5006 | 8.627 | 24.1438 | 70.5088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 461.84 | 458.8 | 462.38 | 410.16 | 439.25 | 417.01 | 313.26 | 0.57469 | -0.74732 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6567108.4351 | 7693103.3027 | 7693103.3027 | 62.4288 | 62.1321 | 1.0018 | 0.9979 | 683074.1008 | 890399.2649 | 461.0067 | 0.47866 | 0 | 0 | 29.6505 | 24.1438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01624 | 0.017882 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.7827 | 1367.8638 | 53.6502 | 44.0846 | 28.9536 | 1786.8629 | 85.4258 | 24.574 | 461.7237 | 0.006332 | 60.0074 | 0.57388 | -0.043629 | 94.0092 | 2.1935 | 0.16751 | 0.11653 | 5.1901 | 0.35305 | 0.22943 | 0 | 100 | 575.6 | 315 | 115.53 | 108.39 | 100.16 | 304.7 | 4 | 95.71 | 42.41 | 4 | 37.63 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.3 | 53 | 53 | 110.43 | 93.12 | 87.93 | 0 | 100.16 | 2.43 | 94.89 | 43.09 | 115.53 | 12.68 | 108.39 | 110 | 0 | 15714 | 83.23 | 117.33 | 221.93 | 215.91 | 221.24 | 0 | 33.9 | 49.87 | 15557 | 95.71 | 42.41 | 37.63 | 1.59 | 42.41 | 0 | 606 | 427.8 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.6 | 310.9 | 0 | 304.7 | 100.1 | 15714 | 15714 | 315
03/26/22 11:09:51.177 | 544.4077 | 1362.9371 | 53.5328 | 43.9746 | 9.5582 | 28.9475 | 51.0744 | 0 | 1790.6603 | 94.1219 | 85.4967 | 8.6252 | 25.9015 | 70.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.994 | 461.88 | 458.81 | 462.46 | 410.2 | 439.44 | 417.03 | 313.35 | 0.57558 | -1.1545 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6558245.8716 | 7715875.4452 | 7715875.4452 | 62.4289 | 62.1321 | 1.0018 | 0.9979 | 682245.197 | 892986.4747 | 461.05 | 0.48585 | 0 | 0 | 28.9475 | 25.9015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017874 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.7201 | 1367.8365 | 53.6475 | 44.0827 | 28.9461 | 1786.8335 | 85.431 | 24.5759 | 461.7203 | 0.0063248 | 60.0073 | 0.57395 | -0.048429 | 94.0141 | 2.224 | 0.16534 | 0.11564 | 5.1531 | 0.34706 | 0.2351 | 0 | 100 | 575.9 | 315 | 115.48 | 108.39 | 100.07 | 305.7 | 4 | 95.68 | 42.41 | 4 | 37.63 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.85 | 0 | 38.3 | 53 | 53 | 110.43 | 93.12 | 87.91 | 0 | 100.07 | 2.43 | 94.87 | 43.09 | 115.45 | 12.72 | 108.39 | 110 | 0 | 15714 | 83.21 | 117.33 | 221.93 | 215.91 | 221.24 | 0 | 33.75 | 49.81 | 15562 | 95.67 | 42.41 | 37.63 | 1.59 | 42.41 | 0 | 606 | 430.3 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 313.9 | 0 | 307.6 | 100.23 | 15713 | 15714 | 316
03/26/22 11:09:56.177 | 545.4898 | 1365.4505 | 53.5278 | 43.9682 | 9.5596 | 28.5695 | 51.0836 | 0 | 1796.3012 | 94.1178 | 85.4927 | 8.6251 | 26.0333 | 70.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.994 | 461.88 | 458.81 | 462.46 | 410.2 | 439.44 | 417.03 | 313.35 | 0.57444 | -1.3023 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6570946.6736 | 7740286.7557 | 7740286.7557 | 62.4289 | 62.1322 | 1.0018 | 0.9979 | 683503.5414 | 895800.1758 | 461.05 | 0.48585 | 0 | 0 | 28.5695 | 26.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016238 | 0.017855 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.6613 | 1367.8199 | 53.6447 | 44.0809 | 28.9364 | 1786.8357 | 85.4361 | 24.5775 | 461.717 | 0.0063176 | 60.0072 | 0.57401 | -0.054322 | 94.019 | 2.2306 | 0.16305 | 0.11473 | 5.157 | 0.34095 | 0.2403 | 0 | 100 | 576.4 | 315 | 115.33 | 108.39 | 100.24 | 306.6 | 4 | 95.62 | 42.43 | 4 | 37.64 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.75 | 0 | 38.31 | 53 | 53 | 110.33 | 93.07 | 87.91 | 0 | 100.24 | 2.42 | 94.82 | 43.1 | 115.35 | 12.77 | 108.39 | 110 | 0 | 15714 | 83.19 | 117.3 | 221.93 | 215.91 | 221.24 | 0 | 33.68 | 50 | 15566 | 95.62 | 42.43 | 37.64 | 1.58 | 42.43 | 0 | 606 | 427 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 311.2 | 0 | 305 | 100.28 | 15717 | 15714 | 317
03/26/22 11:10:01.176 | 545.765 | 1365.9149 | 53.5256 | 43.9644 | 9.5612 | 28.6662 | 51.084 | 0 | 1799.4753 | 94.1152 | 85.4892 | 8.6259 | 25.8834 | 70.4505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.994 | 461.88 | 458.81 | 462.46 | 410.2 | 439.44 | 417.03 | 313.35 | 0.57415 | -1.4417 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6574342.481 | 7754529.9983 | 7754529.9983 | 62.4289 | 62.1322 | 1.0018 | 0.99791 | 683736.1487 | 897383.5449 | 461.05 | 0.48585 | 0 | 0 | 28.6662 | 25.8834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017846 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.6058 | 1367.8139 | 53.6418 | 44.0789 | 28.9206 | 1786.8827 | 85.4412 | 24.5888 | 461.7136 | 0.0063103 | 60.007 | 0.57408 | -0.062293 | 94.0238 | 2.2343 | 0.16057 | 0.11376 | 5.2334 | 0.33473 | 0.24535 | 0 | 100 | 576.4 | 314 | 115.28 | 108.37 | 100.26 | 305.6 | 4 | 95.58 | 42.43 | 4 | 37.64 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.68 | 0 | 38.31 | 53 | 53 | 110.3 | 93.05 | 87.83 | 0 | 100.26 | 2.42 | 94.78 | 43.1 | 115.3 | 12.78 | 108.37 | 110 | 0 | 15714 | 83.19 | 117.33 | 221.81 | 215.91 | 221.24 | 0 | 33.95 | 50.75 | 15571 | 95.6 | 42.43 | 37.64 | 1.6 | 42.43 | 0 | 606 | 430.5 | 459.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 311.9 | 0 | 305.6 | 100.24 | 15713 | 15714 | 314
03/26/22 11:10:06.177 | 547.8852 | 1370.565 | 53.5214 | 43.9557 | 9.5657 | 28.6097 | 51.064 | 0 | 1800.7707 | 94.1071 | 85.478 | 8.6291 | 26.2783 | 70.4906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9901 | 461.8401 | 458.7501 | 462.4801 | 410.2501 | 439.8101 | 417.1201 | 313.4601 | 0.57213 | -1.2204 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6599820.4054 | 7763425.3605 | 7763425.3605 | 62.4289 | 62.1323 | 1.0018 | 0.99791 | 686064.0293 | 898031.2413 | 461.0234 | 0.49311 | 0 | 0 | 28.6097 | 26.2783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017844 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.5623 | 1367.837 | 53.6389 | 44.077 | 28.9046 | 1786.9649 | 85.4463 | 24.6035 | 461.7102 | 0.0063462 | 60.0069 | 0.57412 | -0.070358 | 94.0285 | 2.2411 | 0.15793 | 0.11277 | 5.3343 | 0.32833 | 0.25032 | 0 | 100 | 576.1 | 315 | 115.3 | 108.33 | 100.17 | 305.6 | 4 | 95.6 | 42.41 | 4 | 37.63 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.65 | 0 | 38.3 | 53 | 53 | 110.2 | 93 | 87.75 | 0 | 100.17 | 2.42 | 94.78 | 43.09 | 115.3 | 12.74 | 108.33 | 110 | 0 | 15714 | 83.17 | 117.35 | 221.81 | 215.91 | 221.24 | 0 | 34.4 | 51.26 | 15577 | 95.6 | 42.41 | 37.63 | 1.61 | 42.41 | 0 | 606 | 427.4 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 313.8 | 0 | 307.5 | 100.17 | 15711 | 15714 | 315
03/26/22 11:10:11.177 | 547.1951 | 1368.3922 | 53.5172 | 43.9483 | 9.5688 | 28.3631 | 51.0867 | 0 | 1797.1838 | 94.0957 | 85.4643 | 8.6314 | 26.5702 | 70.4704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 461.81 | 458.74 | 462.47 | 410.22 | 439.94 | 417.17 | 313.48 | 0.57289 | -1.1612 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6591282.1808 | 7750329.4029 | 7750329.4029 | 62.4289 | 62.1324 | 1.0018 | 0.99791 | 684976.5716 | 896244.5229 | 461.0067 | 0.49168 | 0 | 0 | 28.3631 | 26.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017836 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.5149 | 1367.851 | 53.636 | 44.075 | 28.8887 | 1787.0591 | 85.4513 | 24.6179 | 461.7066 | 0.0064036 | 60.0068 | 0.57418 | -0.079708 | 94.0332 | 2.2516 | 0.15514 | 0.11172 | 5.4067 | 0.32172 | 0.25547 | 0 | 100 | 575.5 | 315 | 115.28 | 108.31 | 100.17 | 304.2 | 4 | 95.58 | 42.39 | 4 | 37.6 | 43.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.6 | 0 | 38.29 | 53 | 53 | 110.2 | 93 | 87.71 | 0 | 100.17 | 2.42 | 94.74 | 43.07 | 115.23 | 12.76 | 108.31 | 110 | 0 | 15714 | 83.17 | 117.37 | 221.81 | 215.91 | 221.24 | 0 | 34.61 | 51.2 | 15582 | 95.56 | 42.39 | 37.6 | 1.6 | 42.39 | 0 | 606 | 428.1 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.1 | 310.2 | 0 | 304 | 100.02 | 15716 | 15714 | 315
03/26/22 11:10:16.176 | 547.4041 | 1368.7999 | 53.5139 | 43.9443 | 9.5696 | 28.4346 | 51.0915 | 0 | 1798.7011 | 94.0873 | 85.4547 | 8.6326 | 26.1258 | 70.4481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9841 | 461.7801 | 458.7101 | 462.4601 | 410.2201 | 440.1201 | 417.2601 | 313.5301 | 0.57276 | -1.2187 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6593861.1337 | 7757467.2907 | 7757467.2907 | 62.4289 | 62.1325 | 1.0018 | 0.99791 | 685180.7981 | 897002.6506 | 460.9834 | 0.49315 | 0 | 0 | 28.4346 | 26.1258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017823 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.4648 | 1367.8592 | 53.6329 | 44.0729 | 28.8706 | 1787.1822 | 85.4562 | 24.6334 | 461.703 | 0.0064175 | 60.0067 | 0.57424 | -0.090885 | 94.0379 | 2.2525 | 0.15215 | 0.11064 | 5.4075 | 0.31486 | 0.26072 | 0 | 100 | 575.7 | 317 | 115.18 | 108.31 | 100.12 | 306.8 | 4 | 95.55 | 42.36 | 4 | 37.58 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.55 | 0 | 38.26 | 53 | 53 | 110.15 | 92.98 | 87.67 | 0 | 100.12 | 2.42 | 94.71 | 43.05 | 115.2 | 12.77 | 108.31 | 110 | 0 | 15714 | 83.17 | 117.37 | 221.81 | 215.91 | 221.24 | 0 | 34.6 | 50.95 | 15587 | 95.55 | 42.36 | 37.58 | 1.61 | 42.36 | 0 | 606 | 429.7 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 308.7 | 0 | 302.5 | 100.14 | 15713 | 15714 | 315
03/26/22 11:10:21.177 | 546.8147 | 1367.3239 | 53.5091 | 43.9394 | 9.5696 | 28.9047 | 51.0766 | 0 | 1799.4649 | 94.0757 | 85.4419 | 8.6338 | 25.145 | 70.4427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.982 | 461.75 | 458.69 | 462.45 | 410.09 | 440.18 | 417.2 | 313.48 | 0.57328 | -1.3454 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6587174.4128 | 7760699.4021 | 7760699.4021 | 62.429 | 62.1327 | 1.0018 | 0.99791 | 684442.1519 | 897385.4772 | 460.9633 | 0.49317 | 0 | 0 | 28.9047 | 25.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.01782 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.4156 | 1367.8698 | 53.6299 | 44.0708 | 28.8594 | 1787.3027 | 85.4611 | 24.6377 | 461.6995 | 0.0064748 | 60.0065 | 0.57429 | -0.10152 | 94.0424 | 2.2478 | 0.14901 | 0.1095 | 5.4425 | 0.30777 | 0.26613 | 0 | 100 | 576 | 315 | 115.13 | 108.29 | 100.17 | 302.8 | 4 | 95.52 | 42.36 | 4 | 37.58 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.55 | 0 | 38.26 | 53 | 53 | 110.13 | 92.96 | 87.65 | 0 | 100.17 | 2.42 | 94.71 | 43.05 | 115.15 | 12.77 | 108.29 | 110 | 0 | 15714 | 83.17 | 117.37 | 221.81 | 215.8 | 221.12 | 0 | 34.48 | 50.7 | 15591 | 95.52 | 42.36 | 37.58 | 1.61 | 42.36 | 0 | 606 | 429 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.3 | 310.9 | 0 | 304.7 | 100.05 | 15714 | 15714 | 315
03/26/22 11:10:26.176 | 546.8599 | 1367.8142 | 53.504 | 43.935 | 9.569 | 29.8811 | 51.0636 | 0 | 1792.3892 | 94.0642 | 85.4296 | 8.6346 | 24.0497 | 70.4642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9821 | 461.7501 | 458.6901 | 462.4501 | 410.0901 | 440.1801 | 417.2001 | 313.4801 | 0.57324 | -1.0419 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6588520.1817 | 7738365.9861 | 7738365.9861 | 62.429 | 62.1328 | 1.0018 | 0.99791 | 684530.1638 | 894874.9054 | 460.9634 | 0.49317 | 0 | 0 | 29.8811 | 24.0497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017835 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.3697 | 1367.8907 | 53.6268 | 44.0686 | 28.8587 | 1787.3252 | 85.4659 | 24.6257 | 461.6959 | 0.0065104 | 60.0063 | 0.57435 | -0.1065 | 94.0468 | 2.2295 | 0.14568 | 0.10829 | 5.4552 | 0.30047 | 0.27164 | 0 | 100 | 575.5 | 316 | 115.15 | 108.28 | 100.09 | 305.3 | 4 | 95.53 | 42.34 | 4 | 37.55 | 44.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.58 | 0 | 38.24 | 53 | 53 | 110.13 | 92.96 | 87.61 | 0 | 100.09 | 2.42 | 94.73 | 43.04 | 115.18 | 12.75 | 108.28 | 110 | 0 | 15716 | 83.15 | 117.37 | 221.81 | 215.8 | 221.12 | 0 | 34.46 | 50.52 | 15596 | 95.52 | 42.34 | 37.55 | 1.69 | 42.34 | 0 | 606 | 428.5 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574.8 | 312.3 | 0 | 306.1 | 99.97 | 15713 | 15716 | 318
03/26/22 11:10:31.176 | 547.5384 | 1369.4915 | 53.4942 | 43.9271 | 9.5671 | 28.6234 | 51.0783 | 0 | 1785.7005 | 94.0434 | 85.4077 | 8.6357 | 26.0232 | 70.4266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 461.6801 | 458.6601 | 462.4601 | 409.8501 | 440.3801 | 417.1901 | 313.4401 | 0.57245 | -0.50532 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6595651.6304 | 7704121.9066 | 7704121.9066 | 62.429 | 62.133 | 1.0018 | 0.99791 | 685527.8258 | 890526.3308 | 460.9334 | 0.4932 | 0 | 0 | 28.6234 | 26.0232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017834 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.3219 | 1367.9058 | 53.6236 | 44.0664 | 28.8543 | 1787.3003 | 85.4706 | 24.6201 | 461.6923 | 0.0065028 | 60.0061 | 0.5744 | -0.10867 | 94.0512 | 2.23 | 0.14218 | 0.107 | 5.4423 | 0.29297 | 0.277 | 0 | 100 | 575.3 | 315 | 115.28 | 108.28 | 100.05 | 306.9 | 4 | 95.58 | 42.33 | 4 | 37.54 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.63 | 0 | 38.24 | 53 | 53 | 110.15 | 92.98 | 87.58 | 0 | 100.05 | 2.42 | 94.75 | 43.02 | 115.28 | 12.69 | 108.28 | 110 | 0 | 15722 | 83.12 | 117.35 | 221.81 | 215.8 | 221.12 | 0 | 34.21 | 50.05 | 15601 | 95.58 | 42.33 | 37.54 | 1.7 | 42.33 | 0 | 606 | 430.8 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.3 | 313.9 | 0 | 307.7 | 100.05 | 15723 | 15722 | 313
03/26/22 11:10:36.176 | 547.1986 | 1368.7793 | 53.4903 | 43.9242 | 9.5661 | 29.3094 | 51.0651 | 0 | 1788.6114 | 94.0357 | 85.3998 | 8.6358 | 24.9837 | 70.4324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 461.6801 | 458.6601 | 462.4601 | 409.8501 | 440.3801 | 417.1901 | 313.4401 | 0.57281 | -0.7016 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6592163.9787 | 7715608.4312 | 7715608.4312 | 62.429 | 62.1331 | 1.0018 | 0.99791 | 685171.496 | 891979.1154 | 460.9334 | 0.4932 | 0 | 0 | 29.3094 | 24.9837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017827 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.2684 | 1367.9096 | 53.6204 | 44.0641 | 28.8476 | 1787.2607 | 85.4751 | 24.6193 | 461.6888 | 0.0065601 | 60.0059 | 0.57447 | -0.11122 | 94.0555 | 2.2309 | 0.13853 | 0.10566 | 5.4063 | 0.28527 | 0.28255 | 0 | 100 | 575.7 | 315 | 115.25 | 108.28 | 100.12 | 306.9 | 4 | 95.57 | 42.3 | 4 | 37.51 | 44.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.6 | 0 | 38.21 | 53 | 53 | 110.18 | 92.99 | 87.56 | 0 | 100.12 | 2.42 | 94.74 | 43 | 115.25 | 12.7 | 108.28 | 110 | 0 | 15722 | 83.12 | 117.33 | 221.81 | 215.8 | 221.12 | 0 | 33.96 | 49.8 | 15606 | 95.57 | 42.3 | 37.51 | 1.77 | 42.3 | 0 | 606 | 427.8 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 314 | 0 | 307.8 | 100.14 | 15721 | 15722 | 318
03/26/22 11:10:41.176 | 547.2614 | 1369.089 | 53.4838 | 43.9195 | 9.5643 | 29.8752 | 51.0597 | 0 | 1788.6372 | 94.024 | 85.3877 | 8.6362 | 23.929 | 70.4576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.987 | 461.67 | 458.66 | 462.47 | 409.75 | 440.46 | 417.16 | 313.43 | 0.57272 | -0.6756 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6593361.0243 | 7714773.4346 | 7714773.4346 | 62.429 | 62.1332 | 1.0018 | 0.99791 | 685349.9794 | 891983.126 | 460.9334 | 0.4932 | 0 | 0 | 29.8752 | 23.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017835 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.2199 | 1367.925 | 53.6171 | 44.0618 | 28.8447 | 1787.2004 | 85.4796 | 24.612 | 461.6854 | 0.0065528 | 60.0058 | 0.57452 | -0.11155 | 94.0597 | 2.2294 | 0.13467 | 0.10425 | 5.3292 | 0.27739 | 0.28795 | 0 | 100 | 575.7 | 317 | 115.25 | 108.28 | 100.12 | 307.4 | 4 | 95.57 | 42.3 | 4 | 37.51 | 43.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.6 | 0 | 38.21 | 53 | 53 | 110.15 | 92.98 | 87.56 | 0 | 100.12 | 2.42 | 94.74 | 43 | 115.28 | 12.69 | 108.28 | 110 | 0 | 15722 | 83.1 | 117.33 | 221.81 | 215.8 | 221.12 | 0 | 33.85 | 49.78 | 15611 | 95.58 | 42.3 | 37.51 | 1.69 | 42.3 | 0 | 606 | 428.5 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.6 | 313.9 | 0 | 307.7 | 100.1 | 15722 | 15722 | 317
03/26/22 11:10:46.176 | 546.3245 | 1367.489 | 53.4689 | 43.9091 | 9.5598 | 29.9452 | 51.0634 | 0 | 1784.0129 | 94.0008 | 85.3632 | 8.6376 | 23.7671 | 70.4699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9811 | 461.6501 | 458.6601 | 462.4801 | 409.6301 | 440.4801 | 417.0301 | 313.3701 | 0.5736 | -0.57823 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6582209.3593 | 7695980.2623 | 7695980.2623 | 62.429 | 62.1335 | 1.0018 | 0.99791 | 684526.5401 | 889691.2945 | 460.9301 | 0.49248 | 0 | 0 | 29.9452 | 23.7671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017835 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.1713 | 1367.9402 | 53.6138 | 44.0595 | 28.842 | 1787.134 | 85.484 | 24.6032 | 461.6819 | 0.006567 | 60.0056 | 0.57458 | -0.11147 | 94.0637 | 2.2242 | 0.13063 | 0.10279 | 5.2794 | 0.26929 | 0.29334 | 0 | 100 | 576.1 | 316 | 115.3 | 108.28 | 100.19 | 304.8 | 4 | 95.6 | 42.31 | 4 | 37.53 | 43.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.65 | 0 | 38.21 | 53 | 53 | 110.2 | 93 | 87.54 | 0 | 100.1 | 2.43 | 94.76 | 43 | 115.3 | 12.68 | 108.28 | 110 | 0 | 15722 | 83.08 | 117.33 | 221.81 | 215.8 | 221.12 | 0 | 33.74 | 49.8 | 15616 | 95.6 | 42.31 | 37.53 | 1.6 | 42.31 | 0 | 606 | 429.8 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.4 | 313.5 | 0 | 307.2 | 100.07 | 15723 | 15722 | 316
03/26/22 11:10:51.176 | 546.6974 | 1368.7999 | 53.461 | 43.9039 | 9.5571 | 29.7198 | 51.0712 | 0 | 1780.7047 | 93.9902 | 85.3527 | 8.6375 | 24.3141 | 70.4794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.981 | 461.65 | 458.66 | 462.48 | 409.63 | 440.48 | 417.03 | 313.37 | 0.57321 | -0.34526 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6586510.7889 | 7682251.5152 | 7682251.5152 | 62.4291 | 62.1336 | 1.0018 | 0.99791 | 685183.0771 | 888043.0465 | 460.93 | 0.49248 | 0 | 0 | 29.7198 | 24.3141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017847 | 0.010636 | 0.004632 | 0.011584 | 0.0119 | 546.1181 | 1367.9513 | 53.6103 | 44.0571 | 28.8332 | 1787.0596 | 85.4882 | 24.604 | 461.6783 | 0.0065594 | 60.0054 | 0.57464 | -0.1118 | 94.0677 | 2.2235 | 0.12637 | 0.10127 | 5.275 | 0.26097 | 0.29852 | 0 | 100 | 574.9 | 315 | 115.25 | 108.28 | 99.98 | 307.5 | 4 | 95.57 | 42.29 | 4 | 37.5 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.68 | 0 | 38.2 | 53 | 53 | 110.23 | 93.01 | 87.56 | 0 | 99.98 | 2.43 | 94.78 | 42.99 | 115.28 | 12.69 | 108.28 | 110 | 0 | 15723 | 83.08 | 117.33 | 221.81 | 215.8 | 221.12 | 0 | 33.71 | 49.94 | 15621 | 95.58 | 42.29 | 37.5 | 1.57 | 42.29 | 0 | 606 | 429.5 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.5 | 313.3 | 0 | 307 | 100.09 | 15722 | 15723 | 316
03/26/22 11:10:56.176 | 547.591 | 1370.8386 | 53.4438 | 43.8924 | 9.5514 | 29.8518 | 51.0741 | 0 | 1779.1151 | 93.9712 | 85.3348 | 8.6363 | 24.1248 | 70.4266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.981 | 461.65 | 458.65 | 462.48 | 409.64 | 440.52 | 417.02 | 313.39 | 0.57231 | -0.079213 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6597410.9449 | 7672817.0585 | 7672817.0585 | 62.4291 | 62.1338 | 1.0018 | 0.99791 | 686669.2423 | 887075.1166 | 460.9267 | 0.49393 | 0 | 0 | 29.8518 | 24.1248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.01785 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.0701 | 1367.9799 | 53.6068 | 44.0546 | 28.824 | 1786.9999 | 85.4924 | 24.6057 | 461.6747 | 0.0065515 | 60.0052 | 0.57469 | -0.11214 | 94.0715 | 2.2393 | 0.12187 | 0.099697 | 5.3079 | 0.25241 | 0.30367 | 0 | 100 | 575.2 | 317 | 115.25 | 108.28 | 100.03 | 303.1 | 4 | 95.58 | 42.28 | 4 | 37.49 | 43.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.68 | 0 | 38.19 | 53 | 53 | 110.2 | 93 | 87.61 | 0 | 100.03 | 2.43 | 94.78 | 42.97 | 115.25 | 12.7 | 108.28 | 110 | 0 | 15724 | 83.08 | 117.33 | 221.81 | 215.8 | 221.12 | 0 | 33.85 | 50.3 | 15626 | 95.57 | 42.28 | 37.49 | 1.54 | 42.28 | 0 | 606 | 430.2 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 311.5 | 0 | 305.3 | 100.14 | 15723 | 15724 | 314
03/26/22 11:11:01.176 | 545.3254 | 1366.6943 | 53.4308 | 43.883 | 9.5478 | 30.1657 | 51.063 | 0 | 1777.4739 | 93.9606 | 85.325 | 8.6356 | 23.674 | 70.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.987 | 461.64 | 458.63 | 462.48 | 409.79 | 440.69 | 417.03 | 313.46 | 0.57481 | -0.34291 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6570398.6698 | 7665971.4417 | 7665971.4417 | 62.4291 | 62.134 | 1.0018 | 0.99791 | 684130.3397 | 886435.9506 | 460.9167 | 0.49611 | 0 | 0 | 30.1657 | 23.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01623 | 0.017859 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.0108 | 1367.9711 | 53.6032 | 44.052 | 28.821 | 1786.95 | 85.4965 | 24.6014 | 461.671 | 0.0065437 | 60.005 | 0.57476 | -0.11539 | 94.0753 | 2.2352 | 0.1171 | 0.09802 | 5.3391 | 0.24357 | 0.30868 | 0 | 100 | 576.1 | 316 | 115.33 | 108.28 | 100.19 | 306.5 | 4 | 95.61 | 42.28 | 4 | 37.49 | 43.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.7 | 0 | 38.19 | 53 | 53 | 110.23 | 93.01 | 87.59 | 0 | 100.19 | 2.43 | 94.79 | 42.97 | 115.3 | 12.68 | 108.28 | 110 | 0 | 15724 | 83.08 | 117.33 | 221.81 | 215.8 | 221.12 | 0 | 34.08 | 50.7 | 15631 | 95.6 | 42.28 | 37.49 | 1.54 | 42.28 | 0 | 606 | 431.9 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.4 | 310.9 | 0 | 304.7 | 100.07 | 15724 | 15724 | 318
03/26/22 11:11:06.176 | 545.7302 | 1368.2322 | 53.4158 | 43.8715 | 9.5444 | 30.0463 | 51.0644 | 0 | 1777.4429 | 93.9519 | 85.3176 | 8.6343 | 23.961 | 70.3907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 461.63 | 458.62 | 462.47 | 409.86 | 440.73 | 417 | 313.48 | 0.57442 | -0.2119 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6575146.7896 | 7660932.9485 | 7660932.9485 | 62.4292 | 62.134 | 1.0018 | 0.99791 | 684833.557 | 885916.9361 | 460.9067 | 0.49612 | 0 | 0 | 30.0463 | 23.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017863 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.9448 | 1367.9565 | 53.5995 | 44.0494 | 28.8166 | 1786.8962 | 85.5005 | 24.5984 | 461.6673 | 0.0065789 | 60.0048 | 0.57483 | -0.11879 | 94.079 | 2.2256 | 0.11219 | 0.096345 | 5.396 | 0.23444 | 0.3137 | 0 | 100 | 575.6 | 318 | 115.28 | 108.29 | 100.1 | 307.5 | 4 | 95.58 | 42.26 | 4 | 37.48 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.73 | 0 | 38.18 | 53 | 53 | 110.25 | 93.03 | 87.56 | 0 | 100.1 | 2.43 | 94.8 | 42.96 | 115.28 | 12.71 | 108.29 | 110 | 0 | 15725 | 83.08 | 117.35 | 221.81 | 215.8 | 221.12 | 0 | 34.29 | 50.91 | 15636 | 95.58 | 42.26 | 37.48 | 1.59 | 42.26 | 0 | 606 | 427.8 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.4 | 310.2 | 0 | 304 | 100.07 | 15726 | 15725 | 315
03/26/22 11:11:11.176 | 545.8595 | 1368.6709 | 53.4103 | 43.867 | 9.5433 | 29.6367 | 51.0665 | 0 | 1778.0261 | 93.9498 | 85.3163 | 8.6336 | 24.6592 | 70.3998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9921 | 461.6301 | 458.6201 | 462.4701 | 409.8601 | 440.7301 | 417.0001 | 313.4801 | 0.57429 | -0.28282 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6576381.2469 | 7667674.4586 | 7667674.4586 | 62.4292 | 62.1341 | 1.0018 | 0.99791 | 685120.6804 | 886712.6174 | 460.9067 | 0.49612 | 0 | 0 | 29.6367 | 24.6592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017864 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.8839 | 1367.9489 | 53.5957 | 44.0466 | 28.8093 | 1786.8511 | 85.5044 | 24.598 | 461.6637 | 0.0065927 | 60.0047 | 0.5749 | -0.12225 | 94.0826 | 2.2208 | 0.10716 | 0.094579 | 5.4361 | 0.22506 | 0.31869 | 0 | 100 | 575.2 | 315 | 115.45 | 108.31 | 100.03 | 304.4 | 4 | 95.67 | 42.28 | 4 | 37.49 | 43.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.78 | 0 | 38.18 | 53 | 53 | 110.33 | 93.07 | 87.56 | 0 | 100.03 | 2.43 | 94.83 | 42.96 | 115.45 | 12.64 | 108.31 | 110 | 0 | 15725 | 83.08 | 117.35 | 221.81 | 215.8 | 221.12 | 0 | 34.39 | 50.89 | 15641 | 95.67 | 42.28 | 37.49 | 1.63 | 42.28 | 0 | 606 | 430.2 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.2 | 310.6 | 0 | 304.4 | 100.03 | 15722 | 15725 | 315
03/26/22 11:11:16.176 | 546.6876 | 1370.983 | 53.3996 | 43.858 | 9.5416 | 29.6666 | 51.0719 | 0 | 1781.5924 | 93.9471 | 85.3158 | 8.6313 | 24.5875 | 70.4055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9971 | 461.6501 | 458.6301 | 462.4701 | 409.9201 | 440.7601 | 416.9201 | 313.4901 | 0.57344 | -0.32506 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6586388.8359 | 7680953.7285 | 7680953.7285 | 62.4292 | 62.1341 | 1.0018 | 0.99791 | 686278.5267 | 888491.1899 | 460.9167 | 0.49611 | 0 | 0 | 29.6666 | 24.5875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017868 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.8413 | 1367.9708 | 53.5921 | 44.0439 | 28.8006 | 1786.8274 | 85.5083 | 24.6024 | 461.66 | 0.0065849 | 60.0046 | 0.57496 | -0.12494 | 94.0863 | 2.2312 | 0.10238 | 0.092733 | 5.4498 | 0.21565 | 0.32344 | 0 | 100 | 575.5 | 317 | 115.4 | 108.33 | 100.12 | 306.9 | 4 | 95.65 | 42.28 | 4 | 37.49 | 43.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.78 | 0 | 38.19 | 53 | 53 | 110.35 | 93.08 | 87.65 | 0 | 100.12 | 2.43 | 94.83 | 42.96 | 115.4 | 12.69 | 108.33 | 110 | 0 | 15725 | 83.08 | 117.35 | 221.68 | 215.8 | 221.12 | 0 | 34.4 | 50.79 | 15646 | 95.65 | 42.28 | 37.49 | 1.62 | 42.28 | 0 | 606 | 430.5 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.5 | 311.5 | 0 | 305.3 | 100.09 | 15724 | 15725 | 317
03/26/22 11:11:21.176 | 547.085 | 1371.6385 | 53.3846 | 43.8438 | 9.5407 | 29.7386 | 51.0624 | 0 | 1780.2918 | 93.9477 | 85.3211 | 8.6266 | 24.565 | 70.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 461.6801 | 458.5901 | 462.4701 | 410.0501 | 440.8301 | 416.7401 | 313.4901 | 0.57302 | -0.1094 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6591346.9742 | 7669472.7301 | 7669472.7301 | 62.4293 | 62.1341 | 1.0018 | 0.99791 | 686837.1554 | 887620.5998 | 460.9134 | 0.50407 | 0 | 0 | 29.7386 | 24.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017874 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.8063 | 1367.9868 | 53.5885 | 44.041 | 28.7912 | 1786.8411 | 85.512 | 24.6064 | 461.6564 | 0.0065985 | 60.0045 | 0.57501 | -0.12976 | 94.0899 | 2.2505 | 0.098202 | 0.090932 | 5.4288 | 0.20643 | 0.32814 | 0 | 100 | 575.7 | 318 | 115.4 | 108.33 | 100.12 | 307.4 | 4 | 95.65 | 42.28 | 4 | 37.49 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.83 | 0 | 38.18 | 53 | 53 | 110.38 | 93.09 | 87.67 | 0 | 100.12 | 2.43 | 94.85 | 42.96 | 115.4 | 12.69 | 108.33 | 110 | 0 | 15725 | 83.06 | 117.33 | 221.68 | 215.69 | 221.12 | 0 | 34.48 | 50.81 | 15651 | 95.65 | 42.28 | 37.49 | 1.58 | 42.28 | 0 | 606 | 427.9 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7 | 312.1 | 0 | 305.9 | 100.12 | 15724 | 15725 | 316
03/26/22 11:11:26.176 | 544.8132 | 1366.3124 | 53.3732 | 43.8318 | 9.5413 | 29.2472 | 51.0676 | 0 | 1785.6283 | 93.9526 | 85.3311 | 8.6215 | 24.855 | 70.4192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0041 | 461.6801 | 458.5901 | 462.4701 | 410.0501 | 440.8301 | 416.7401 | 313.4901 | 0.57541 | -0.74221 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6563438.5742 | 7689975.5522 | 7689975.5522 | 62.4293 | 62.134 | 1.0018 | 0.99791 | 683941.6579 | 890501.6858 | 460.9134 | 0.50407 | 0 | 0 | 29.2472 | 24.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017868 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.7649 | 1367.9683 | 53.585 | 44.0382 | 28.7834 | 1786.8758 | 85.5156 | 24.6065 | 461.6526 | 0.0066339 | 60.0044 | 0.57506 | -0.13762 | 94.0934 | 2.2402 | 0.094511 | 0.089207 | 5.3863 | 0.1973 | 0.33274 | 0 | 100 | 574.7 | 316 | 115.45 | 108.35 | 99.95 | 307.1 | 4 | 95.67 | 42.26 | 4 | 37.48 | 43.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.8 | 0 | 38.16 | 53 | 53 | 110.38 | 93.09 | 87.63 | 0 | 99.95 | 2.43 | 94.84 | 42.95 | 115.45 | 12.68 | 108.35 | 110 | 0 | 15727 | 83.06 | 117.33 | 221.68 | 215.69 | 221 | 0 | 34.55 | 50.83 | 15656 | 95.67 | 42.26 | 37.48 | 1.55 | 42.26 | 0 | 606 | 430.1 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7 | 311 | 0 | 304.7 | 100.12 | 15726 | 15727 | 316
03/26/22 11:11:31.176 | 544.4773 | 1365.3731 | 53.3666 | 43.8246 | 9.542 | 28.9663 | 51.055 | 0 | 1788.0024 | 93.9571 | 85.3395 | 8.6176 | 25.1427 | 70.4274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 461.7301 | 458.5801 | 462.5101 | 410.2801 | 441.1501 | 416.7201 | 313.6401 | 0.57604 | -0.89044 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6559142.9003 | 7697048.7204 | 7697048.7204 | 62.4293 | 62.1339 | 1.0018 | 0.99791 | 683471.738 | 891684.3899 | 460.9401 | 0.512 | 0 | 0 | 28.9663 | 25.1427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017866 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.7369 | 1367.961 | 53.5818 | 44.0353 | 28.7755 | 1786.8921 | 85.519 | 24.6028 | 461.6488 | 0.0066258 | 60.0043 | 0.5751 | -0.14357 | 94.0969 | 2.2441 | 0.09148 | 0.087591 | 5.3794 | 0.1885 | 0.33725 | 0 | 100 | 576.3 | 317 | 115.38 | 108.37 | 100.17 | 304.8 | 4 | 95.63 | 42.26 | 4 | 37.48 | 43.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.78 | 0 | 38.16 | 53 | 53 | 110.33 | 93.07 | 87.71 | 0 | 100.17 | 2.43 | 94.83 | 42.96 | 115.35 | 12.75 | 108.37 | 110 | 0 | 15729 | 83.06 | 117.33 | 221.68 | 215.69 | 221 | 0 | 34.59 | 50.71 | 15661 | 95.62 | 42.26 | 37.48 | 1.53 | 42.26 | 0 | 606 | 432.3 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 311.9 | 0 | 305.6 | 100.19 | 15728 | 15729 | 317
03/26/22 11:11:36.176 | 544.6562 | 1365.6776 | 53.3618 | 43.8188 | 9.543 | 29.2269 | 51.0566 | 0 | 1789.9429 | 93.962 | 85.3477 | 8.6144 | 25.1264 | 70.4146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.018 | 461.75 | 458.57 | 462.53 | 410.41 | 441.31 | 416.71 | 313.72 | 0.576 | -0.92282 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6561524.6558 | 7702461.635 | 7702461.635 | 62.4293 | 62.1338 | 1.0018 | 0.99791 | 683624.3591 | 892650.9157 | 460.95 | 0.51632 | 0 | 0 | 29.2269 | 25.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017861 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.7249 | 1367.9649 | 53.5787 | 44.0325 | 28.7631 | 1786.9008 | 85.5222 | 24.6082 | 461.6451 | 0.0066393 | 60.0043 | 0.57513 | -0.1482 | 94.1003 | 2.2393 | 0.08953 | 0.086325 | 5.3819 | 0.18048 | 0.34135 | 0 | 100 | 576.4 | 315 | 115.33 | 108.37 | 100.24 | 307.7 | 4 | 95.61 | 42.28 | 4 | 37.49 | 43.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.73 | 0 | 38.18 | 53 | 53 | 110.3 | 93.05 | 87.67 | 0 | 100.24 | 2.43 | 94.8 | 42.96 | 115.33 | 12.77 | 108.37 | 110 | 0 | 15729 | 83.04 | 117.33 | 221.68 | 215.69 | 221 | 0 | 34.51 | 50.5 | 15666 | 95.61 | 42.28 | 37.49 | 1.52 | 42.28 | 0 | 606 | 430 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 313.3 | 0 | 307 | 100.24 | 15728 | 15729 | 315
03/26/22 11:11:41.176 | 546.0972 | 1368.7896 | 53.3561 | 43.8096 | 9.5464 | 29.5798 | 51.0665 | 0 | 1790.3248 | 93.972 | 85.3618 | 8.6102 | 24.8413 | 70.4633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 461.77 | 458.56 | 462.52 | 410.56 | 441.41 | 416.74 | 313.79 | 0.5746 | -0.65343 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6579185.4875 | 7700031.6687 | 7700031.6687 | 62.4293 | 62.1337 | 1.0019 | 0.99791 | 685182.4384 | 892839.2625 | 460.95 | 0.51849 | 0 | 0 | 29.5798 | 24.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01622 | 0.017862 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.7277 | 1367.9784 | 53.5759 | 44.0298 | 28.7563 | 1786.9388 | 85.5251 | 24.6082 | 461.6413 | 0.0066745 | 60.0043 | 0.57514 | -0.1534 | 94.1036 | 2.2321 | 0.08855 | 0.08547 | 5.3864 | 0.17333 | 0.34526 | 0 | 100 | 576.6 | 319 | 115.38 | 108.35 | 100.28 | 307.5 | 4 | 95.65 | 42.28 | 4 | 37.49 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.75 | 0 | 38.18 | 53 | 53 | 110.3 | 93.05 | 87.75 | 0 | 100.28 | 2.43 | 94.82 | 42.96 | 115.38 | 12.71 | 108.35 | 110 | 0 | 15729 | 83.04 | 117.33 | 221.68 | 215.69 | 221 | 0 | 34.38 | 50.18 | 15671 | 95.65 | 42.28 | 37.49 | 1.48 | 42.28 | 0 | 606 | 430.7 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 313.8 | 0 | 307.5 | 100.28 | 15728 | 15729 | 319
03/26/22 11:11:46.175 | 546.7482 | 1369.9767 | 53.3541 | 43.8047 | 9.5494 | 29.7655 | 51.0661 | 0 | 1790.0048 | 93.9777 | 85.3694 | 8.6083 | 24.6941 | 70.4609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.01 | 461.75 | 458.53 | 462.51 | 410.68 | 441.55 | 416.81 | 313.86 | 0.57405 | -0.53234 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6587102.812 | 7698672.7708 | 7698672.7708 | 62.4294 | 62.1336 | 1.0019 | 0.99791 | 685830.9666 | 892848.6388 | 460.93 | 0.52069 | 0 | 0 | 29.7655 | 24.6941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017858 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.7397 | 1367.9907 | 53.5734 | 44.0271 | 28.7524 | 1786.9334 | 85.5278 | 24.6039 | 461.6373 | 0.006666 | 60.0042 | 0.57514 | -0.15607 | 94.1067 | 2.2376 | 0.088356 | 0.085013 | 5.3826 | 0.16707 | 0.34908 | 0 | 100 | 576.4 | 316 | 115.4 | 108.35 | 100.24 | 305.2 | 4 | 95.65 | 42.28 | 4 | 37.49 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.75 | 0 | 38.18 | 53 | 53 | 110.33 | 93.07 | 87.67 | 0 | 100.24 | 2.43 | 94.82 | 42.96 | 115.38 | 12.72 | 108.35 | 110 | 0 | 15729 | 83.04 | 117.33 | 221.68 | 215.69 | 221 | 0 | 34.13 | 49.86 | 15676 | 95.63 | 42.28 | 37.49 | 1.48 | 42.28 | 0 | 606 | 429.7 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 312.3 | 0 | 306.1 | 100.28 | 15731 | 15729 | 318
03/26/22 11:11:51.175 | 546.1487 | 1367.3807 | 53.3528 | 43.7991 | 9.5537 | 29.6665 | 51.0576 | 0 | 1789.1636 | 93.9842 | 85.3782 | 8.606 | 24.4266 | 70.4283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.007 | 461.73 | 458.48 | 462.48 | 410.85 | 441.69 | 416.87 | 313.93 | 0.57481 | -0.5444 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6579965.4065 | 7692665.0309 | 7692665.0309 | 62.4294 | 62.1335 | 1.0019 | 0.99791 | 684787.3002 | 892427.8353 | 460.8967 | 0.52434 | 0 | 0 | 29.6665 | 24.4266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017862 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.7492 | 1367.9832 | 53.571 | 44.0246 | 28.7473 | 1786.8997 | 85.5303 | 24.6011 | 461.6329 | 0.0067214 | 60.0042 | 0.57514 | -0.15871 | 94.1097 | 2.2352 | 0.08861 | 0.084861 | 5.347 | 0.16137 | 0.35297 | 1 | 100 | 576.3 | 315 | 115.38 | 108.35 | 100.23 | 306.6 | 4 | 95.63 | 42.28 | 4 | 37.49 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.78 | 0 | 38.18 | 53 | 53 | 110.35 | 93.08 | 87.69 | 0 | 100.23 | 2.43 | 94.83 | 42.96 | 115.4 | 12.72 | 108.35 | 110 | 0 | 15729 | 83.04 | 117.3 | 221.68 | 215.69 | 221 | 0 | 33.94 | 49.7 | 15681 | 95.65 | 42.26 | 37.48 | 1.55 | 42.26 | 0 | 606 | 432.5 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 312.5 | 0 | 306.3 | 100.24 | 15726 | 15729 | 316
03/26/22 11:11:56.175 | 546.2161 | 1368.2839 | 53.3526 | 43.7956 | 9.557 | 29.7212 | 51.0609 | 0 | 1788.2656 | 93.9884 | 85.3838 | 8.6046 | 24.0269 | 70.4142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 461.7301 | 458.4801 | 462.4801 | 410.8501 | 441.6901 | 416.8701 | 313.9301 | 0.57474 | -0.41201 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6580700.831 | 7683465.482 | 7683465.482 | 62.4294 | 62.1335 | 1.0019 | 0.99791 | 684634.8859 | 891549.3157 | 460.8967 | 0.52434 | 0 | 0 | 29.7212 | 24.0269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017859 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.7669 | 1367.977 | 53.569 | 44.0222 | 28.741 | 1786.8725 | 85.5324 | 24.5951 | 461.6282 | 0.0068196 | 60.004 | 0.57513 | -0.16093 | 94.1124 | 2.2328 | 0.08943 | 0.085222 | 5.3274 | 0.15676 | 0.35711 | 1 | 100 | 576.4 | 319 | 115.35 | 108.35 | 100.24 | 306.6 | 4 | 95.62 | 42.29 | 4 | 37.5 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.78 | 0 | 38.18 | 53 | 53 | 110.35 | 93.07 | 87.73 | 0 | 100.24 | 2.43 | 94.83 | 42.96 | 115.35 | 12.73 | 108.35 | 110 | 0 | 15729 | 83.04 | 117.3 | 221.68 | 215.69 | 221 | 0 | 33.76 | 49.64 | 15686 | 95.62 | 42.29 | 37.5 | 1.52 | 42.29 | 0 | 606 | 429.2 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 311.2 | 0 | 305 | 100.24 | 15729 | 15729 | 315
03/26/22 11:12:01.176 | 545.6526 | 1365.084 | 53.354 | 43.7895 | 9.5645 | 29.8036 | 51.0607 | 0 | 1785.1535 | 93.9967 | 85.3947 | 8.6021 | 24.4192 | 70.4398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9981 | 461.7101 | 458.4501 | 462.4601 | 411.0201 | 441.8801 | 416.9801 | 314.0201 | 0.57549 | -0.32497 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6573975.8178 | 7670033.8108 | 7670033.8108 | 62.4294 | 62.1334 | 1.0019 | 0.99791 | 683327.5857 | 890255.4474 | 460.8734 | 0.52581 | 0 | 0 | 29.8036 | 24.4192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017864 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.7933 | 1367.9791 | 53.5672 | 44.0199 | 28.7399 | 1786.8684 | 85.5344 | 24.5818 | 461.6235 | 0.0068096 | 60.0039 | 0.57512 | -0.16333 | 94.115 | 2.2341 | 0.090467 | 0.085885 | 5.3261 | 0.15272 | 0.36115 | 1 | 100 | 576.2 | 317 | 115.38 | 108.35 | 100.21 | 307.5 | 4 | 95.63 | 42.28 | 4 | 37.49 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.83 | 0 | 38.18 | 53 | 53 | 110.38 | 93.09 | 87.71 | 0 | 100.21 | 2.43 | 94.85 | 42.96 | 115.4 | 12.71 | 108.35 | 110 | 0 | 15729 | 83.04 | 117.3 | 221.68 | 215.69 | 221 | 0 | 33.77 | 49.89 | 15691 | 95.65 | 42.28 | 37.49 | 1.5 | 42.28 | 0 | 606 | 426.5 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 312.8 | 0 | 306.6 | 100.19 | 15730 | 15729 | 317
03/26/22 11:12:06.175 | 544.572 | 1361.9513 | 53.355 | 43.7874 | 9.5676 | 28.9115 | 51.0626 | 0 | 1783.7445 | 94 | 85.3986 | 8.6014 | 25.7587 | 70.4101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.993 | 461.69 | 458.44 | 462.45 | 411.03 | 441.91 | 416.99 | 314.02 | 0.57664 | -0.43491 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6560168.2881 | 7664911.7097 | 7664911.7097 | 62.4294 | 62.1333 | 1.0019 | 0.99791 | 681759.3797 | 889552.2168 | 460.86 | 0.52511 | 0 | 0 | 28.9115 | 25.7587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.01786 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.8008 | 1367.9252 | 53.5656 | 44.0178 | 28.7297 | 1786.8318 | 85.5361 | 24.5863 | 461.6187 | 0.0068642 | 60.0037 | 0.57512 | -0.16743 | 94.1174 | 2.2618 | 0.091654 | 0.08691 | 5.3248 | 0.14932 | 0.36534 | 1 | 100 | 575.7 | 316 | 115.5 | 108.37 | 100.12 | 307 | 4 | 95.7 | 42.28 | 4 | 37.49 | 43.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.88 | 0 | 38.18 | 53 | 53 | 110.45 | 93.14 | 87.65 | 0 | 100.12 | 2.43 | 94.88 | 42.96 | 115.48 | 12.69 | 108.37 | 110 | 0 | 15729 | 83.02 | 117.3 | 221.68 | 215.69 | 221 | 0 | 33.81 | 50.08 | 15696 | 95.7 | 42.28 | 37.49 | 1.46 | 42.28 | 0 | 606 | 431.3 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7 | 313.3 | 0 | 307 | 100.12 | 15724 | 15729 | 316
03/26/22 11:12:11.175 | 545.171 | 1363.9641 | 53.3561 | 43.7857 | 9.5705 | 29.374 | 51.0694 | 0 | 1786.707 | 94.0029 | 85.4026 | 8.6003 | 24.8987 | 70.3754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.993 | 461.69 | 458.44 | 462.45 | 411.03 | 441.91 | 416.99 | 314.02 | 0.576 | -0.4212 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6567675.515 | 7671399.8757 | 7671399.8757 | 62.4294 | 62.1333 | 1.0019 | 0.99791 | 682343.2025 | 890483.4499 | 460.86 | 0.52511 | 0 | 0 | 29.374 | 24.8987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017858 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.819 | 1367.9009 | 53.5642 | 44.0159 | 28.7227 | 1786.8399 | 85.5376 | 24.5848 | 461.614 | 0.0068758 | 60.0035 | 0.57511 | -0.17184 | 94.1195 | 2.2808 | 0.092924 | 0.088219 | 5.3235 | 0.14657 | 0.36963 | 1 | 100 | 576.1 | 316 | 115.48 | 108.37 | 100.19 | 307 | 4 | 95.68 | 42.29 | 4 | 37.5 | 43.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.85 | 0 | 38.19 | 53 | 53 | 110.4 | 93.1 | 87.65 | 0 | 100.19 | 2.43 | 94.87 | 42.97 | 115.48 | 12.69 | 108.37 | 110 | 0 | 15729 | 83.02 | 117.3 | 221.68 | 215.69 | 221 | 0 | 33.83 | 50.14 | 15701 | 95.68 | 42.29 | 37.5 | 1.46 | 42.29 | 0 | 606 | 429.3 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7 | 313.4 | 0 | 307.2 | 100.12 | 15728 | 15729 | 317
03/26/22 11:12:16.177 | 547.2308 | 1368.129 | 53.3584 | 43.7838 | 9.5747 | 29.7778 | 51.0659 | 0 | 1788.343 | 94.0067 | 85.4068 | 8.5999 | 24.4524 | 70.3593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9891 | 461.6701 | 458.4201 | 462.4301 | 411.0201 | 441.8501 | 417.0001 | 313.9901 | 0.57378 | -0.24288 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6593018.2467 | 7683033.9485 | 7683033.9485 | 62.4294 | 62.1333 | 1.0019 | 0.99791 | 684624.3264 | 892003.8965 | 460.8401 | 0.52513 | 0 | 0 | 29.7778 | 24.4524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016229 | 0.017861 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.8492 | 1367.9028 | 53.563 | 44.0142 | 28.7173 | 1786.847 | 85.5389 | 24.5814 | 461.6093 | 0.0069089 | 60.0033 | 0.57509 | -0.17443 | 94.1215 | 2.2808 | 0.094175 | 0.089678 | 5.3247 | 0.14422 | 0.37405 | 1 | 100 | 576.5 | 317 | 115.43 | 108.37 | 100.16 | 307.7 | 4 | 95.66 | 42.3 | 4 | 37.51 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.85 | 0 | 38.2 | 53 | 53 | 110.4 | 93.12 | 87.65 | 0 | 100.16 | 2.43 | 94.87 | 42.99 | 115.43 | 12.72 | 108.37 | 110 | 0 | 15729 | 83.02 | 117.33 | 221.68 | 215.69 | 221 | 0 | 33.76 | 50.08 | 15706 | 95.66 | 42.3 | 37.51 | 1.55 | 42.3 | 0 | 606 | 427.3 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.5 | 314 | 0 | 307.7 | 100.26 | 15730 | 15729 | 317
03/26/22 11:12:21.175 | 549.0608 | 1371.4321 | 53.3616 | 43.7818 | 9.5797 | 28.8612 | 51.0587 | 0 | 1790.6913 | 94.0112 | 85.4108 | 8.6004 | 25.7107 | 70.4138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 461.66 | 458.44 | 462.42 | 410.96 | 441.7 | 416.96 | 313.94 | 0.57178 | -0.11025 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6614166.0224 | 7693851.4442 | 7693851.4442 | 62.4294 | 62.1332 | 1.0019 | 0.99791 | 686504.9313 | 893014.7263 | 460.84 | 0.52079 | 0 | 0 | 28.8612 | 25.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017848 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.8891 | 1367.9243 | 53.562 | 44.0126 | 28.709 | 1786.8527 | 85.5401 | 24.5812 | 461.6045 | 0.0068987 | 60.0031 | 0.57506 | -0.17514 | 94.1233 | 2.2958 | 0.09536 | 0.09124 | 5.3282 | 0.14223 | 0.37836 | 1 | 100 | 575.8 | 318 | 115.43 | 108.37 | 100.1 | 307.5 | 4 | 95.67 | 42.3 | 4 | 37.51 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.83 | 0 | 38.2 | 53 | 53 | 110.4 | 93.1 | 87.67 | 0 | 100.1 | 2.43 | 94.85 | 42.99 | 115.43 | 12.72 | 108.37 | 110 | 0 | 15729 | 83.02 | 117.33 | 221.68 | 215.69 | 221 | 0 | 33.67 | 50.05 | 15711 | 95.66 | 42.3 | 37.51 | 1.67 | 42.3 | 0 | 606 | 429.6 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 313.5 | 0 | 307.3 | 100.14 | 15728 | 15729 | 318
03/26/22 11:12:26.175 | 548.6967 | 1370.0747 | 53.3635 | 43.7807 | 9.5829 | 29.5951 | 51.0611 | 0 | 1793.7259 | 94.0146 | 85.4145 | 8.6002 | 24.882 | 70.4249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 461.66 | 458.46 | 462.44 | 410.91 | 441.68 | 416.96 | 313.94 | 0.57216 | -0.31285 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6610417.5587 | 7705694.5386 | 7705694.5386 | 62.4294 | 62.1332 | 1.0019 | 0.99791 | 685825.3985 | 894527.5574 | 460.8534 | 0.51933 | 0 | 0 | 29.5951 | 24.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017845 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.931 | 1367.9509 | 53.561 | 44.0111 | 28.7007 | 1786.8761 | 85.5412 | 24.5821 | 461.5998 | 0.0068886 | 60.0029 | 0.57502 | -0.17627 | 94.1249 | 2.2994 | 0.096475 | 0.092826 | 5.3514 | 0.14046 | 0.38241 | 1 | 100 | 576.3 | 317 | 115.4 | 108.37 | 100.24 | 307.1 | 4 | 95.65 | 42.29 | 4 | 37.5 | 43.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.8 | 0 | 38.19 | 53 | 53 | 110.38 | 93.09 | 87.69 | 0 | 100.24 | 2.43 | 94.84 | 42.97 | 115.4 | 12.71 | 108.35 | 110 | 0 | 15729 | 83.02 | 117.33 | 221.68 | 215.69 | 221 | 0 | 33.7 | 50.23 | 15716 | 95.65 | 42.28 | 37.49 | 1.68 | 42.28 | 0 | 606 | 428.7 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 312.2 | 0 | 306 | 100.19 | 15728 | 15729 | 317
03/26/22 11:12:31.175 | 547.9324 | 1367.6697 | 53.3643 | 43.7805 | 9.5837 | 30.2359 | 51.0702 | 0 | 1789.3545 | 94.0167 | 85.4173 | 8.5994 | 24.0419 | 70.4171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.988 | 461.66 | 458.46 | 462.44 | 410.91 | 441.68 | 416.96 | 313.94 | 0.57295 | -0.21843 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6601680.8053 | 7689666.562 | 7689666.562 | 62.4294 | 62.1331 | 1.0019 | 0.99791 | 684822.9907 | 892818.2487 | 460.8534 | 0.51933 | 0 | 0 | 30.2359 | 24.0419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017856 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.9694 | 1367.9646 | 53.5602 | 44.0097 | 28.6959 | 1786.8768 | 85.5423 | 24.5809 | 461.5951 | 0.0068785 | 60.0027 | 0.57499 | -0.17667 | 94.1265 | 2.2902 | 0.097529 | 0.094392 | 5.3518 | 0.13883 | 0.38636 | 1 | 100 | 577.1 | 316 | 115.45 | 108.35 | 100.37 | 306.1 | 4 | 95.67 | 42.29 | 4 | 37.5 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.83 | 0 | 38.19 | 53 | 53 | 110.4 | 93.1 | 87.69 | 0 | 100.37 | 2.43 | 94.85 | 42.97 | 115.45 | 12.68 | 108.35 | 110 | 0 | 15729 | 83.02 | 117.35 | 221.68 | 215.69 | 221 | 0 | 33.9 | 50.64 | 15721 | 95.67 | 42.29 | 37.5 | 1.54 | 42.29 | 0 | 606 | 431.3 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 314.7 | 0 | 308.4 | 100.28 | 15726 | 15729 | 318
03/26/22 11:12:36.175 | 548.6368 | 1369.6412 | 53.3659 | 43.7811 | 9.5849 | 29.9243 | 51.0661 | 0 | 1781.8969 | 94.0211 | 85.4227 | 8.5984 | 24.1998 | 70.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.985 | 461.69 | 458.51 | 462.46 | 410.91 | 441.48 | 416.98 | 313.95 | 0.57224 | 0.37345 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6609979.5558 | 7652554.7151 | 7652554.7151 | 62.4294 | 62.1331 | 1.0019 | 0.99791 | 685608.2868 | 888627.2398 | 460.8867 | 0.51567 | 0 | 0 | 29.9243 | 24.1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017864 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 545.9988 | 1367.9647 | 53.5594 | 44.0085 | 28.6924 | 1786.8712 | 85.5432 | 24.579 | 461.5904 | 0.0068683 | 60.0025 | 0.57497 | -0.17731 | 94.128 | 2.2902 | 0.098512 | 0.095924 | 5.3523 | 0.13735 | 0.38999 | 1 | 100 | 576.6 | 317 | 115.45 | 108.35 | 100.28 | 307 | 4 | 95.67 | 42.3 | 4 | 37.51 | 43.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.83 | 0 | 38.2 | 53 | 53 | 110.4 | 93.1 | 87.69 | 0 | 100.28 | 2.43 | 94.85 | 42.99 | 115.45 | 12.68 | 108.35 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.68 | 215.69 | 221 | 0 | 34.21 | 51.15 | 15726 | 95.67 | 42.3 | 37.51 | 1.43 | 42.3 | 0 | 606 | 432.3 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.7 | 313 | 0 | 306.8 | 100.3 | 15728 | 15729 | 316
03/26/22 11:12:41.175 | 547.766 | 1367.3858 | 53.3669 | 43.7815 | 9.5854 | 29.7924 | 51.0622 | 0 | 1782.4079 | 94.0237 | 85.425 | 8.5986 | 24.5768 | 70.4183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9851 | 461.6901 | 458.5101 | 462.4601 | 410.9101 | 441.4801 | 416.9801 | 313.9501 | 0.57315 | 0.19914 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6599370.8922 | 7655352.0664 | 7655352.0664 | 62.4294 | 62.1331 | 1.0019 | 0.99791 | 684479.2619 | 888881.6994 | 460.8867 | 0.51567 | 0 | 0 | 29.7924 | 24.5768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.017863 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.0306 | 1367.9732 | 53.5587 | 44.0073 | 28.6814 | 1786.864 | 85.5442 | 24.5868 | 461.5857 | 0.0068582 | 60.0023 | 0.57494 | -0.1773 | 94.1294 | 2.2851 | 0.099422 | 0.0974 | 5.3574 | 0.13592 | 0.39336 | 1 | 100 | 576.8 | 316 | 115.5 | 108.35 | 100.31 | 305.2 | 4 | 95.7 | 42.3 | 4 | 37.51 | 43.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.85 | 0 | 38.2 | 53 | 53 | 110.38 | 93.09 | 87.71 | 0 | 100.31 | 2.43 | 94.87 | 42.99 | 115.5 | 12.66 | 108.35 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.68 | 215.69 | 221 | 0 | 34.45 | 51.19 | 15731 | 95.7 | 42.3 | 37.51 | 1.38 | 42.3 | 0 | 606 | 430.8 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 312.1 | 0 | 305.9 | 100.28 | 15730 | 15729 | 318
03/26/22 11:12:46.175 | 546.7034 | 1364.6453 | 53.368 | 43.7819 | 9.5861 | 29.6804 | 51.0692 | 0 | 1784.7922 | 94.0265 | 85.4272 | 8.5993 | 24.7192 | 70.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.992 | 461.73 | 458.55 | 462.49 | 410.97 | 441.44 | 417.04 | 314 | 0.57435 | -0.11229 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6586468.6101 | 7666313.7043 | 7666313.7043 | 62.4294 | 62.133 | 1.0019 | 0.99791 | 683107.3935 | 890070.4605 | 460.9234 | 0.51491 | 0 | 0 | 29.6804 | 24.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016236 | 0.017861 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.0554 | 1367.9669 | 53.5581 | 44.0062 | 28.6715 | 1786.8972 | 85.5451 | 24.5935 | 461.5811 | 0.0068483 | 60.0021 | 0.57492 | -0.18026 | 94.1308 | 2.2928 | 0.10027 | 0.098819 | 5.3258 | 0.13455 | 0.39623 | 1 | 100 | 577 | 316 | 115.48 | 108.35 | 100.35 | 306.9 | 4 | 95.68 | 42.29 | 4 | 37.5 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.8 | 0 | 38.19 | 53 | 53 | 110.38 | 93.09 | 87.73 | 0 | 100.35 | 2.43 | 94.84 | 42.97 | 115.48 | 12.67 | 108.35 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.68 | 215.69 | 221 | 0 | 34.44 | 50.77 | 15736 | 95.68 | 42.29 | 37.5 | 1.35 | 42.29 | 0 | 606 | 429.6 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 315.1 | 0 | 308.8 | 100.24 | 15728 | 15729 | 318
03/26/22 11:12:51.175 | 547.1672 | 1365.5485 | 53.3709 | 43.7831 | 9.5879 | 28.6178 | 51.0591 | 0 | 1785.4425 | 94.0313 | 85.4298 | 8.6015 | 26.1378 | 70.4452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 461.81 | 458.62 | 462.54 | 411.11 | 441.37 | 417.09 | 314.08 | 0.57401 | -0.12939 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6591119.3415 | 7672725.5211 | 7672725.5211 | 62.4294 | 62.133 | 1.0019 | 0.99791 | 683559.386 | 890394.3585 | 460.99 | 0.51411 | 0 | 0 | 28.6178 | 26.1378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016232 | 0.017857 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.0797 | 1367.963 | 53.5575 | 44.0052 | 28.6559 | 1786.9357 | 85.546 | 24.6064 | 461.5765 | 0.0068383 | 60.002 | 0.5749 | -0.18367 | 94.1321 | 2.2967 | 0.10104 | 0.10017 | 5.2882 | 0.13325 | 0.39864 | 1 | 100 | 576.3 | 317 | 115.4 | 108.35 | 100.23 | 305.2 | 4 | 95.65 | 42.31 | 4 | 37.53 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.78 | 0 | 38.21 | 53 | 53 | 110.38 | 93.09 | 87.73 | 0 | 100.23 | 2.43 | 94.83 | 43 | 115.4 | 12.71 | 108.35 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.68 | 215.69 | 220.88 | 0 | 34.19 | 50.41 | 15741 | 95.65 | 42.31 | 37.54 | 1.3 | 42.31 | 0 | 606 | 429.2 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 311.4 | 0 | 305.2 | 100.23 | 15728 | 15729 | 317
03/26/22 11:12:56.175 | 547.1516 | 1365.3112 | 53.3732 | 43.7839 | 9.5892 | 29.155 | 51.0587 | 0 | 1790.041 | 94.0338 | 85.4306 | 8.6032 | 25.5861 | 70.4423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 461.81 | 458.62 | 462.54 | 411.11 | 441.37 | 417.09 | 314.08 | 0.57403 | -0.39378 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6591399.7805 | 7693319.865 | 7693319.865 | 62.4294 | 62.133 | 1.0019 | 0.99791 | 683440.4651 | 892687.4837 | 460.99 | 0.51411 | 0 | 0 | 29.155 | 25.5861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016235 | 0.017849 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.1026 | 1367.9573 | 53.557 | 44.0042 | 28.6437 | 1786.9921 | 85.5468 | 24.6161 | 461.5719 | 0.0068286 | 60.0019 | 0.57489 | -0.18811 | 94.1333 | 2.3021 | 0.10174 | 0.10145 | 5.2666 | 0.13202 | 0.40065 | 1 | 100 | 576.3 | 314 | 115.33 | 108.37 | 100.23 | 305.5 | 4 | 95.61 | 42.3 | 4 | 37.51 | 43.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.75 | 0 | 38.2 | 53 | 53 | 110.3 | 93.05 | 87.71 | 0 | 100.23 | 2.43 | 94.82 | 42.99 | 115.35 | 12.77 | 108.37 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.68 | 215.69 | 220.88 | 0 | 34.07 | 50.18 | 15746 | 95.61 | 42.3 | 37.51 | 1.32 | 42.3 | 0 | 606 | 428.3 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 309.9 | 0 | 303.7 | 100.21 | 15728 | 15729 | 315
03/26/22 11:13:01.175 | 547.215 | 1365.1976 | 53.376 | 43.785 | 9.5911 | 29.4846 | 51.0828 | 0 | 1794.082 | 94.036 | 85.4301 | 8.6059 | 24.9937 | 70.4312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 461.81 | 458.62 | 462.54 | 411.11 | 441.37 | 417.09 | 314.08 | 0.57396 | -0.57349 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6592356.4754 | 7708120.3986 | 7708120.3986 | 62.4294 | 62.133 | 1.0019 | 0.99791 | 683414.5187 | 894236.9302 | 460.99 | 0.51411 | 0 | 0 | 29.4846 | 24.9937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016231 | 0.01785 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.1269 | 1367.956 | 53.5566 | 44.0033 | 28.6304 | 1787.0851 | 85.5476 | 24.6247 | 461.5674 | 0.0068188 | 60.0018 | 0.57487 | -0.19412 | 94.1345 | 2.3036 | 0.10238 | 0.10267 | 5.243 | 0.13086 | 0.40259 | 1 | 100 | 576.4 | 317 | 115.38 | 108.37 | 100.24 | 307.8 | 4 | 95.63 | 42.33 | 4 | 37.54 | 43.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.78 | 0 | 38.21 | 53 | 53 | 110.35 | 93.08 | 87.77 | 0 | 100.24 | 2.43 | 94.83 | 43 | 115.38 | 12.74 | 108.37 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.68 | 215.69 | 220.88 | 0 | 33.85 | 49.93 | 15751 | 95.63 | 42.33 | 37.54 | 1.31 | 42.33 | 0 | 606 | 429.2 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.9 | 313.1 | 0 | 306.9 | 100.16 | 15731 | 15729 | 315
03/26/22 11:13:06.175 | 548.5171 | 1368.5522 | 53.3794 | 43.7866 | 9.5928 | 29.7932 | 51.0818 | 0 | 1790.4384 | 94.0375 | 85.4285 | 8.609 | 24.5041 | 70.4481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0171 | 461.8701 | 458.6401 | 462.5501 | 411.2401 | 441.3801 | 417.1401 | 314.1301 | 0.57269 | -0.26915 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6608240.1592 | 7700794.569 | 7700794.569 | 62.4293 | 62.133 | 1.0019 | 0.99791 | 684905.0205 | 893104.6995 | 461.0201 | 0.51625 | 0 | 0 | 29.7932 | 24.5041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017861 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.1555 | 1367.9685 | 53.5561 | 44.0024 | 28.6205 | 1787.1645 | 85.5484 | 24.6257 | 461.563 | 0.0068094 | 60.0018 | 0.57484 | -0.19906 | 94.1357 | 2.3006 | 0.10296 | 0.10383 | 5.1845 | 0.1298 | 0.40424 | 1 | 100 | 576.2 | 317 | 115.45 | 108.37 | 100.21 | 305 | 4 | 95.68 | 42.3 | 4 | 37.51 | 43.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.8 | 0 | 38.2 | 53 | 53 | 110.38 | 93.09 | 87.71 | 0 | 100.21 | 2.43 | 94.84 | 42.99 | 115.48 | 12.69 | 108.37 | 110 | 0 | 15729 | 83.04 | 117.35 | 221.68 | 215.69 | 220.88 | 0 | 33.68 | 49.79 | 15756 | 95.68 | 42.3 | 37.51 | 1.35 | 42.3 | 0 | 606 | 429.5 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.3 | 315.1 | 0 | 308.9 | 100.23 | 15729 | 15729 | 317
03/26/22 11:13:11.175 | 549.3675 | 1370.307 | 53.3823 | 43.7893 | 9.593 | 29.8681 | 51.0655 | 0 | 1783.2955 | 94.0372 | 85.4259 | 8.6113 | 24.5078 | 70.4307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 461.8901 | 458.6401 | 462.5601 | 411.2501 | 441.3901 | 417.1601 | 314.1201 | 0.57179 | 0.26366 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6618711.4067 | 7670283.1744 | 7670283.1744 | 62.4293 | 62.133 | 1.0019 | 0.99791 | 685940.8458 | 889324.2475 | 461.0301 | 0.5184 | 0 | 0 | 29.8681 | 24.5078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017866 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.188 | 1367.9904 | 53.5557 | 44.0016 | 28.6157 | 1787.1716 | 85.549 | 24.62 | 461.5587 | 0.0068002 | 60.0018 | 0.57482 | -0.19973 | 94.1368 | 2.3041 | 0.10349 | 0.10491 | 5.1781 | 0.12887 | 0.40579 | 1 | 100 | 576 | 317 | 115.5 | 108.35 | 100.17 | 305.3 | 4 | 95.68 | 42.3 | 4 | 37.51 | 43.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.88 | 0 | 38.2 | 53 | 53 | 110.43 | 93.12 | 87.75 | 0 | 100.17 | 2.43 | 94.87 | 42.99 | 115.5 | 12.66 | 108.35 | 110 | 0 | 15729 | 83.04 | 117.35 | 221.68 | 215.69 | 220.88 | 0 | 33.58 | 49.83 | 15761 | 95.7 | 42.3 | 37.51 | 1.41 | 42.3 | 0 | 606 | 431.8 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7 | 312.3 | 0 | 306 | 100.12 | 15728 | 15729 | 318
03/26/22 11:13:16.175 | 549.9276 | 1372.1701 | 53.3846 | 43.7922 | 9.5924 | 29.6328 | 51.0795 | 0 | 1780.6067 | 94.0363 | 85.4236 | 8.6127 | 25.2036 | 70.4312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 461.9001 | 458.6501 | 462.5801 | 411.3401 | 441.4801 | 417.2301 | 314.1701 | 0.57129 | 0.46599 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6625288.2988 | 7661393.8598 | 7661393.8598 | 62.4293 | 62.133 | 1.0018 | 0.99791 | 686679.6259 | 888076.2977 | 461.0434 | 0.51911 | 0 | 0 | 29.6328 | 25.2036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017868 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.2201 | 1368.0146 | 53.5554 | 44.0009 | 28.6086 | 1787.146 | 85.5497 | 24.6204 | 461.5545 | 0.0067912 | 60.0018 | 0.57479 | -0.19813 | 94.1378 | 2.3175 | 0.10399 | 0.10594 | 5.1987 | 0.12801 | 0.40724 | 1 | 100 | 576.6 | 317 | 115.58 | 108.35 | 100.26 | 307.5 | 4 | 95.73 | 42.3 | 4 | 37.51 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.2 | 53 | 53 | 110.45 | 93.13 | 87.69 | 0 | 100.26 | 2.43 | 94.89 | 42.99 | 115.55 | 12.62 | 108.35 | 110 | 0 | 15729 | 83.04 | 117.35 | 221.68 | 215.58 | 220.88 | 0 | 33.63 | 50.17 | 15766 | 95.73 | 42.3 | 37.51 | 1.51 | 42.3 | 0 | 606 | 431.8 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 311.1 | 0 | 304.9 | 100.28 | 15726 | 15729 | 317
03/26/22 11:13:21.175 | 549.2328 | 1370.2295 | 53.3854 | 43.7942 | 9.5912 | 30.1256 | 51.0667 | 0 | 1782.0517 | 94.0363 | 85.4239 | 8.6124 | 24.6952 | 70.4258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.016 | 461.88 | 458.63 | 462.58 | 411.33 | 441.45 | 417.2 | 314.15 | 0.57198 | 0.30161 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6617320.1531 | 7666155.5895 | 7666155.5895 | 62.4293 | 62.133 | 1.0018 | 0.99791 | 685901.947 | 888704.2563 | 461.03 | 0.52057 | 0 | 0 | 30.1256 | 24.6952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.017869 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.2481 | 1368.0296 | 53.555 | 44.0002 | 28.6049 | 1787.0954 | 85.5501 | 24.6167 | 461.5504 | 0.0067823 | 60.0018 | 0.57477 | -0.19562 | 94.1387 | 2.3331 | 0.10446 | 0.10691 | 5.2033 | 0.12739 | 0.40863 | 1 | 100 | 577 | 315 | 115.53 | 108.37 | 100.35 | 307.2 | 4 | 95.71 | 42.29 | 4 | 37.5 | 43.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.9 | 0 | 38.19 | 53 | 53 | 110.43 | 93.12 | 87.73 | 0 | 100.35 | 2.43 | 94.89 | 42.97 | 115.53 | 12.67 | 108.37 | 110 | 0 | 15729 | 83.04 | 117.35 | 221.68 | 215.58 | 220.88 | 0 | 33.86 | 50.58 | 15771 | 95.71 | 42.29 | 37.5 | 1.48 | 42.29 | 0 | 606 | 427.3 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 313.8 | 0 | 307.5 | 100.28 | 15728 | 15729 | 316
03/26/22 11:13:26.175 | 548.1985 | 1367.9277 | 53.3849 | 43.7958 | 9.5891 | 29.5631 | 51.0692 | 0 | 1786.3663 | 94.0374 | 85.4268 | 8.6107 | 25.6347 | 70.4266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 461.8801 | 458.6301 | 462.5801 | 411.3301 | 441.4501 | 417.2001 | 314.1501 | 0.57306 | -0.04287 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6604329.5025 | 7679544.8115 | 7679544.8115 | 62.4293 | 62.133 | 1.0018 | 0.99791 | 684741.9915 | 890294.4841 | 461.0301 | 0.52057 | 0 | 0 | 29.5631 | 25.6347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016226 | 0.01786 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.2659 | 1368.0243 | 53.5547 | 43.9995 | 28.5985 | 1787.0593 | 85.5506 | 24.6173 | 461.5463 | 0.0067733 | 60.0018 | 0.57475 | -0.19561 | 94.1396 | 2.3323 | 0.10492 | 0.10783 | 5.1933 | 0.12682 | 0.41011 | 1 | 100 | 576.4 | 315 | 115.6 | 108.37 | 100.24 | 307 | 4 | 95.75 | 42.29 | 4 | 37.5 | 43.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.95 | 0 | 38.19 | 53 | 53 | 110.45 | 93.13 | 87.75 | 0 | 100.24 | 2.43 | 94.92 | 42.97 | 115.58 | 12.64 | 108.37 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.56 | 215.58 | 220.88 | 0 | 34.18 | 51.05 | 15776 | 95.73 | 42.29 | 37.5 | 1.43 | 42.29 | 0 | 606 | 429.2 | 459.1 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 313.4 | 0 | 307.2 | 100.19 | 15729 | 15729 | 316
03/26/22 11:13:31.175 | 548.292 | 1368.3509 | 53.3844 | 43.7965 | 9.5879 | 29.4004 | 51.0679 | 0 | 1790.4951 | 94.0383 | 85.4293 | 8.609 | 25.6072 | 70.4303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0161 | 461.8801 | 458.6301 | 462.5801 | 411.3301 | 441.4501 | 417.2001 | 314.1501 | 0.57296 | -0.30226 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6605356.5164 | 7700521.1685 | 7700521.1685 | 62.4293 | 62.1329 | 1.0018 | 0.99791 | 684961.6225 | 892914.1602 | 461.0301 | 0.52057 | 0 | 0 | 29.4004 | 25.6072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017854 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.2904 | 1368.0384 | 53.5543 | 43.9988 | 28.5865 | 1787.0359 | 85.5509 | 24.6256 | 461.5421 | 0.0067644 | 60.0018 | 0.57473 | -0.1954 | 94.1403 | 2.3265 | 0.10539 | 0.10872 | 5.1681 | 0.1264 | 0.41154 | 1 | 100 | 576 | 316 | 115.58 | 108.39 | 100.17 | 307.4 | 4 | 95.73 | 42.29 | 4 | 37.5 | 43.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.93 | 0 | 38.19 | 53 | 53 | 110.45 | 93.13 | 87.75 | 0 | 100.17 | 2.43 | 94.9 | 42.97 | 115.55 | 12.67 | 108.39 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.56 | 215.58 | 220.88 | 0 | 34.42 | 51.13 | 15781 | 95.72 | 42.3 | 37.51 | 1.43 | 42.3 | 0 | 606 | 429.1 | 459.2 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 313.3 | 0 | 307 | 100.14 | 15727 | 15729 | 317
03/26/22 11:13:36.174 | 548.1644 | 1368.3458 | 53.3835 | 43.7977 | 9.5857 | 29.383 | 51.0785 | 0 | 1791.6874 | 94.0403 | 85.4348 | 8.6055 | 25.5068 | 70.4766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.017 | 461.87 | 458.61 | 462.55 | 411.33 | 441.43 | 417.22 | 314.11 | 0.57302 | -0.34604 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6603810.0212 | 7702341.182 | 7702341.182 | 62.4293 | 62.1329 | 1.0018 | 0.99791 | 684959.0899 | 893507.8948 | 461.01 | 0.5206 | 0 | 0 | 29.383 | 25.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017851 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.3154 | 1368.0524 | 53.554 | 43.9981 | 28.5736 | 1787.023 | 85.5513 | 24.6347 | 461.538 | 0.0067555 | 60.0018 | 0.57471 | -0.19525 | 94.1411 | 2.3207 | 0.10586 | 0.10959 | 5.1535 | 0.12598 | 0.41312 | 1 | 100 | 577.1 | 317 | 115.53 | 108.41 | 100.37 | 304.6 | 4 | 95.7 | 42.31 | 4 | 37.53 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.88 | 0 | 38.21 | 53 | 53 | 110.48 | 93.16 | 87.81 | 0 | 100.37 | 2.43 | 94.88 | 43 | 115.5 | 12.72 | 108.41 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.56 | 215.58 | 220.88 | 0 | 34.45 | 51.06 | 15786 | 95.7 | 42.31 | 37.53 | 1.44 | 42.31 | 0 | 606 | 428 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 313.7 | 0 | 307.4 | 100.28 | 15728 | 15729 | 317
03/26/22 11:13:41.174 | 548.4622 | 1369.5793 | 53.3815 | 43.7992 | 9.5823 | 30.2259 | 51.0836 | 0 | 1788.89 | 94.046 | 85.4471 | 8.5989 | 23.874 | 70.4869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.012 | 461.77 | 458.53 | 462.44 | 411.5 | 441.45 | 417.47 | 314.15 | 0.57278 | -0.032451 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6608148.3784 | 7682564.9326 | 7682564.9326 | 62.4293 | 62.1328 | 1.0018 | 0.99791 | 685576.6195 | 892111.0597 | 460.9134 | 0.51709 | 0 | 0 | 30.2259 | 23.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017855 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.325 | 1368.0364 | 53.5536 | 43.9975 | 28.5668 | 1787.0183 | 85.5515 | 24.6319 | 461.5335 | 0.006746 | 60.0018 | 0.57471 | -0.19766 | 94.1417 | 2.2983 | 0.10636 | 0.11043 | 5.1508 | 0.12568 | 0.41486 | 1 | 100 | 576.6 | 317 | 115.55 | 108.43 | 100.28 | 305.3 | 4 | 95.73 | 42.33 | 4 | 37.54 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.95 | 0 | 38.23 | 53 | 53 | 110.55 | 93.18 | 87.75 | 0 | 100.28 | 2.43 | 94.92 | 43.01 | 115.58 | 12.7 | 108.43 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.56 | 215.58 | 220.88 | 0 | 34.53 | 51 | 15791 | 95.73 | 42.33 | 37.54 | 1.42 | 42.33 | 0 | 606 | 431.8 | 459 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 312.2 | 0 | 305.9 | 100.37 | 15728 | 15729 | 316
03/26/22 11:13:46.175 | 548.3503 | 1369.3832 | 53.3807 | 43.7995 | 9.5811 | 30.1728 | 51.0857 | 0 | 1786.0102 | 94.0483 | 85.4518 | 8.5965 | 23.9806 | 70.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0121 | 461.7701 | 458.5301 | 462.4401 | 411.5001 | 441.4501 | 417.4701 | 314.1501 | 0.5729 | 0.086594 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6606817.2907 | 7672094.7116 | 7672094.7116 | 62.4293 | 62.1328 | 1.0018 | 0.99791 | 685499.1396 | 891093.8888 | 460.9134 | 0.51709 | 0 | 0 | 30.1728 | 23.9806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.01786 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.3322 | 1368.0163 | 53.5532 | 43.9968 | 28.565 | 1786.9955 | 85.5518 | 24.6261 | 461.5287 | 0.0067356 | 60.0018 | 0.5747 | -0.19934 | 94.1423 | 2.2702 | 0.10688 | 0.11126 | 5.1461 | 0.12541 | 0.41699 | 1 | 100 | 576.9 | 315 | 115.6 | 108.43 | 100.33 | 305.9 | 4 | 95.73 | 42.33 | 4 | 37.54 | 43.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.98 | 0 | 38.23 | 53 | 53 | 110.55 | 93.18 | 87.81 | 0 | 100.33 | 2.43 | 94.93 | 43.01 | 115.6 | 12.69 | 108.43 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.56 | 215.58 | 220.88 | 0 | 34.49 | 50.69 | 15796 | 95.75 | 42.33 | 37.54 | 1.42 | 42.33 | 0 | 606 | 426.2 | 458.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 313.6 | 0 | 307.4 | 100.21 | 15729 | 15729 | 316
03/26/22 11:13:51.175 | 549.2287 | 1372.0153 | 53.3788 | 43.8002 | 9.5786 | 29.4397 | 51.0876 | 0 | 1786.4541 | 94.0534 | 85.4616 | 8.5919 | 25.4949 | 70.5191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.003 | 461.7 | 458.53 | 462.37 | 411.51 | 441.28 | 417.66 | 314.15 | 0.57198 | 0.2738 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6616701.2857 | 7667705.0621 | 7667705.0621 | 62.4293 | 62.1327 | 1.0018 | 0.99791 | 686796.133 | 890894.0959 | 460.8667 | 0.50702 | 0 | 0 | 29.4397 | 25.4949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016214 | 0.017857 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.3464 | 1368.0196 | 53.5527 | 43.9961 | 28.56 | 1786.9771 | 85.5521 | 24.6276 | 461.5235 | 0.0067244 | 60.0017 | 0.57469 | -0.19939 | 94.1429 | 2.2756 | 0.10743 | 0.11208 | 5.142 | 0.12513 | 0.41939 | 1 | 100 | 577 | 318 | 115.65 | 108.45 | 100.35 | 305.9 | 4 | 95.77 | 42.31 | 4 | 37.53 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.03 | 0 | 38.21 | 53 | 53 | 110.6 | 93.21 | 87.83 | 0 | 100.35 | 2.43 | 94.95 | 43 | 115.63 | 12.69 | 108.45 | 110 | 0 | 15729 | 83.04 | 117.37 | 221.56 | 215.58 | 220.88 | 0 | 34.18 | 50.05 | 15801 | 95.76 | 42.31 | 37.53 | 1.55 | 42.31 | 0 | 606 | 429.6 | 458.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6 | 312.9 | 0 | 306.7 | 100.28 | 15728 | 15729 | 316
03/26/22 11:13:56.174 | 549.2695 | 1371.8604 | 53.378 | 43.8008 | 9.5772 | 29.2499 | 51.0905 | 0 | 1790.1235 | 94.0592 | 85.471 | 8.5882 | 25.8857 | 70.4976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0031 | 461.7001 | 458.5301 | 462.3701 | 411.5101 | 441.2801 | 417.6601 | 314.1501 | 0.57194 | 0.14873 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6616963.254 | 7677460.4175 | 7677460.4175 | 62.4293 | 62.1326 | 1.0018 | 0.99791 | 686948.5972 | 892305.8345 | 460.8668 | 0.50702 | 0 | 0 | 29.2499 | 25.8857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017849 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.3631 | 1368.0278 | 53.5523 | 43.9954 | 28.5495 | 1786.9994 | 85.5524 | 24.6364 | 461.5183 | 0.0067132 | 60.0017 | 0.57468 | -0.20097 | 94.1435 | 2.2868 | 0.10801 | 0.1129 | 5.147 | 0.12486 | 0.42169 | 1 | 100 | 576.1 | 317 | 115.6 | 108.45 | 100.19 | 306.6 | 4 | 95.75 | 42.33 | 4 | 37.54 | 43.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.95 | 0 | 38.23 | 53 | 53 | 110.55 | 93.17 | 87.81 | 0 | 100.19 | 2.43 | 94.92 | 43.01 | 115.6 | 12.71 | 108.45 | 110 | 0 | 15729 | 83.04 | 117.35 | 221.56 | 215.58 | 220.88 | 0 | 33.85 | 49.67 | 15806 | 95.75 | 42.34 | 37.54 | 1.58 | 42.34 | 0 | 606 | 427.7 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 312.8 | 0 | 306.6 | 100.19 | 15727 | 15729 | 317
03/26/22 11:14:01.174 | 547.9019 | 1368.8361 | 53.3795 | 43.8018 | 9.5777 | 30.1825 | 51.0888 | 0 | 1787.414 | 94.0693 | 85.4843 | 8.585 | 23.8383 | 70.4753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0051 | 461.6501 | 458.5001 | 462.2701 | 411.6801 | 441.2001 | 417.8901 | 314.2001 | 0.57346 | 0.12389 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6601373.2635 | 7663796.9638 | 7663796.9638 | 62.4293 | 62.1325 | 1.0018 | 0.99791 | 685204.6851 | 891369.4316 | 460.8068 | 0.50057 | 0 | 0 | 30.1825 | 23.8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017855 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.3737 | 1368.0239 | 53.5518 | 43.9948 | 28.542 | 1787.0348 | 85.5528 | 24.6397 | 461.5131 | 0.0067019 | 60.0017 | 0.57467 | -0.20418 | 94.1441 | 2.2835 | 0.10859 | 0.1137 | 5.1454 | 0.12457 | 0.42391 | 1 | 100 | 577.1 | 315 | 115.55 | 108.43 | 100.37 | 307.7 | 4 | 95.72 | 42.35 | 4 | 37.56 | 43.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.95 | 0 | 38.25 | 53 | 53 | 110.5 | 93.16 | 87.75 | 0 | 100.37 | 2.43 | 94.92 | 43.04 | 115.53 | 12.72 | 108.43 | 110 | 0 | 15729 | 83.02 | 117.33 | 221.56 | 215.58 | 220.88 | 0 | 33.62 | 49.63 | 15811 | 95.71 | 42.35 | 37.55 | 1.64 | 42.35 | 0 | 606 | 431 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.1 | 313.9 | 0 | 307.6 | 100.37 | 15730 | 15729 | 315
03/26/22 11:14:06.175 | 548.457 | 1370.1005 | 53.3809 | 43.8023 | 9.5786 | 29.8907 | 51.0793 | 0 | 1783.342 | 94.0755 | 85.4915 | 8.584 | 24.4607 | 70.4894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.005 | 461.65 | 458.5 | 462.27 | 411.68 | 441.2 | 417.89 | 314.2 | 0.57288 | 0.44029 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6607801.9072 | 7646156.9223 | 7646156.9223 | 62.4293 | 62.1324 | 1.0018 | 0.99791 | 685837.5703 | 889337.6844 | 460.8067 | 0.50057 | 0 | 0 | 29.8907 | 24.4607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016215 | 0.017864 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.3863 | 1368.0236 | 53.5513 | 43.9941 | 28.5363 | 1787.0375 | 85.5532 | 24.6373 | 461.5072 | 0.0066894 | 60.0017 | 0.57466 | -0.20479 | 94.1447 | 2.2832 | 0.10916 | 0.1145 | 5.1434 | 0.12423 | 0.42637 | 1 | 100 | 576.1 | 317 | 115.58 | 108.43 | 100.19 | 305.3 | 4 | 95.73 | 42.34 | 4 | 37.55 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.03 | 0 | 38.24 | 53 | 53 | 110.6 | 93.19 | 87.75 | 0 | 100.19 | 2.43 | 94.95 | 43.02 | 115.6 | 12.69 | 108.43 | 110 | 0 | 15729 | 83.02 | 117.33 | 221.56 | 215.58 | 220.88 | 0 | 33.62 | 49.92 | 15815 | 95.75 | 42.34 | 37.55 | 1.61 | 42.34 | 0 | 606 | 427.7 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.1 | 311.5 | 0 | 305.3 | 100.19 | 15728 | 15729 | 317
03/26/22 11:14:11.174 | 547.6233 | 1367.9123 | 53.3831 | 43.8037 | 9.5793 | 29.9826 | 51.0896 | 0 | 1781.7524 | 94.083 | 85.4998 | 8.5832 | 24.6083 | 70.5113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0061 | 461.5501 | 458.4101 | 462.1401 | 411.7701 | 441.1601 | 418.0101 | 314.1801 | 0.57372 | 0.40844 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6597836.0226 | 7638769.4589 | 7638769.4589 | 62.4293 | 62.1323 | 1.0018 | 0.99791 | 684742.0862 | 888543.7357 | 460.7001 | 0.49707 | 0 | 0 | 29.9826 | 24.6083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016219 | 0.017863 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.4039 | 1368.0367 | 53.5508 | 43.9933 | 28.5274 | 1787.0181 | 85.5536 | 24.639 | 461.5009 | 0.0066758 | 60.0018 | 0.57465 | -0.20322 | 94.1454 | 2.2837 | 0.10973 | 0.11529 | 5.152 | 0.12388 | 0.42923 | 1 | 100 | 575.9 | 318 | 115.53 | 108.43 | 100.16 | 306.4 | 4 | 95.72 | 42.33 | 4 | 37.54 | 43.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114 | 0 | 38.23 | 53 | 53 | 110.55 | 93.18 | 87.83 | 0 | 100.16 | 2.43 | 94.94 | 43.01 | 115.55 | 12.71 | 108.43 | 110 | 0 | 15729 | 83.02 | 117.35 | 221.56 | 215.58 | 220.88 | 0 | 33.8 | 50.38 | 15820 | 95.72 | 42.33 | 37.54 | 1.55 | 42.33 | 0 | 605 | 431.5 | 458.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.9 | 313.8 | 0 | 307.5 | 100.16 | 15728 | 15729 | 316
03/26/22 11:14:16.174 | 547.5978 | 1368.1084 | 53.3848 | 43.8053 | 9.5795 | 29.9555 | 51.0781 | 0 | 1781.0711 | 94.0884 | 85.5051 | 8.5833 | 24.5911 | 70.4576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.012 | 461.52 | 458.4 | 462.13 | 411.7 | 441.11 | 417.94 | 314.14 | 0.57367 | 0.39111 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6597558.2418 | 7639646.5989 | 7639646.5989 | 62.4293 | 62.1323 | 1.0018 | 0.99791 | 684698.1121 | 888658.9337 | 460.6834 | 0.49564 | 0 | 0 | 29.9555 | 24.5911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016216 | 0.017873 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.422 | 1368.0501 | 53.5503 | 43.9926 | 28.5178 | 1786.9953 | 85.5541 | 24.6445 | 461.4943 | 0.0066833 | 60.0018 | 0.57463 | -0.20135 | 94.146 | 2.2752 | 0.11028 | 0.11606 | 5.1652 | 0.12351 | 0.43237 | 1 | 100 | 576 | 318 | 115.63 | 108.43 | 100.17 | 307.4 | 4 | 95.76 | 42.33 | 4 | 37.54 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.08 | 0 | 38.21 | 53 | 53 | 110.6 | 93.19 | 87.87 | 0 | 100.17 | 2.43 | 94.97 | 43 | 115.63 | 12.67 | 108.43 | 110 | 0 | 15729 | 83.02 | 117.37 | 221.56 | 215.58 | 220.88 | 0 | 34.04 | 50.76 | 15826 | 95.76 | 42.33 | 37.54 | 1.53 | 42.33 | 0 | 606 | 429.9 | 458.7 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 312 | 0 | 305.8 | 100.14 | 15729 | 15729 | 317
03/26/22 11:14:21.174 | 547.9671 | 1368.4284 | 53.3868 | 43.8077 | 9.579 | 30.3687 | 51.0708 | 0 | 1779.9667 | 94.0948 | 85.5105 | 8.5842 | 23.9189 | 70.4547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.015 | 461.55 | 458.42 | 462.16 | 411.64 | 441.05 | 417.8 | 314.1 | 0.57321 | 0.51099 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6602317.0001 | 7635092.3357 | 7635092.3357 | 62.4293 | 62.1322 | 1.0018 | 0.99791 | 685181.129 | 888127.9045 | 460.71 | 0.49706 | 0 | 0 | 30.3687 | 23.9189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017879 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.4381 | 1368.057 | 53.5498 | 43.9919 | 28.5166 | 1786.9674 | 85.5546 | 24.637 | 461.4876 | 0.0066903 | 60.0018 | 0.57462 | -0.19927 | 94.1467 | 2.2756 | 0.11083 | 0.11682 | 5.1845 | 0.12313 | 0.43549 | 1 | 100 | 576.2 | 318 | 115.68 | 108.43 | 100.21 | 307.3 | 4 | 95.78 | 42.33 | 4 | 37.54 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.1 | 0 | 38.23 | 53 | 53 | 110.6 | 93.21 | 87.81 | 0 | 100.21 | 2.43 | 94.99 | 43.01 | 115.68 | 12.65 | 108.43 | 110 | 0 | 15729 | 83.02 | 117.4 | 221.56 | 215.58 | 220.88 | 0 | 34.4 | 51.32 | 15831 | 95.78 | 42.33 | 37.55 | 1.53 | 42.33 | 0 | 606 | 427.9 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.2 | 312.9 | 0 | 306.7 | 100.21 | 15728 | 15729 | 317
03/26/22 11:14:26.174 | 547.0429 | 1366.0337 | 53.3877 | 43.8097 | 9.578 | 30.306 | 51.075 | 0 | 1780.2712 | 94.0992 | 85.5146 | 8.5846 | 24.1333 | 70.4753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.015 | 461.55 | 458.42 | 462.16 | 411.64 | 441.05 | 417.8 | 314.1 | 0.57418 | 0.4003 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6591121.7196 | 7632261.5991 | 7632261.5991 | 62.4293 | 62.1321 | 1.0018 | 0.9979 | 684090.8597 | 887715.4843 | 460.71 | 0.49706 | 0 | 0 | 30.306 | 24.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016224 | 0.017883 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.4477 | 1368.0416 | 53.5493 | 43.9911 | 28.5103 | 1786.9286 | 85.5551 | 24.6362 | 461.481 | 0.0066762 | 60.0019 | 0.57462 | -0.19783 | 94.1474 | 2.2799 | 0.11135 | 0.11755 | 5.2084 | 0.12277 | 0.43824 | 1 | 100 | 575.7 | 316 | 115.7 | 108.45 | 100.12 | 302.9 | 4 | 95.81 | 42.33 | 4 | 37.54 | 43.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.13 | 0 | 38.23 | 53 | 53 | 110.65 | 93.23 | 87.87 | 0 | 100.12 | 2.43 | 95 | 43.01 | 115.7 | 12.67 | 108.45 | 110 | 0 | 15729 | 83.02 | 117.4 | 221.56 | 215.58 | 220.88 | 0 | 34.69 | 51.41 | 15836 | 95.78 | 42.33 | 37.54 | 1.51 | 42.33 | 0 | 606 | 428 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 313 | 0 | 306.8 | 100.14 | 15726 | 15729 | 317
03/26/22 11:14:31.175 | 546.3628 | 1365.4556 | 53.3883 | 43.8139 | 9.5745 | 29.5729 | 51.0766 | 0 | 1783.9716 | 94.1089 | 85.5253 | 8.5836 | 24.7637 | 70.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0171 | 461.5801 | 458.3901 | 462.1601 | 411.7101 | 441.0801 | 417.5701 | 314.0601 | 0.57482 | 0.06918 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6582303.5275 | 7648763.7433 | 7648763.7433 | 62.4293 | 62.132 | 1.0018 | 0.9979 | 683512.1286 | 889646.6397 | 460.7101 | 0.50357 | 0 | 0 | 29.5729 | 24.7637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.017876 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.4565 | 1368.0303 | 53.5488 | 43.9904 | 28.503 | 1786.899 | 85.5557 | 24.6359 | 461.4744 | 0.006662 | 60.002 | 0.57461 | -0.19718 | 94.1482 | 2.2889 | 0.11188 | 0.11824 | 5.2142 | 0.12244 | 0.44087 | 1 | 100 | 575.7 | 316 | 115.73 | 108.47 | 100.12 | 306.9 | 4 | 95.81 | 42.34 | 4 | 37.55 | 43.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.13 | 0 | 38.23 | 53 | 53 | 110.65 | 93.23 | 87.83 | 0 | 100.12 | 2.43 | 95 | 43.01 | 115.73 | 12.66 | 108.47 | 110 | 0 | 15729 | 83.02 | 117.4 | 221.56 | 215.58 | 220.88 | 0 | 34.76 | 51.26 | 15840 | 95.81 | 42.34 | 37.55 | 1.48 | 42.34 | 0 | 606 | 430 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.8 | 313.3 | 0 | 307.1 | 100.14 | 15730 | 15729 | 316
03/26/22 11:14:36.176 | 546.6461 | 1366.3227 | 53.389 | 43.8157 | 9.5734 | 30.1072 | 51.0789 | 0 | 1788.312 | 94.1143 | 85.5312 | 8.5831 | 24.0528 | 70.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 461.58 | 458.37 | 462.17 | 411.63 | 441.05 | 417.38 | 313.98 | 0.57438 | -0.10887 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6586187.9789 | 7666146.2953 | 7666146.2953 | 62.4293 | 62.132 | 1.0018 | 0.9979 | 683946.1224 | 891810.2915 | 460.7067 | 0.50719 | 0 | 0 | 30.1072 | 24.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016222 | 0.01787 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.4667 | 1368.0196 | 53.5483 | 43.9897 | 28.4981 | 1786.8639 | 85.5562 | 24.6317 | 461.4677 | 0.0066693 | 60.002 | 0.5746 | -0.196 | 94.1489 | 2.2996 | 0.1124 | 0.11892 | 5.2033 | 0.12212 | 0.44329 | 1 | 100 | 576.3 | 317 | 115.7 | 108.49 | 100.23 | 305.9 | 4 | 95.8 | 42.35 | 4 | 37.56 | 43.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.1 | 0 | 38.24 | 53 | 53 | 110.6 | 93.21 | 87.89 | 0 | 100.23 | 2.43 | 94.99 | 43.02 | 115.7 | 12.69 | 108.49 | 110 | 0 | 15729 | 83.04 | 117.4 | 221.56 | 215.58 | 220.88 | 0 | 34.7 | 50.88 | 15845 | 95.8 | 42.35 | 37.56 | 1.46 | 42.35 | 0 | 606 | 428.1 | 458.8 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.4 | 311.3 | 0 | 305.1 | 100.24 | 15728 | 15729 | 317
03/26/22 11:14:41.173 | 546.9317 | 1367.0865 | 53.3903 | 43.8173 | 9.573 | 30.5042 | 51.0822 | 0 | 1786.836 | 94.1199 | 85.5369 | 8.583 | 23.5611 | 70.4481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.014 | 461.58 | 458.37 | 462.17 | 411.63 | 441.05 | 417.38 | 313.98 | 0.57408 | 0.028385 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6589978.5498 | 7659148.1488 | 7659148.1488 | 62.4293 | 62.1319 | 1.0018 | 0.9979 | 684328.4148 | 891073.3509 | 460.7067 | 0.50719 | 0 | 0 | 30.5042 | 23.5611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016218 | 0.017884 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.4779 | 1368.0156 | 53.5478 | 43.9889 | 28.4924 | 1786.8563 | 85.5567 | 24.6288 | 461.461 | 0.0066983 | 60.0019 | 0.57459 | -0.19618 | 94.1496 | 2.3006 | 0.11291 | 0.11958 | 5.2023 | 0.12186 | 0.44567 | 1 | 100 | 574.3 | 319 | 115.75 | 108.49 | 99.88 | 305.8 | 4 | 95.83 | 42.36 | 4 | 37.58 | 43.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 114.15 | 0 | 38.25 | 53 | 53 | 110.68 | 93.25 | 87.91 | 0 | 99.88 | 2.43 | 95.02 | 43.04 | 115.75 | 12.67 | 108.49 | 106.7 | 0 | 15679 | 83.04 | 117.37 | 221.56 | 215.58 | 220.88 | 4.35 | 34.44 | 50.3 | 15850 | 95.82 | 42.38 | 37.59 | 1.44 | 42.38 | 0 | 606 | 423.6 | 458.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572.5 | 310.3 | 0 | 304.1 | 99.57 | 15700 | 15679 | 317
03/26/22 11:14:46.174 | 547.2492 | 1367.6955 | 53.3945 | 43.8202 | 9.5743 | 30.6977 | 51.0781 | 0 | 1781.3808 | 94.132 | 85.5489 | 8.5831 | 23.0937 | 70.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0071 | 461.7001 | 458.4701 | 462.3001 | 404.4701 | 433.5201 | 409.7801 | 308.3201 | 0.5634 | 0.33047 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6593971.139 | 7635297.9721 | 7635297.9721 | 62.4293 | 62.1318 | 1.0018 | 0.9979 | 684633.0894 | 888351.1249 | 460.8234 | 0.51068 | 0 | 0 | 30.6977 | 23.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016225 | 0.017886 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.4909 | 1368.0141 | 53.5473 | 43.9882 | 28.4877 | 1786.8349 | 85.5572 | 24.6244 | 461.4545 | 0.0066843 | 60.0019 | 0.57456 | -0.19543 | 94.1503 | 2.3001 | 0.1134 | 0.12021 | 5.2167 | 0.1216 | 0.44769 | 1 | 100 | 544.6 | 315 | 115.5 | 108.47 | 95.23 | 287.3 | 4 | 95.71 | 42.51 | 4 | 37.73 | 43.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.93 | 0 | 38.38 | 53 | 53 | 110.48 | 93.14 | 87.91 | 0 | 95.23 | 2.42 | 94.92 | 43.15 | 115.45 | 12.79 | 108.47 | 100.5 | 0 | 15579 | 83.04 | 117.33 | 221.56 | 215.58 | 220.88 | 10.23 | 34.02 | 49.85 | 15855 | 95.68 | 42.51 | 37.74 | 1.34 | 42.51 | 0 | 607 | 399.8 | 459.6 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.6 | 293.2 | 0 | 287.3 | 94.71 | 15625 | 15579 | 315
03/26/22 11:14:51.174 | 547.6268 | 1368.5522 | 53.3966 | 43.8216 | 9.5749 | 30.7799 | 51.0793 | 0 | 1778.759 | 94.1378 | 85.5557 | 8.582 | 23.2797 | 70.4316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.007 | 461.7 | 458.47 | 462.3 | 404.47 | 433.52 | 409.78 | 308.32 | 0.56301 | 0.35739 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6598590.9433 | 7623328.1977 | 7623328.1977 | 62.4293 | 62.1317 | 1.0018 | 0.9979 | 685061.8564 | 887042.6702 | 460.8234 | 0.51068 | 0 | 0 | 30.7799 | 23.2797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016217 | 0.017898 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.502 | 1368.0094 | 53.5468 | 43.9875 | 28.4833 | 1786.8327 | 85.5577 | 24.6214 | 461.4485 | 0.0066713 | 60.0018 | 0.5745 | -0.19713 | 94.1511 | 2.2982 | 0.11387 | 0.12083 | 5.2201 | 0.12137 | 0.44886 | 1 | 100 | 503.8 | 312 | 114.65 | 108.28 | 88.24 | 265.5 | 4 | 95.27 | 42.9 | 4 | 38.11 | 43.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 113.23 | 0 | 38.78 | 53 | 53 | 109.85 | 92.82 | 87.95 | 0 | 88.24 | 2.39 | 94.55 | 43.55 | 114.43 | 13.05 | 108.24 | 91.3 | 0 | 15489 | 83.04 | 117.28 | 221.56 | 215.58 | 220.88 | 19.06 | 33.58 | 49.72 | 15861 | 95.18 | 42.97 | 38.21 | 1 | 42.97 | 0 | 609 | 365.2 | 461 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496.4 | 267.2 | 0 | 261.8 | 86.33 | 15518 | 15489 | 312
03/26/22 11:14:56.174 | 547.3387 | 1367.6904 | 53.4015 | 43.8255 | 9.5759 | 30.1978 | 51.071 | 0 | 1781.1382 | 94.1459 | 85.5684 | 8.5776 | 24.1897 | 70.4274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.004 | 461.81 | 458.58 | 462.41 | 395.97 | 424.5 | 400.86 | 301.6 | 0.55103 | -0.090237 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6594605.5714 | 7630589.8059 | 7630589.8059 | 62.4293 | 62.1316 | 1.0018 | 0.9979 | 684630.2191 | 888227.2792 | 460.9334 | 0.51056 | 0 | 0 | 30.1978 | 24.1897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016221 | 0.017896 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.5136 | 1368.0069 | 53.5462 | 43.9867 | 28.4797 | 1786.8458 | 85.5583 | 24.6174 | 461.4431 | 0.0066598 | 60.0016 | 0.57436 | -0.20118 | 94.1518 | 2.2981 | 0.11432 | 0.12141 | 5.2015 | 0.12118 | 0.44921 | 1 | 100 | 472.8 | 311 | 113.4 | 107.89 | 82.23 | 246.3 | 4 | 94.64 | 43.54 | 4 | 38.76 | 44.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 112.18 | 0 | 39.39 | 53 | 53 | 108.88 | 92.31 | 88.01 | 0 | 82.23 | 2.35 | 94.02 | 44.13 | 113.15 | 13.28 | 107.79 | 84.7 | 0 | 15379 | 83.04 | 117.18 | 221.56 | 215.58 | 220.88 | 24.94 | 33.08 | 50.01 | 15866 | 94.54 | 43.64 | 38.89 | 0.59 | 43.64 | 0 | 610 | 341.5 | 461.9 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465.6 | 246.4 | 0 | 241.4 | 80.97 | 15410 | 15379 | 311
03/26/22 11:15:01.173 | 547.2099 | 1366.9626 | 53.4051 | 43.8293 | 9.5758 | 30.3739 | 51.0766 | 0 | 1781.1744 | 94.1468 | 85.5729 | 8.5739 | 23.7541 | 70.4539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.004 | 461.81 | 458.58 | 462.41 | 395.97 | 424.5 | 400.86 | 301.6 | 0.55116 | -0.089163 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6593119.8069 | 7629020.6037 | 7629020.6037 | 62.4293 | 62.1316 | 1.0018 | 0.9979 | 684462.1881 | 888327.1159 | 460.9333 | 0.51056 | 0 | 0 | 30.3739 | 23.7541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.0179 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.5222 | 1367.9956 | 53.5457 | 43.986 | 28.4747 | 1786.8395 | 85.5588 | 24.615 | 461.4378 | 0.0066482 | 60.0015 | 0.57422 | -0.20425 | 94.1525 | 2.2983 | 0.11475 | 0.12197 | 5.2078 | 0.12102 | 0.44949 | 1 | 100 | 441.1 | 309 | 111.83 | 107.28 | 76.71 | 230.6 | 4 | 93.84 | 44.34 | 4 | 39.58 | 44.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 110.85 | 0 | 40.05 | 53 | 53 | 107.6 | 91.65 | 88.05 | 0 | 76.71 | 2.29 | 93.34 | 44.77 | 111.68 | 13.5 | 107.24 | 75.2 | 0 | 15289 | 83.04 | 117.06 | 221.56 | 215.47 | 220.88 | 33.76 | 32.75 | 50.71 | 15871 | 93.76 | 44.38 | 39.63 | 0.27 | 44.38 | 0 | 611 | 317.4 | 463 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435.3 | 231.9 | 0 | 227.1 | 75.7 | 15320 | 15289 | 308
03/26/22 11:15:06.174 | 546.3738 | 1366.1059 | 53.4213 | 43.8511 | 9.5702 | 29.5732 | 51.0882 | 0 | 1784.2297 | 94.1333 | 85.5748 | 8.5585 | 25.0031 | 70.4481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.999 | 462.34 | 459.13 | 462.95 | 353.34 | 379.6 | 356.45 | 267.88 | 0.49029 | -1.1156 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6582447.4257 | 7627790.8837 | 7627790.8837 | 62.4292 | 62.1316 | 1.0018 | 0.9979 | 683836.2226 | 889767.9685 | 461.4734 | 0.50779 | 0 | 0 | 29.5732 | 25.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016227 | 0.017896 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.5231 | 1367.9692 | 53.5452 | 43.9853 | 28.4709 | 1786.8263 | 85.5594 | 24.611 | 461.4343 | 0.0066407 | 60.0014 | 0.57389 | -0.20738 | 94.1531 | 2.2879 | 0.11514 | 0.12245 | 5.2159 | 0.12089 | 0.44839 | 1 | 100 | 408 | 306 | 110.25 | 106.71 | 70.96 | 211.8 | 4 | 93.03 | 45.07 | 4 | 40.28 | 45.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 109.3 | 0 | 40.84 | 53 | 53 | 106.05 | 90.83 | 88.28 | 0 | 70.96 | 2.23 | 92.54 | 45.55 | 109.93 | 13.74 | 106.62 | 69.1 | 0 | 15189 | 83.04 | 116.94 | 221.31 | 215.36 | 220.75 | 39.64 | 32.55 | 51.76 | 15875 | 92.96 | 45.13 | 40.48 | -0.02 | 45.13 | 0 | 613 | 290.2 | 464.3 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401.7 | 213.7 | 0 | 209.2 | 69.86 | 15226 | 15189 | 306
03/26/22 11:15:11.173 | 544.1973 | 1361.9874 | 53.4468 | 43.8906 | 9.5562 | 29.5213 | 51.075 | 0 | 1786.7069 | 94.0977 | 85.5605 | 8.5372 | 25.2693 | 70.4427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.994 | 462.58 | 459.39 | 463.2 | 332.18 | 357.39 | 334.54 | 251.09 | 0.4614 | -2.0544 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6556108.957 | 7625210.8223 | 7625210.8223 | 62.4291 | 62.1318 | 1.0018 | 0.9979 | 681915.8183 | 891241.76 | 461.7234 | 0.50535 | 0 | 0 | 29.5213 | 25.2693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016234 | 0.017897 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.5099 | 1367.9232 | 53.5449 | 43.9848 | 28.461 | 1786.8219 | 85.5598 | 24.6165 | 461.4321 | 0.0066361 | 60.0013 | 0.57344 | -0.2201 | 94.1534 | 2.3187 | 0.11536 | 0.12268 | 5.2152 | 0.12077 | 0.44729 | 1 | 100 | 370.9 | 307 | 108.18 | 106.05 | 64.5 | 189.2 | 4 | 91.95 | 46.08 | 4 | 41.39 | 45.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 107.43 | 0 | 41.8 | 53 | 53 | 104.55 | 90.03 | 88.51 | 0 | 64.5 | 2.16 | 91.56 | 46.47 | 107.98 | 14.12 | 105.99 | 59.7 | 0 | 15099 | 83.04 | 116.85 | 221.07 | 215.25 | 220.5 | 48.47 | 32.78 | 53.72 | 15880 | 91.88 | 46.15 | 41.5 | -0.36 | 46.15 | 0 | 614 | 259.7 | 465.5 | 27 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360.9 | 189 | 0 | 185 | 62.77 | 15137 | 15099 | 307
03/26/22 11:15:16.174 | 544.4949 | 1368.8929 | 53.5069 | 43.9888 | 9.5182 | 30.6299 | 51.0679 | 0 | 1784.9316 | 93.9993 | 85.5055 | 8.4938 | 23.9989 | 70.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 462.89 | 459.75 | 463.54 | 304.21 | 328.03 | 305.59 | 228.56 | 0.41977 | -2.0635 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6560882.8979 | 7572293.1231 | 7572293.1231 | 62.4289 | 62.1327 | 1.0018 | 0.99791 | 685227.6182 | 890128.3007 | 462.06 | 0.49994 | 0 | 0 | 30.6299 | 23.9989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016223 | 0.017898 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.4953 | 1367.8827 | 53.5446 | 43.9846 | 28.4518 | 1786.8205 | 85.5601 | 24.6229 | 461.4316 | 0.006635 | 60.0012 | 0.57281 | -0.2366 | 94.1536 | 2.3374 | 0.11549 | 0.12277 | 5.2155 | 0.12069 | 0.44689 | 1 | 100 | 316.5 | 303 | 105.53 | 105.36 | 55.04 | 161.3 | 4 | 90.6 | 47.31 | 4 | 42.74 | 46.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 105.2 | 0 | 42.99 | 53 | 53 | 102.65 | 89.05 | 88.73 | 0 | 55.04 | 2.08 | 90.38 | 47.58 | 105.53 | 14.75 | 105.36 | 53.7 | 0 | 14999 | 83.02 | 116.75 | 220.71 | 214.92 | 220.14 | 54.35 | 33.31 | 55.89 | 15885 | 90.6 | 47.31 | 42.74 | -0.72 | 47.31 | 0 | 616 | 229.4 | 466.8 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316.5 | 164.9 | 0 | 161.3 | 55.04 | 15040 | 14999 | 303
03/26/22 11:15:21.174 | 541.8804 | 1367.582 | 53.5609 | 44.0792 | 9.4817 | 29.7685 | 51.0582 | 0 | 1786.8256 | 93.9048 | 85.4467 | 8.4581 | 25.1777 | 70.4278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.996 | 462.89 | 459.75 | 463.54 | 304.21 | 328.03 | 305.59 | 228.56 | 0.42179 | -3.2499 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6528726.1161 | 7550053.1882 | 7550053.1882 | 62.4287 | 62.1336 | 1.0018 | 0.99791 | 684569.076 | 891081.614 | 462.06 | 0.49994 | 0 | 0 | 29.7685 | 25.1777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016228 | 0.017896 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.474 | 1367.8763 | 53.5448 | 43.9851 | 28.4377 | 1786.8324 | 85.5597 | 24.6376 | 461.4331 | 0.0066382 | 60.0012 | 0.57196 | -0.25664 | 94.1527 | 2.3367 | 0.11547 | 0.12297 | 5.2131 | 0.12091 | 0.44855 | 1 | 100 | 237.7 | 271 | 102.65 | 104.76 | 41.34 | 104.9 | 4 | 89.06 | 48.71 | 4 | 44.27 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 102.33 | 0 | 44.52 | 53 | 53 | 100.2 | 87.74 | 88.69 | 0 | 41.34 | 1.98 | 88.9 | 48.99 | 102.43 | 15.8 | 104.69 | 44 | 0 | 14749 | 83.02 | 116.68 | 220.22 | 214.57 | 219.76 | 63.17 | 24.49 | 58.62 | 15891 | 88.89 | 48.87 | 44.4 | -1.3 | 48.87 | 0 | 621 | 138.8 | 470 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218.6 | 99.1 | 0 | 96.1 | 38.02 | 13103 | 14749 | 267
03/26/22 11:15:26.174 | 537.9633 | 1365.9304 | 53.6412 | 44.2164 | 9.4248 | 29.5151 | 51.0543 | 0 | 1790.9699 | 93.7586 | 85.3529 | 8.4057 | 25.8578 | 70.4084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #NV | #NV | #NV | #NV | #NV | #NV | #NV | #NV | #NV | #NV | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 6481467.7275 | 7521731.4884 | 7521731.4884 | 62.4284 | 62.1349 | 1.0018 | 0.99791 | 683738.8948 | 893162.3154 | #NV | #NV | 0 | 0 | 29.5151 | 25.8578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016233 | 0.017881 | 0.010636 | 0.004474 | 0.011584 | 0.0119 | 546.4358 | 1367.8719 | 53.5455 | 43.9864 | 28.4271 | 1786.8779 | 85.5589 | 24.6469 | #NV | #NV | #NV | #NV | #NV | 94.151 | 2.3396 | 0.11568 | 0.12417 | 5.2132 | 0.12183 | #NV | 0 | 100 | 95.4 | 226 | 98.08 | 103.68 | 16.59 | 26.1 | 4 | 86.5 | 50.97 | 4 | 46.74 | 48.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 0 | 98.35 | 0 | 46.88 | 53 | 53 | 96.5 | 85.61 | 88.33 | 0 | 16.59 | 1.84 | 86.65 | 51.09 | 97.13 | 17.41 | 103.61 | 37.5 | 0 | 14839 | 83 | 116.85 | 219.71 | 214.15 | 219.24 | 59.61 | 18.61 | 66.09 | 15895 | 86.2 | 51.2 | 47.14 | -2.46 | 51.2 | 0 | 633 | 33.6 | 477.9 | 27 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.1 | 22.3 | 0 | 21.2 | 11.84 | 11156 | 14839 | 217